## vera.php
B-2 | SEWERAGE - UNDERGROUND FLOOR
CODE | DESCRIPTION | u.m. | QUANTITY | UNIT PRICE | TOTAL
01 | UNDERGROUND FLOOR
TB | Pipes
TB.120.A1 | GALVANIZED STEEL PIPES | kg
GALVANIZED STEEL PIPES In compliance with norms UNI EN 10255 medium series, galvanized before treatment for diameters in inches or nominal diameter DN, up to 4’’ with a bell-and-spigot joint; UNI EN 10216-1/TR1 galvanized after treatment for larger diameters, expressed in milimeters or in DN (minimum table thickness 5 as per the norm), with a flange joint; UNI EN 10240-A1 (for galvanization). Construction and mounting characteristics: - hot-dip galvanized steel pipes drawn without welding (for pipes UNI EN 10255 medium series, it is possible to also get welded pipes Fretz-Moon for the same price); bell-and-spigot joint with special parts, from flange (with galvanized screws) for commercial smooth pipes (UNI EN 10216-1/TR1). – the conventional weights of pipes of various diameters as well typology of use of pipes for various devices are defined by the norm, established in the Specification and/or other technical documents;
- as per bookkeeping needs, values of linear density will be used depending on the typology of pipes and applied diameter, as indicated in tables of the UNI EN norm. The price shall include: - as appropriate, for imbeded pipes: external coating of extruded polyethylene, with a layer on every joint; - scraps and write-offs; - special parts, accessories and possible fixing parts; - carriers, supports and clips; - various expendables.
Galvanized steel pipe
| Underground floor - Water supply |  | 1590
| Underground floor - Fire protection |  | 1800
| Total |  | 3390
TB.130.A1 | ELECTRIC WELDED STAINLESS STEEL PIPES | kg
ELECTRIC WELDED STAINLESS STEEL PIPES In compliance with norms: UNI EN ISO 1127 Construction and mounting characteristics: - austenitic stainless steel pipes type AISI 304 (ASTMTP304) and/or AISI 316 (ASTMTP316), welded and calibrated (removed external seem), white spheroidization, pickled. Seems are made by welding with electric arc with austenitic steel electrodes; when needed and/or emphasized, joints of parts with flanges on extremities are possible; – the conventional weights of pipes of various diameters, as well the typology of use of pipes for various devices are determined by the norm, established in the Specification and/or other technical documents. The price shall include: - scraps and write-offs; - special parts, accessories and possible fixing parts; - carriers, supports and clips; - various expendables.
AISI 304 galvanized steel pipe
| Underground floor - Water supply |  | 2600
| Total |  | 2600
TB.150.A3 | RUN-OFF CAST IRON PIPES WITH BELL-AND-SPIGOT JOINT | m
RUN-OFF CAST IRON PIPES WITH BELL-AND-SPIGOT JOINT In compliance with norms: UNI EN 877/2007. Compliance with these norms will be confirmed by outside mark EN 877 and the pipes will be accompanied by a certificate of compliance with such norms. Construction and mounting characteristics: - centrifugally cast iron pipes with smooth edges, painted on the outside and protected on the inside by epoxy resin treatment; - clamping flange connection; - – B28: - scraps and write-offs; - special parts, accessories and possible fixing parts; - carriers, supports and clips; - various expendables.
Cast iron pipes for waste waters, DN75
| Underground floor - Water supply |  | 4
| Total |  | 4
TB.150.A4 | RUN-OFF CAST IRON PIPES WITH BELL-AND-SPIGOT JOINT | m
RUN-OFF CAST IRON PIPES WITH BELL-AND-SPIGOT JOINT In compliance with norms: UNI EN 877/2007. Compliance with these norms will be confirmed by outside mark EN 877 and the pipes will be accompanied by a certificate of compliance with such norms. Construction and mounting characteristics: - centrifugally cast iron pipes with smooth edges, painted on the outside and protected on the inside by epoxy resin treatment; - clamping flange connection; - – the conventional weights of pipes of various diameters, as well the typology of use of pipes for various devices are determined by the norm, established in the Specification and/or other technical documents. The price shall include: - scraps and write-offs; - special parts, accessories and possible fixing parts; - carriers, supports and clips; - various expendables.
Cast iron pipes for waste waters, DN100
| Underground floor - Water supply |  | 137
| Total |  | 137
TB.150.A5 | RUN-OFF CAST IRON PIPES WITH BELL-AND-SPIGOT JOINT | m
RUN-OFF CAST IRON PIPES WITH BELL-AND-SPIGOT JOINT In compliance with norms: UNI EN 877/2007. Compliance with these norms will be confirmed by outside mark EN 877 and the pipes will be accompanied by a certificate of compliance with such norms. Construction and mounting characteristics: - centrifugally cast iron pipes with smooth edges, painted on the outside and protected on the inside by epoxy resin treatment; - clamping flange connection; - – the conventional weights of pipes of various diameters, as well the typology of use of pipes for various devices are determined by the norm, established in the Specification and/or other technical documents. The price shall include: - scraps and write-offs; - special parts, accessories and possible fixing parts; - carriers, supports and clips; - various expendables.
Cast iron pipes for waste waters, DN125
| Underground floor - Water supply |  | 42
| Total |  | 42
Total PIPES
TC | VALVES
TC.110.A4 | BLEACHED BRASS THREADED BALL VALVE BLEACHED BRASS THREADED BALL VALVE, PN16 In compliance with norms: UNI EN 1074; UNI 8858 Construction and mounting characteristics: 2-way or 3-way valve (as needed and/or requested) with a brass body POT 58Pb, chromed or nickel-plated, with the ball of stainless steel inox AISI 304; full flow, with handle nut mounted on the inside of the body with double gasket (2 Viton O-rings and PTFE sealing ring), a handle with a bar or a fly made of plasticized metal (with axis bumper bearing, included in the price in case of insulated pipes) and thread connections; for hot or cold water, drinking water, fire protection installations and gas/air networks; - procurement in the version with hoses, muškim/ženskim spojevima ili sa holanderima, po zahtijevu. Technical characteristics: - maximum temperature 110°C – working nominal pressure: PN16. The price shall include: - fittings, accessories; - various expendables. | pcs
Ball valve, diam. 3/4"
| Underground floor - Water supply |  | 3
| Total |  | 3
TC.110.A5 | BLEACHED BRASS THREADED BALL VALVE, PN16 In compliance with norms: UNI EN 1074; UNI 8858 Construction and mounting characteristics: 2-way or 3-way valve (as needed and/or requested) with a brass body POT 58Pb, chromed or nickel-plated, with the ball of stainless steel inox AISI 304; full flow, with handle nut mounted on the inside of the body with double gasket (2 Viton O-rings and PTFE sealing ring), a handle with a bar or a fly made of plasticized metal (with axis bumper bearing, included in the price in case of insulated pipes) and thread connections; for hot or cold water, drinking water, fire protection installations and gas/air networks; - procurement in the version with hoses; muškim/ženskim spojevima ili sa holanderima, po zahtijevu. Technical characteristics: - maximum temperature 110°C – working nominal pressure: PN16. The price shall include: - fittings, accessories; - various expendables. | kom.
BLEACHED BRASS THREADED BALL VALVE, PN16 In compliance with norms: UNI EN 1074; UNI 8858 Construction and mounting characteristics: 2-way or 3-way valve (as needed and/or requested) with a brass body POT 58Pb, chromed or nickel-plated, with the ball of stainless steel inox AISI 304; full flow, with handle nut mounted on the inside of the body with double gasket (2 Viton O-rings and PTFE sealing ring), a handle with a bar or a fly made of plasticized metal (with axis bumper bearing, included in the price in case of insulated pipes) and thread connections; for hot or cold water, drinking water, fire protection installations and gas/air networks; - procurement in the version with hoses, male/female couplings or with Hollander couplings, as requested. Technical characteristics: - maximum temperature 110°C – working nominal pressure: PN16. The price shall include: - fittings, accessories; - various expendables.
Ball valve, diam. 1"
| Underground floor - Water supply |  | 6
| Total |  | 6
TC.113.A8 | BALL VALVE OF INOX STEEL 316, PN16 | pcs
BALL VALVE OF INOX STEEL 316, PN16 In compliance with norms: UNI EN 1074 Construction and mounting characteristics: 2-way valve with housing and sphere of stainless steel inox AISI 316 and with a full flow; ball plug with cylindrical linear flow of inox steel and teflon gaskets; a handle with bar of inox steel and thread or flange joints (as needed or requested). For hot or cold wanter, steam, drinking water, demineralized water etc. Technical characteristics: - working temperature: from -20°C to +120°C – working nominal pressure: PN16. The price shall include: - fittings, accessories, suprotne prirubnice; - various expendables.
Stainless steel ball valve, 2"
| Underground floor - Water supply |  | 15
| Total |  | 15
TC.130.A10 | CAST IRON BUTTERFLY VALVE WITH FLANGE, PN16 | pcs
CAST IRON BUTTERFLY VALVE WITH FLANGE, PN16 Construction and mounting characteristics: butterfly valve with spheroid cast iron housing GG40, fully coated by EPDM rubber and perforated holding rings with: - threaded through holes for screw fixing, in the same number as holes of flange joints on pipes, or centring through holes (wafer type) for fixing with clips and screws; placed so as to, when the valve is closed, allow dismantling of pipes and/or a stopping section prior or after the initial mounting; - axis and plugging disc with inox steel lense or spherois cast iron GG40, coated with material that prevents transmission of vibrations; - a handle of solid resistant material with appropriate holes for installation of a lock with a key and a safety seal which is included in the price in case of a batterfly valve for fire extinguishers; - a system for blocking and/or pre-determined proper positioning (for diameters above DN200 with a light operation wheel and a reducer).
In case of the use for drinking water intended to humans, the valve shall be treated by a special interior epoxy treatment certified by the norms in force. In case of the use for fire protection devices, all locks will have the same keys. In case of the use for flammable gases, butterfly valve shall be as previously described, except for connections which will be implemented with nitrile gasket. Technical characteristics: - maximum working temperature: 120°C – nominal working pressure: 16 bars. The price shall include: - accessories, oppostite flanges and screws; - various expendables.
Butterfly valve, DN80
| Underground floor - Water supply |  | 12
| Total |  | 12
Total VALVES
TD | AIR DISTRIBUTION AND DIFFUSION SYSTEMS
TD.160.A1 | FIBRE SILICATE COATINGS | m
Construction and prefabrication characteristics
Coatings REI 60 or REI 120 depending on the need and/or indication in technical documents, for square or rectangular structures, manufactured of homologated calcium silicate asbestos-free panels that do not burn (class 0), minimum thickness sufficient to guarantee behaviour when in contact with fire. Coating will be performed by clips, covers, steel structures connected to holders with angle screws and galvanized steel sections (for ceiling installation) with L profile, dimensions minimum 50x50x5mm, placed with maximum wheelbase of 1500 mm.
Methods of applications are described in the Specification.
The price shall include:
-special parts,
- various expendables;
- technical and photo documentation for technical supervision, previously mentioned certificates and conformity certificates required for control and testing.
Circular ducts insulated by calcium silicate, diam.: inside 270 mm/outside 330 mm
| Underground floor - Fire protection |  | 75
| Total |  | 75
TD.410.A3 | GALVANIZED STEEL AIR INTAKE AND EXHAUST VENTILATION GRILLE | pcs
GALVANIZED STEEL AIR INTAKE AND EXHAUST VENTILATION GRILLE Technical characteristics: Air intake and exhaust ventilation grille consisting of: - a square or rectangular resistant perimetral frame of galvanized steel with holes for fastening visible screws; - watertight and light-impermeable fixed blinds, horizontally spaced and placed from an angle of 45° downwards; holes of around 25mm for dimensions up to 100 dm², around 35mm for larger dimensions; - galvanizes steel control frame for wall installations; - insect net of galvaniyed steel with maximum mesh size of 1cm; painting in RAL colour as chosen by the contractor. As specificallz requested or needed: - a spiral system with self-regulating electrical heating cable for preventing frost and congestion, together with electrical supply accessories. Installation can be performed directly on the channel, on the panel or on the wall, with a suitablel control frame (included in the price) and, as needed, grate will be divided into several units, depending on space and structure it will be mounted on.
For air conditioners for air flow: or for external air exhaust or for air intake into large spaces. The price shall include: - accessories; - various holders and fasteners; - possibly electrical connection of the heating cable; - various expendables.
Anti-rain shutter for air circulation, from 8.1 to 12 dmq
| Underground floor - Fire protection |  | 3
| Total |  | 3
Total AIR DISTRIBUTION AND DIFFUSION SYSTEMS
TE | REGULATION SYSTEMS
TE.700.A10 | ELECTRICAL INSTALLATION WITH A CONDUIT BOX AND ELECTRICAL LINES FOR ALL APPLIANCES | pcs
Construction and mounting characteristics
- a conduit box for thermo-mechanical appliances, implemented and completed as per requirements and specifications in technical documents and the project Specification, together with a connection to the distribution supply network;
- connecting the conduit box with all appliances, including conductor pipes, pipes, lines and all small material that is required for completing mounting and for proper functioning of the installation;
- connecting the conduit box with all appliances, including conductor pipes, pipes, lines and all small material that is needed for completing mounting and for proper functioning of the installation;
- connecting all appliances to appropriate lines of the conduit box.
Methods of application are described in the Specification.
Distribution board, EB_WW1
| Underground floor - Water supply |  | 1
| Total |  | 1
Total REGULATION SYSTEMS
TH | PROTECTION OF HEATING BODIES
TH.710.A1 | SYSTEM WITH SELF-REGULATING HEATING CABLE | m
SYSTEM WITH SELF-REGULATING HEATING CABLE In conformity with norms: Approvals: BS; OVE; DIN VDE; DVGW. Construction and mounting characteristics: a system for maintaining temperature and/or frost protection for transient fluids contained in pipes, reservoirs, drains etc. or for avoiding creating of ice on street slopes, squares, staircases etc., implemented of heating cable consisting of: - appropriate electrical copper sheet conductors depending on the required application on the cable; - heating self-regulating core (internal layer that is expanding or narrowing) of polymer mixed with graphite particles; - insulating polyolefin or fluoropolymer coating; - durable copper sheet cover for mechanical protection and proper laying of cable; - outside coating of polyolefin, fluoropolymer or similar material, resistant to UV rays, thickness suitable for the function of the required application; - B114 IP66;
- B115. Methods of application are described in the Specification. Technical characteristics: - heating cable power supply: around 230°C (+/- 10%) – frequency: 50Hz. The price shall include: - special parts; - a connection strip resistant to high temperatures and UV radiation for fixing and perfect adhesion of the heating cable to the element to be protected; - holders and fittings; - electrical connection; - various expendables.
Winding heating cable
| Underground floor - Water supply |  | 136
| Underground floor - Fire protection |  | 330
| Total |  | 466
TH.710.Z1 | SYSTEM WITH SELF-REGULATING HEATING CABLE | Lump sum
SYSTEM WITH SELF-REGULATING HEATING CABLE In conformity with norms: Approvals: BS; OVE; DIN VDE; DVGW. Construction and mounting characteristics: a system for maintaining temperature and/or frost protection for transient fluids contained in pipes, reservoirs, drains etc. or for avoiding creating of ice on street slopes, squares, staircases etc., made of heating cable consisting of: - appropriate copper sheet electrical conductors depending of the required application on the cable; - heating self-regulating core (interior layer that expands or narrows) of polymer mixed with graphite particles; - insulating polyolefine or fluoropolymer insulating coating; - durable durable copper sheet cover for mechanical protection and proper laying of the cable; - outside coating of polyolefine, fluoropolymer or similar material resistant to UV rays, thickness suitable for the function of the required application; - a box or a fitting set for electrical supply of the cable, made of resistant plastics, protection level minimum IP66;
- set, extensions and/or cable receptacles for linear connections and connecting multiple cables, provided by the same manufacturer as for the cable. Where specifically emphasized and/or requested: - temperature control equipment suitable for installation on the conduit box, including temperature sensors and with a display for direct reading of main parameters (temperature, heating on etc.), a relay outlet for indicating failures and a remote alarm+B82. Methods of application are described in the Specification. Technical characteristics: - power supply of the heating cable: around 230°C (+/- 10%) – frequency: 50Hz. The price shall include: - special parts; - connecting strip resistant to high temperatures and UV radiation for fixing and perfect adhesion of the heating cable to the element to be protected; - holders and fittings; - electrical connection; - various expendables.
Regulator of the heating cable temperature
| Underground floor - Water supply |  | 1
| Total |  | 1
Total PROTECTION OF HEATING BODIES
TI
TI.670.A1 |  | pcs
Ventilation system for maintaining positive pressure in the room, 1000 mc/h - P= 100 Pa
| Underground floor - Fire protection |  | 3
| Total |  | 3
TL | FIRE PROTECTION DEVICES
TL.120.B1 | WALL HYDRANT IN A CABINET UNI 45 | pcs
WALL HYDRANT IN A CABINET UNI 45 In conformity with norms: UNI EN 671-2/2004 UNI 9487. Construction and mounting characteristics: Fire extinguisher consisting of: wall cabinet, 60x38x17cm approximately, for preventing accidents, suitable for mounting in a visible places or for installation (same price and as selected by D.L.) also suitable for outside installation; of galvanized steel sheet and painted red (or, if requested, of INOX steel AISI 304), with doors, lock (with two keys) and an emergency opening system of breakable transparent safe crash materijal. In any case, the opening system will imply a possibility for equipping with a safety stamp. Cabinets intended for outside mounting (outdoors) will have an include roof and ventilation holes. – brass hydrant UNI 45, screwing type or similar slow opening type, with screw in conformity with the norm ISO 7-1; connecting brass parts 1’’1/2;
- flexible pipes (possible to be arranged) of synthetic material, homologated and certified, in conformity with the norm UNI 9487, 20 m long and 45 mm inside diameter, together with accessories in conformity with the norm UNI 804-En 1982, made of brass, with suitable couplings and special galvanized steel wire bandages as per UNI 7422. – a nozzle type UNI 45 of durable material, with a valve with minimum three jet regulating positions, with an option for conical fractionated jet or diffused jet, a 12 mm sprayer with a capacity of 120 l/min of 2 bars; - sprayer holder; - flexible pipe holder in red RAL colour as indicated by ISO 3864.
Full connection-fire hose will have the following hydraulic properties: *minimum working pressure: 1,2 MPa (12 bar); *checked to pressure of 2,4 MPa (24 bars); minimum spraying pressure: 4,2 MPa (42 bars); * maximum temperature 200°C; the cabinet will display information as per UNI 671-2/94 and will be identified by symbols defined by Directive 92/58/CEE. The price shall include: - minor accessories; -connection to water supply network; - regulation table of varnished fire proof steel in accordance with the Law no. 493 14/8/1996, indicative dimensions 30x30cm; - mounting, use and maintenance instructions; - small expendables.
UNI 45 wall hydrant
| Underground floor - Fire protection |  | 8
| Total |  | 8
TL.210.A2 | MANUAL POWDER FIRE EXTINGUISHER | pcs
MANUAL POWDER FIRE EXTINGUISHER In conformity with norms: D.M. 20/12/1982 (and subsequent amendments); D.L. n.93 25/02/2000 (act Dir. 97/23/CE) Construction and mounting characteristics: welded steel mobile fire extinguisher with a welded steel tank filled with fire extinguishing agent (powder) which can be directed towards fore due to internal pressure, manufactured as per the norms D.M. 20/12/1982 and designed so that it can be carried and used manually, maximum mass 20kg. Polyvalent and atoxic type for fires type A, B and C, nitrogene pressurized and completed with: - unscrewing valves with a bar or a trigger; - safety system against accidentals manouvers; - control gauge (zero position, green position for safe use, two red zones outside the green zone); - pipes and nozzle (for the capacity exceeding 3kg or 3l); - suitable holder for hanging on the wall; - red varnishing of the fire extinguisher body, RAL 3000;
'- easy to read identification marks as per instructions D.M. 20/12/1982 on the extinguisher. Technical features: - calibration pressure minimum 1 ¼ of the pressure developed inside the extinguisher at the temperature of 60°C and in any case not exceeding 2,4 MPa. – working pressure between -20 and +60°C; - filling depending on various types offered. The price shall include: - two-sided wall mark as per norms of the Law no. 493 14/08/1996, indicative dimensions 25x25 cm; - potential accessories; - various expendables.
Fire extinguisher, 34A-233BC, 6 kg
| Underground floor - Fire protection |  | 17
| Total |  | 17
TL.211.A2 | MOBILE FIRE EXTINGUISHER CO2 | pcs
MOBILE FIRE EXTINGUISHER CO2 In conformity with norms: D.M. 20/12/1982 (and subsequent amendments); D.L. n.93 25702/2000 (act Dir 97/23/CE) Construction and mounting characteristics: mobile fire extinguisher with a welded steel tank filled with fire extinguishing agent (CO2) which can be directed towards fire due to inside pressure, manufactured as per the norms D.M. 20/12/1982 and designed so that it can be carried and used manually, mass not exceeding 20 kg. Polyvalent and atoxic type for fires type B and C, nitrogen-pressurized and completed with: - unscrewing valves with a bar or a trigger; - safety system against accidental manouvers; - control gauge (zero position, green safe use position, two red zones outside the green zone); - pipe and a sprayer and safety bar (for capacities exceeding 3 kg or 3l); ); - suitable holder for hanging on the wall;
- varnishing fire extinguisher body red with grey end section; - easy-to-read identification marks as per instructions D.M. 20/12/1982 on the extinguisher. Technical features: - cylinder ISPESL with pressure of 250 bars; - calibration pressure between 17 and 20 MPa; – working pressure between -20 and +60°C; - filling depending on various types offered. The price shall include: - two-sided wall mark as per norms of the Law no. 493 14/08/1996, indicative dimensions 25x25 cm; - potential accessories; - various expendables.
Fire extinguisher, CO2 113BBC, 5 kg
| Underground floor - Fire protection |  | 3
| Total |  | 3
Total FIRE PROTECTION DEVICES
TN | THERMAL INSULATION AND COATINGS
TN.110.A7 | THERMAL INSULATION FOR PIPES COATED WITH ELASTOMER EXPANDED FOAM | m2
THERMAL INSULATION FOR PIPES COATED WITH ELASTOMER EXPANDED FOAM In conformity with norms UNI EN 10376; UNI EN ISO 8497; - UNI EN 12086; - behaviour in fire: first class fire reaction certificate. Construction and mounting characteristics: insulation in expanded elastomer of closed cells, implemented by extrusion and vulcanization of synthetic nitrile rubber, smooth surface and cylindrical cross-section, switching off automatically and resistant to the effects of oil, usual chemical solvents and mold. For larger diameters, when coating is not available, panels of the same material will be used. Joints between various parts will be glued and sealed with appropriate self-adhesive tape to be provided by the same manufacturer.
Mounting typology is described in the Specification or other technical documents of the project. Technical characteristics: - thermal conductivity at the temperature of 40°C not exceeding 0.040 W/mK (the value certified by a University laboratory); - vapour spreading resistance factor above 7000; - working temperature range: between -50°C and +100°C; - product without CFC, HCFC, PVC and alogens (chlorine and bromine); fire behaviour as indicated previously, with low toxicity and mistiness. The price shall include: - scraps and write-offs and special parts; - various expendables.
Flexible elastomer foam for pipe insulation, 30 mm thick
| Underground floor - Water supply |  | 135
| Underground floor - Fire protection |  | 150
| Total |  | 285
TN.410.A1 | OUTSIDE THIN METAL SHEET COATING | m2
Construction and prefabrication characteristics
Outside thin metal sheet coating (aluminium or galvanized or varnished, or of inox steel depending on the requirements and indications in the project technical documents), minimum thickness 0.6 mm, consisting of polished parts (cylidrical in case of pipes and round canals), carved and arranged along generatrice.
Methods of application are described in the Specification.
The price shall include:
- write-offs, refuse and special parts;
- various expendables.
Aluminium coating
| Underground floor - Water supply |  | 135
| Underground floor - Fire protection |  | 150
| Total |  | 285
Total THERMAL INSULATION AND COATINGS
TP | ELECTRO PUMPS AND COMPRESSORS
TP.420.A20 | ONE-SEGMENT INSTALLATION OF RESERVOIR-PUMP FOR lifting WASTEWATERS (SEWERAGE) | pcs
ONE-SEGMENT INSTALLATION OF RESERVOIR-PUMP FOR lifting WASTEWATERS (SEWERAGE) Construction and mounting characteristics: a wastewater lifting and drainage system consisting of polyethylene reservoir of minimum 400 litres, with two lifting pumps with inside floats. Two possible alternatives are accepted: a) a reservoir with wide cover for opening and inside submerged pumps which can be checked and separated from the cover, with lifting control bar and a cast iron support that is firmly fitted to the reservoir (‘loware’ system or similar); b) a reservoir with a cover that is fitted with screws and with holes, which pump engines are fitted to (with flanges), with inside submerged rotor, pumps that are separated from the cover by opening of flanges (’KSB’ system or similar).
In any case, each pump will consist of: - single-phase or three-phase (with 2 or 4 poles) with minimum safety level of IP58 in case a), IP57 in case b), insulation class F, with the axis on minimum two spherical bearings without maintenance and thermal probes for protection against overheating with automatic feeding; - centrifugal axis suitable for sewerage drains and pump body of material that is highly resistant to wearing and corrosion, for example bronze or cast steel, or stainless stell for rotor; - intake grille with paddles of the same material as the rotor; - one-piece axis of inox steel with mechanical holders without maintenance; outside box of inox steel or of cast iron, varnished in multiple layers (with initial treatment) based on epoxy resin or chlorinated rubber; - screws entirely of inox steel.
Every pump will be completed with: - electrical cable of suitable length (cable entrance to the engine will be protected by resin seal); - a system with automatic switch-mercury float, adequately fixed to the pump supply pipe (or similar) with electrical cable of appropriate length, together with accessories. Pump level switches will be mounted and calibrated so as to achieve proper sequential effect of the pump; - grey cast iron control valve of the type suitable for drain waters, diameter not below DN40, in any case with a plug fully coated by highly resistant rubber, together with the plug control and blocking system. Screws entirely of inox steel; - discharge pipes of HD polyethylene, PN10 or galvanized; pipes of two pumps will be merged into one that is executed outside the reservoir, with thread connection of minimum 2’’.
In any case, the reservoir will be equipped with a cover for internal inspection and access to pumps, with outside openings for inlet pipes at minimum two places or with a joint for exhaust pipes. The system will be completed by a distribution box (installed in the system's proximity) and with connection lines (voltage, signal transmission, earthing) of the distribution box and the system. Except in cases of specific instructions, the distribution box will of the wall cabinet type of galvanized steel, varnished (or with epoxy coating), or of solid resistant plastics, in any case with protection not below IP44 (IP20 with open distribution box). Together with general switch, it will contain the pump operation, protection and safety units and will comply with the following criteria: - selector for every pump with three positions, manual or automatic; - operation indicators for every pump, for manual start, automatic start and for failure indicator;
- a system of automatic alternation of the order of pump insertion; - presence of contacts without voltage for remote signalling of the operation overview. The electrical system will be completed with voltage connection lines, earthing and signal transmission lines (with suitable electrical cables) between the distribution box and devices (pumps, switch-floats etc.), which will be placed with pipes with solid PVC threads.
Where requested and/or emphasized: - the lifting system will be supplied by a generator with 230 volts outlet as described in the second document, and with automatic effect upon electricity disconnection by the provider. In this case, all cables between distribution box and the generator will be provided. – pumps will be entirely of inox steel AISI 316 and suitable for aggressive waters. Technical characteristics: - working temperature: -20°C - +50°C; - supply voltage: around 230 V single-phase (+/- 10%) for indicative power of every pump above 1kW, around 400V three-phase (+/- 10%) for indicative power of every pump above 1kW; - frequency 50 Hz; - engine with insulation class ’F’ and protection level not below IP58/57. The price shall include: - various accessories to completion; - electrical and hydraulic connection; - small expendables.
Displacement unit for sewerage with 2 pumps and a distribution panel, Q=13 mc/h P=90 kPa kom.
| Underground floor - Water supply |  | 1
| Total |  | 1
TP.440.A1 | SYSTEM FOR LIFTING NON-WASTEWATER (RAINWATER AND SIMILAR) WITH TWO HIGHLY EFFICIENT PUMPS (MORE THAN 10 mc/h FOR EACH PUMP) | pcs
SYSTEM FOR LIFTING NON-WASTEWATER (RAINWATER AND SIMILAR) WITH TWO HIGHLY EFFICIENT PUMPS (MORE THAN 10 mc/h FOR EACH PUMP) Construction and mounting characteristics: a system for lifting and draining of non-wastewaters, with two submersible pumps, each consisting of: electrical three-phase motor with the number of poles not less than 4, with safety level not below IP58, insulation class F, with axis on minimum two spherical bearings without maintenance and thermal probes for overheating protection with automatic feeding. For engines of nominal power equal or above 5,5 kW, a starting system with reduced apsorption will be mandatory (part-winding or star-delta); centrifugal single-channel rotor, or with 2 or 3 channels (suitable for collecting solid and/or tensile particles in solution), high efficiency (optimum functioning not below 70%) and pump body of material highly resistant to wearing and corrosion, for example bronze or cast steel, or for rotor, of stainless steel.
The body of the pump will be provided with flange joints with plugs for automatic gravitation connection with the feeding section, without screws; - single-part axis of inox steel, with mechanical holders without meintenance; varnished in multiple layers (with initial treatment) based on epoxy resins or chlorine-rubber; - screws entirely of inox steel.
Every pump will be provided with: - feeding knee of grey cast iron varnished as previously described, together with a support and with expanding screws of inox steel; - a lifting-submerging system with an inox cord, a lifting rope (galvanized or inox) of suitable length, various mounting accessories; - an eelctrical cable of suitable length (motor cable inlet will be protected by a resin seal); - a system with automatic mercury switch-float, properly fixed to the pump feeding pipe or to the well wall by eelctrical cable of suitable length, together with accessories.
Pump level switches will be mounted and calibrated so as to achieve proper sequential pump operation; - control valve of grey cast iron, type appropriate for drains, minimum diameter DN65, in any case with a plug entirely coated with highly resistant rubber, together with a plug control and blocking system. Screw entitely of inox steel; - HD polyethylene discharge pipes, PN10, with flange joints, executed outside the well, together with supports and holders of galvanized steel. The system will be completed with a distribution box (installed near the system) and with connection lines (voltage, signal transmission, earthing) between the distribution box and the system.
Except in cases of special instructions, the distribution box will be of wall cabinet type, of galvanized steel, varnished (or with epoxy coating), or of solid resistant plastic, in any case with minimum protection of IP44 (IP20 with open distribution box). It will contain, together with a general switch, units for operation, protection and safety of the pump and will comply with the following criteria: - selector for each pump with three positions, manual or automatic; - operation indicators for every pump, for manual start, automatic start and for malfunction indicator; - presnce of an alarm for maximum water level in the well in which pumps are installed, connected with a system of floats that move pumps, or with a special float;
- presence of aoustic signal of operation overview; - a system of automatic alternation of the order of pump insertion; - presence of contacts without voltage for remote signalling of operation overview. Electrical system will be completed with voltage connection lines, earthing and signal transmission lines (with suitable electrical cables) between the distribution box and devices (pumps, switches-floats etc.), which will be placed between pipes with solid PVC threads.
For other information about the electrical part, please refer to the corresponding part of this document. Technical characteristics: - working temperature: -20°C - +50°C; - supply voltage: around 230 V single-phase (+/- 10%) for indicative power of every pump above 1kW, around 400V three-phase (+/- 10%) for indicative power of every pump above 1kW; - frequency 50Hz; - engine with insulation class ’F’ and protection level not below IP58. The price shall include: - various accesories to completion; - electrical and hydraulic connection; - small expendables.
Displacement unit with 3 submerged pumps and a distribution board, Q= 300 mc/h, P= 90 kPa pcs.
| Underground floor - Water supply |  | 1
| Total |  | 1
Total EELCTRO PUMPS AND COMPRESSORS
B-2 | TOTAL SEWERAGE - UNDERGROUND FLOOR