## THERMOTECH
NOTE | PRICES TO BE INSERTED MUST BE WITHOUT V.A.T.
B.2. | THERMOTECHNICAL INSTALLATIONS
Notes:
If on some position material or equipment manufacturer is indicated, teneder can instal other materials or equiment if with same or equivalent caracteristics in line with project documentation. All materials and equipment to be used in construction must be authorised by the Investor.
All related preparaory works, finishings, cleanings, correction, testing of materials, instalations, equipment, providing of atests or similar would not be quoted or payed separately. All pricess are to be incorporated in positions of the BoQ of this Volume. For execution of all positions all relevant materials, tools, movements, connections, organisations, worksman, insurance and other related, are suposed to be included in order to execute works in defined conditions, finalisation with indicated guarantee periods - everything ready for technical taking over.
COD. | DESCRIPTION | u.m. | N. | UNITARY PRICE | TOTAL AMMOUNT
01 | THERMOTECH. - CENTRAL PLANTS
TG | REFRIGERATION SYSTEM AND DEVICES
TG.210.B1 | REFRIGERATION UNITS FOR WATER WITH A WATER-COOLED CONDESER AND HERMETIC "SCROLL" OR SEMIHERMETIC ALTERNATIVE | each
REFRIGERATION UNITS FOR WATER WITH A WATER-COOLED CONDESER AND HERMETIC "SCROLL" OR SEMIHERMETIC ALTERNATIVE In accordance with: UNI EN 378/2003; Instruction PED 97/23/CE; Mechanical instruction 98/37/CE; Instruction for low voltage 73/23 CEE;Instruction for magnetic compatibility EMC 89/336 CEE. Construction and installation characteristiks devices for for chilled water producing, compact type, with a water cooled condenser, which consists essentially of: - Structure is consisting of a profiled spring made of galvanized steel, which are the epoxy paint lacquered or equivalent protection; -the evaporator made of pipe bundle with the pipes made of copper or plate-shaped or brazed stainless steel, which separates each of the compressor in case of semi-hermetic alternative compressors, and for each pair in the case of a scroll compressor with an expansion valve for each wheel, which is thermally insulated with at least 20 mm closed cells elastomer, non-flammable, carefully sealed at the joints (or equivalent insulation);
- Condenser-type pipe bundle with a pipes made ​​of copper, or of plate-shaped or brazed stainless steel, which is separated (or in separate parts) for each curcuit; - Hermetic scroll compressors, or alternative semi-hermetic, depending on whether it is necessary and / or required, together with heating oil at the bottom of the window and thermal protection built into the windings. Compressor will be installed on special non-vibrating supporters and connections to inlet and outlet pipes will be made so that vibration will not be transmitted to the whole group and not be able to cause damage to the pipes of the same parts or other parts of the machine.
Starting of the compressor has to go in order or, for semi-hermetic compressors, with the system of part-winding or star-delta; - copper pipes for cooling liquid, properly insulated with closed-cell elastomer membrane; refrigerant circuit with latching connectors and for charging, an expansive thermostatic valves, indicators of passage, clogged filters, liquid collectors, gate valves, safety valves (which are provided with exhaust pipes that are facing outwards, included in the price); the electrical power and command circuit with a degree of protection not less than IP20 (type of protection, suitable for outdoor installation, which can only be opened with a special key or resources) to maintain control and protection of each load, the pressure A.P. and B.P..
Each transmission line within the group will be provided with some form of insulation of a certain capacity; - electronic control system on microprocessor for controlling the temperature of the chilled water (suppression), protection from frost. Protection from high and low pressure for each compressor, protection for oil pressure (in semi-hermetic compressors), rotation of initial order of the compressors, start time, an overview display equipment (set-point, temperature, etc.)., signalization of irregularities in functioning, etc ; calculation of work hours of each compressors. The machine must be equipped for remote control (start-stop), and will also be available for "clean" contact transmission distance for re-signaling malfunctioning.
Standard equipment entering the group (which is included in the price): - Pressure gauge, A.P. and B.P. for each compressor; - flow of chilled water and cooling water or the same protection; - spring supporters to resist vibration; - neopren non-vibrating joints on the input-output pipes for chilled water. - two thermometers for inert gas, made of stainless steel, maximum accuracy (Class 1), input and output of chilled water; - connections for discharge; - charging with refrigerants and oil that does not freeze type suitable to refrigerants. Specifications: - in the case of the cooling group with hermetic compressors are allowed devices with a single compressor only for standard cooling capacity not exceeding 30/35 kW (12/14 kW electric); however, in the case of semi-hermetic compressors, it is not allowed to use a single compressor since they require two or more scroll compressors.
In machines with scroll compressors, each compressor will match the step partiality; those with semi-hermetic compressors will have at least two steps partialisation (50-100%) for each compressor; - specific cooling power (COP) of not less than 3.5 kW total absorbed electrical power at standard conditions (which do not necessarily match with those that are used) for chilled water at 7 ° C and condenser water at 30-35 ° C (operation with the cooling towers); indication of periodic performance IPLV not less than 4.8 according to ARI. SPECIAL VERSIONS: Where is explicitly required and / or specified by the typology, the cooling group will be provided in the following forms: 1) FOR HEAT RECOVERY to be established with any of the following systems: a) a partial refund, that is, from the heat for the overall overheating around 20% of the total internal heat, which is available in the condenser.
Return will be provided through the exchanger which is set ( in a row ) between the compressor and the condenser ; in devices with multiple cooling circuits will be one exchanger for each compressor (or a single exchanger for separate circuits) ; b) total recovery of condensing heat . In this case the device will be provided with some other analogous main condenser , which will be connected in parallel to this cooling side . In devices with multiple cooling machines will be an exchanger for return on each curcuit (or one exchanger for several separate circuits) . In any case , the entry-exit pipes of hot water for a refund will be installed ( and are included in the price): neopren non-vibrating joints ; - thermometers for internal gas made of stainless steel , maximum accuracy (Class 1 ) ; - Pressure gauge with two shut-off valves ( and compounds) ; 2 ) with ELECTRONIC EXPANSION VALVE (instead of the thermostat ) set to the microprocessor of the device , in connection with the evaporation and condensing temperatures , with the degree of heat and load.
Price includes: - hydraulic and electrical connections; - activation and tests of devices ; - various consumables
Water-cooled water chiller and heat pump with circulation pump and 100-litre water tank, heating capacity 33 kW
| CENTRAL PLANTS - AIR CONDITIONING |  | 1
| Total amount |  | 1
TG.536.A1 | GROUP OF POLYVALENT THERMO COOLERS OF HIGH EFFICIENCY, SILENT, WITH THE TRANSFER TO HYDRAULIC CURCUIT | globally
GROUP OF POLYVALENT THERMO COOLERS OF HIGH EFFICIENCY, SILENT, WITH THE TRANSFER TO HYDRAULIC CURCUIT Group of thermo coolers modern generation for chilled or hot water, which uses the technology of functional transfer to the hydraulic circuit. It is realized with the help of a reliable valve for automatic switching, which accurately monitors the load of the building and which returns to the user maximum thermal and cooling energy. Refrigerant curcuit remains so simple, without any change in the cycle (i.e. no pressure drop of four-way valve). This represents a maximum practical matter, when it comes to the efficiency or reliability. Connected to the system for monitoring of the entire installation, protocol Modbus, LonWorks or BACnet based on how much is required in other project-studies.
The units are designed to be connected in parallel modular logic using the following advantages: - Increased flexibility, increased capacity for monitoring load settings. Different temperatures for the supply which are set in a manner that make it perfectly suitable for a variety of installation typologies, for example: - the distribution of generation unit. As fans or air handling units; the distribution of irradiated plates, running for inducing or cooling rays. The choice of the most convenient source of energy in the various load conditions, due to the functioning between the source and the secondary use of a pulsing type.
The automatic variation of the capacity also for secondary use on the basis of the actual requirements. This leaves practically useless the use of accumulation on the installation, eliminating the cost and especially the loss of efficiency. Hermetic spiral scroll compressors which are completed by the motor protection against overheating, and against excessive temperature of the gas which is supplied. Installed on non-vibrating supporters are filled with oil. Oil cooler for automatic insertion provides oil dilution by the refrigerant at the end of the compressor.
STRUCTURE Unit is made of galvanized steel painted with polyester powder RAL9001. Cooling exchanger for direct expansion type brazed plate INOX AISI 316 with high surface area for exchange with external thermal insulation for condensation. Two independent refrigeration circuits water / freon in turn, crossed flow to improve heat exchange; together with differential pressure for the protection of water and antifreeze resistance, which aims to protect against the danger of freezing. External brazed plate heat exchanger INOX AISI 316 high surface for removal together with heat / condensed insulation.
COOLING CURCUIT Use of ecological refrigerant gas R 410 a. The units are implemented with individual independent refrigeration curcuits providing: - replaceable filter dehydrator for cartridge with acids. - An indicator of fluid flow and humidity - electronic expansion valve - safety switch high pressure - low pressure safety switch - a safety valve high pressure - low pressure safety valve - shut-off valve at the compressor discharge. HYDRAULIC CURCUIT FOR THE EXTRACTION, TRANSFER AND REFUND Units were added a couple of electric pumps with stainless steel rotor INOX AISI 316L, which use cold, hot and original curcuits. Motor valves for switching type on-off with full closure. Motor control valves modulation type, all motor valves, together with high-efficiency drivers and border security controls.
ELECTRONIC FRAME Part for the power implies: - main switch for blocking - insulation transformer for power supply of auxiliary circuit - magnetic-heating compressor protection - command controls of the compressors - pumps for motor protection - command-control pumps.
Control part includes: - proportionally-integrated control of water temperature - antifreeze protection - the protection and measuring compressor - auto-diagnosis system with immediate visualization of failure - visualization of time multiscroll compressor operation - remote control ON / OFF - control of automatic rotation of the compressor start - control transfer between car use and the source - relays for remote signaling of the cumulative alarm - input for demand limit (absorbed power limit as a function of external sign 0 ÷ 10V o 4 ÷ 20 mA) - functionality warning for freezing water and high pressure of cooled gas - function to visualize the set values​​, codes of malfunction and displayed parameters - keys for ON / OFF and reset alarms - interface with graphical display - functionality of the Master-Slave.
EQUIPMENT FOR DELIVERY - Shut-off valve on aspiration of compressor - Pressure gauges for high and low pressure - Phase monitoring - Clean contacts for compressor state - Soft starter - Kit serial converter CAN / BACnet - Kit non-vibrating based on the rubber
Package units for simultaneous and independent production ofheat and cooling energy (water cooled), with circulating pumps. Cooling and heat capacity: 300 kW
| CENTRAL PLANTS - AIR CONDITIONING |  | 2
| Total amount |  | 2
TG.610.A2 | AIR CONDITIONING SYSTEM MONOSPLIT / MULTISPLIT, INVERTER, WITH HEAT PUMP | globally
AIR CONDITIONING SYSTEM MONOSPLIT / MULTISPLIT, INVERTER, WITH HEAT PUMP Compliance with standards: Directive 2002/31/CE . Construction and installation : air conditioning system temperature of one or more rooms, characterized by a high technological content , controlled by the inverter with the possibility of cooling the whole system , in order to achieve EER and COP (e.g. cooling of the liquid, on the output of condesator ) , is composed primarily of : OUTDOOR UNIT especially silent , made from strong galvanized steel and painted with epoxy paint ( or strong fiberglass or other material resistant to atmospheric agents ) , with the dismantling panels for access to internal parts . The unit will include : - hermetic electric compressor (installed on resilient mounts ) type " scroll" or " swing " maximum inaudible , with incorporated thermal protection ; - The condenser coil of copper tubing with aluminum blades , large areas ; axial electric fan ( one or more ) a maximum inaudible , with the engine speed, which varies with the level of protection not less than IP55; - network for the protection of the accident in front of the fan , from strong material, resistant to atmospheric agents ; - the cooling circuit from the copper pipe with thermal coating , filter driers , check and shut-off valves , four-way valve / valves , liquid receiver , solenoid / solenoid valves and everything else that is necessary; - Electronic expansion valves ; - Microprocessor system with an inverter to control the capacity of the compressor and system for controlling the fan speed ; probe pressure Manostats , card clock , etc. . ; - Local external switch - insulator and electrical components according to standard ; - holders and mounts of material resistant to atmospheric agents , excluding black iron , even if it is painted ; Indoor / E unit / E , as appropriate , and / or claim , it will be the type of installation from embedding ( with the channels or not , or type " box" ) or a type , in the wall ( hanging or floor ) or ceiling . Each indoor unit will be composed of a chassis from strong galvanized steel, and will include : - the evaporator coil of copper with aluminum blades ; - rlectric fan maximum inaudible , the bare two speeds ; - a container for collecting condensation from the water -resistant material ; access to the network for the ejection of condensation ; - renewable filter that can be cleaned , with easy access , performance at least G -3 ; replacement filter for each indoor unit ; - the version seen unassembled: the outer layer of precision sheet metal painted or made ​​of strong plastic material with drainage grates with adjustable blades and suction easy dismantling for access to the filter ; units - the "box " will of course be equipped with a diffuser outlet by 2/ 4 arms or 4 individually adjustable / removable arms , combined with the central grille with holes for inlet , easy dismantling for access to the filter ; "Box" will be equipped with more and pump discharge condensing with automatic operation . - electronic devices for control - setup ( with the card ) and electrical appliances and a local external switch - insulator , or the appropriate length of cable with plug , as requested and / or required;
AUTO REGULATION – CONTROL by remote control in the wall connected by special cable to the indoor unit , to select the mode of operation , the temperature " set- point" , the various functions necessary for search and signaling failures and irregularities . The removal operation of hot and cold will happen automatically and the operation in the heat pump will be allowed to external temperature of -10 ° C. At the same price will be accepted that the clock card is in each indoor unit , including the price and the connection between the clock card and the clock ; REFRIGERANT CONNECTION between external and internal units implemented with copper pipe suitable for refrigeration devices, appropriately insulated with coat of expanded neoprene thickness of not less than 12 mm ( type Armacell , K - FLEX , etc. . , ecological) , with the final part, for the visible parts, made of aluminum sheet. Sizing and implementation of cooling lines will have to be carried out by all rules , along with considerate following of the instructions of the construction company and the use of materials and / or components supplied by the same construction company or in any case approved by the company. The pipes will need to be installed right , in order , with special supporters made of plastic . All connections will have to be performed by all regulations, excluding alloys with a high silver content , with all the preparatory operations of cleaning. The maximum total length of the line connecting between the outdoor and indoor unit shall be at least 45 meters for the smallest unit ; 65 meters for the biggest; maximum disparity between the outdoor and indoor unit will be at least 25 meters . Cooling fluid will be R410 - A . Charging with cooling fluid R - 410 A (included in the price system ) will have to be carried out according to the rules of refrigeration tecnique, with the prior creation of a vacuum in many occasions. Power supply will be brought to the outdoor unit , and indoor unit will receive power supply from it . Price includes lines Specifications: - power supply , single-phase 230 V ( + / - 10 % ) ; - control of the modulation speed of the compressor will be able to put down to 25 % of the nominal capacity of the system. - If necessary and / or required , the system will not include just one, but up to 4 indoor units , independent , each of which starts with a pipes , the outdoor unit . Price includes: - special parts and a variety of additional parts ; - various supporters, brackets and holders of air conditioning units and refrigeration lines ; - hydraulic and electrical connections , electrical lines to the external units and between external and internal units ; - miscellaneous consumable materials ; - manuals with instructions in Italian ; - and other necessities .
Split air conditioner - 1 indoor unit 1 outdoor unit - cooling capacity 1 kW - heating capacity 1 kW
| CENTRAL PLANTS - AIR CONDITIONING |  | 2
| Total amount |  | 2
TG.610.A4 | AIR CONDITIONING SYSTEM MONOSPLIT / MULTISPLIT, INVERTER, WITH HEAT PUMP | globally
AIR CONDITIONING SYSTEM MONOSPLIT / MULTISPLIT, INVERTER, WITH HEAT PUMP Compliance with standards: Directive 2002/31/CE . Construction and installation : air conditioning system temperature of one or more rooms, characterized by a high technological content , controlled by the inverter with the possibility of cooling the whole system , in order to achieve EER and COP (e.g. cooling of the liquid, on the output of condesator ) , is composed primarily of : OUTDOOR UNIT especially silent , made from strong galvanized steel and painted with epoxy paint ( or strong fiberglass or other material resistant to atmospheric agents ) , with the dismantling panels for access to internal parts . The unit will include : - hermetic electric compressor (installed on resilient mounts ) type " scroll" or " swing " maximum inaudible , with incorporated thermal protection ; - The condenser coil of copper tubing with aluminum blades , large areas ; axial electric fan ( one or more ) a maximum inaudible , with the engine speed, which varies with the level of protection not less than IP55; - network for the protection of the accident in front of the fan , from strong material, resistant to atmospheric agents ; - the cooling circuit from the copper pipe with thermal coating , filter driers , check and shut-off valves , four-way valve / valves , liquid receiver , solenoid / solenoid valves and everything else that is necessary; - Electronic expansion valves ; - Microprocessor system with an inverter to control the capacity of the compressor and system for controlling the fan speed ; probe pressure Manostats , card clock , etc. . ; - Local external switch - insulator and electrical components according to standard ; - holders and mounts of material resistant to atmospheric agents , excluding black iron , even if it is painted ; Indoor / E unit / E , as appropriate , and / or claim , it will be the type of installation from embedding ( with the channels or not , or type " box" ) or a type , in the wall ( hanging or floor ) or ceiling . Each indoor unit will be composed of a chassis from strong galvanized steel, and will include : - the evaporator coil of copper with aluminum blades ; - rlectric fan maximum inaudible , the bare two speeds ; - a container for collecting condensation from the water -resistant material ; access to the network for the ejection of condensation ; - renewable filter that can be cleaned , with easy access , performance at least G -3 ; replacement filter for each indoor unit ; - the version seen unassembled: the outer layer of precision sheet metal painted or made ​​of strong plastic material with drainage grates with adjustable blades and suction easy dismantling for access to the filter ; units - the "box " will of course be equipped with a diffuser outlet by 2/ 4 arms or 4 individually adjustable / removable arms , combined with the central grille with holes for inlet , easy dismantling for access to the filter ; "Box" will be equipped with more and pump discharge condensing with automatic operation . - electronic devices for control - setup ( with the card ) and electrical appliances and a local external switch - insulator , or the appropriate length of cable with plug , as requested and / or required;
AUTO REGULATION – CONTROL by remote control in the wall connected by special cable to the indoor unit , to select the mode of operation , the temperature " set- point" , the various functions necessary for search and signaling failures and irregularities . The removal operation of hot and cold will happen automatically and the operation in the heat pump will be allowed to external temperature of -10 ° C. At the same price will be accepted that the clock card is in each indoor unit , including the price and the connection between the clock card and the clock ; REFRIGERANT CONNECTION between external and internal units implemented with copper pipe suitable for refrigeration devices, appropriately insulated with coat of expanded neoprene thickness of not less than 12 mm ( type Armacell , K - FLEX , etc. . , ecological) , with the final part, for the visible parts, made of aluminum sheet. Sizing and implementation of cooling lines will have to be carried out by all rules , along with considerate following of the instructions of the construction company and the use of materials and / or components supplied by the same construction company or in any case approved by the company. The pipes will need to be installed right , in order , with special supporters made of plastic . All connections will have to be performed by all regulations, excluding alloys with a high silver content , with all the preparatory operations of cleaning. The maximum total length of the line connecting between the outdoor and indoor unit shall be at least 45 meters for the smallest unit ; 65 meters for the biggest; maximum disparity between the outdoor and indoor unit will be at least 25 meters . Cooling fluid will be R410 - A . Charging with cooling fluid R - 410 A (included in the price system ) will have to be carried out according to the rules of refrigeration tecnique, with the prior creation of a vacuum in many occasions. Power supply will be brought to the outdoor unit , and indoor unit will receive power supply from it . Price includes lines Specifications: - power supply , single-phase 230 V ( + / - 10 % ) ; - control of the modulation speed of the compressor will be able to put down to 25 % of the nominal capacity of the system. - If necessary and / or required , the system will not include just one, but up to 4 indoor units , independent , each of which starts with a pipes , the outdoor unit . Price includes: - special parts and a variety of additional parts ; - various supporters, brackets and holders of air conditioning units and refrigeration lines ; - hydraulic and electrical connections , electrical lines to the external units and between external and internal units ; - miscellaneous consumable materials ; - manuals with instructions in Italian ; - and other necessities .
| CENTRAL PLANTS - AIR CONDITIONING |  | 1
| Total amount |  | 1
TG.610.A5 | AIR CONDITIONING SYSTEM MONOSPLIT / MULTISPLIT, INVERTER, WITH HEAT PUMP | globally
AIR CONDITIONING SYSTEM MONOSPLIT / MULTISPLIT, INVERTER, WITH HEAT PUMP Compliance with standards: Directive 2002/31/CE . Construction and installation : air conditioning system temperature of one or more rooms, characterized by a high technological content , controlled by the inverter with the possibility of cooling the whole system , in order to achieve EER and COP (e.g. cooling of the liquid, on the output of condesator ) , is composed primarily of : OUTDOOR UNIT especially silent , made from strong galvanized steel and painted with epoxy paint ( or strong fiberglass or other material resistant to atmospheric agents ) , with the dismantling panels for access to internal parts . The unit will include : - hermetic electric compressor (installed on resilient mounts ) type " scroll" or " swing " maximum inaudible , with incorporated thermal protection ; - The condenser coil of copper tubing with aluminum blades , large areas ; axial electric fan ( one or more ) a maximum inaudible , with the engine speed, which varies with the level of protection not less than IP55;
-network for the protection of the accident in front of the fan , from strong material, resistant to atmospheric agents ; - the cooling circuit from the copper pipe with thermal coating , filter driers , check and shut-off valves , four-way valve / valves , liquid receiver , solenoid / solenoid valves and everything else that is necessary; - Electronic expansion valves ; - Microprocessor system with an inverter to control the capacity of the compressor and system for controlling the fan speed ; probe pressure Manostats , card clock , etc. . ; - Local external switch - insulator and electrical components according to standard ; - holders and mounts of material resistant to atmospheric agents , excluding black iron , even if it is painted ; Indoor / E unit / E , as appropriate , and / or claim , it will be the type of installation from embedding ( with the channels or not , or type " box" ) or a type , in the wall ( hanging or floor ) or ceiling . Each indoor unit will be composed of a chassis from strong galvanized steel, and will include : - the evaporator coil of copper with aluminum blades ; - rlectric fan maximum inaudible , the bare two speeds ; - a container for collecting condensation from the water -resistant material ; access to the network for the ejection of condensation ; - renewable filter that can be cleaned , with easy access , performance at least G -3 ; replacement filter for each indoor unit ; - the version seen unassembled: the outer layer of precision sheet metal painted or made ​​of strong plastic material with drainage grates with adjustable blades and suction easy dismantling for access to the filter ; units - the "box " will of course be equipped with a diffuser outlet by 2/ 4 arms or 4 individually adjustable / removable arms , combined with the central grille with holes for inlet , easy dismantling for access to the filter ; "Box" will be equipped with more and pump discharge condensing with automatic operation . - electronic devices for control - setup ( with the card ) and electrical appliances and a local external switch - insulator , or the appropriate length of cable with plug , as requested and / or required;
AUTO REGULATION – CONTROL by remote control in the wall connected by special cable to the indoor unit , to select the mode of operation , the temperature " set- point" , the various functions necessary for search and signaling failures and irregularities . The removal operation of hot and cold will happen automatically and the operation in the heat pump will be allowed to external temperature of -10 ° C. At the same price will be accepted that the clock card is in each indoor unit , including the price and the connection between the clock card and the clock ; REFRIGERANT CONNECTION between external and internal units implemented with copper pipe suitable for refrigeration devices, appropriately insulated with coat of expanded neoprene thickness of not less than 12 mm ( type Armacell , K - FLEX , etc. . , ecological) , with the final part, for the visible parts, made of aluminum sheet. Sizing and implementation of cooling lines will have to be carried out by all rules , along with considerate following of the instructions of the construction company and the use of materials and / or components supplied by the same construction company or in any case approved by the company.
The pipes will need to be installed right , in order , with special supporters made of plastic . All connections will have to be performed by all regulations, excluding alloys with a high silver content , with all the preparatory operations of cleaning. The maximum total length of the line connecting between the outdoor and indoor unit shall be at least 45 meters for the smallest unit ; 65 meters for the biggest; maximum disparity between the outdoor and indoor unit will be at least 25 meters . Cooling fluid will be R410 - A . Charging with cooling fluid R - 410 A (included in the price system ) will have to be carried out according to the rules of refrigeration tecnique, with the prior creation of a vacuum in many occasions. Power supply will be brought to the outdoor unit , and indoor unit will receive power supply from it . Price includes lines Specifications: - power supply , single-phase 230 V ( + / - 10 % ) ; - control of the modulation speed of the compressor will be able to put down to 25 % of the nominal capacity of the system. - If necessary and / or required , the system will not include just one, but up to 4 indoor units , independent , each of which starts with a pipes , the outdoor unit . Price includes: - special parts and a variety of additional parts ; - various supporters, brackets and holders of air conditioning units and refrigeration lines ; - hydraulic and electrical connections , electrical lines to the external units and between external and internal units ; - miscellaneous consumable materials ; - manuals with instructions in Italian ; - and other necessities .
Split air conditioner - 1 indoor unit 1 outdoor unit - cooling capacity 10 kW - heating capacity 5 kW
| CENTRAL PLANTS - AIR CONDITIONING |  | 1
| Total amount |  | 1
TG.610.B1 | AIR CONDITIONING SYSTEM MONOSPLIT / MULTISPLIT, INVERTER, WITH HEAT PUMP | globally
AIR CONDITIONING SYSTEM MONOSPLIT / MULTISPLIT, INVERTER, WITH HEAT PUMP Compliance with standards: Directive 2002/31/CE . Construction and installation : air conditioning system temperature of one or more rooms, characterized by a high technological content , controlled by the inverter with the possibility of cooling the whole system , in order to achieve EER and COP (e.g. cooling of the liquid, on the output of condesator ) , is composed primarily of : OUTDOOR UNIT especially silent , made from strong galvanized steel and painted with epoxy paint ( or strong fiberglass or other material resistant to atmospheric agents ) , with the dismantling panels for access to internal parts . The unit will include : - hermetic electric compressor (installed on resilient mounts ) type " scroll" or " swing " maximum inaudible , with incorporated thermal protection ; - The condenser coil of copper tubing with aluminum blades , large areas ; axial electric fan ( one or more ) a maximum inaudible , with the engine speed, which varies with the level of protection not less than IP55;
-network for the protection of the accident in front of the fan , from strong material, resistant to atmospheric agents ; - the cooling circuit from the copper pipe with thermal coating , filter driers , check and shut-off valves , four-way valve / valves , liquid receiver , solenoid / solenoid valves and everything else that is necessary; - Electronic expansion valves ; - Microprocessor system with an inverter to control the capacity of the compressor and system for controlling the fan speed ; probe pressure Manostats , card clock , etc. . ; - Local external switch - insulator and electrical components according to standard ; - holders and mounts of material resistant to atmospheric agents , excluding black iron , even if it is painted ; Indoor / E unit / E , as appropriate , and / or claim , it will be the type of installation from embedding ( with the channels or not , or type " box" ) or a type , in the wall ( hanging or floor ) or ceiling . Each indoor unit will be composed of a chassis from strong galvanized steel, and will include : - the evaporator coil of copper with aluminum blades ; - rlectric fan maximum inaudible , the bare two speeds ; - a container for collecting condensation from the water -resistant material ; access to the network for the ejection of condensation ; - renewable filter that can be cleaned , with easy access , performance at least G -3 ; replacement filter for each indoor unit ; - the version seen unassembled: the outer layer of precision sheet metal painted or made ​​of strong plastic material with drainage grates with adjustable blades and suction easy dismantling for access to the filter ; units - the "box " will of course be equipped with a diffuser outlet by 2/ 4 arms or 4 individually adjustable / removable arms , combined with the central grille with holes for inlet , easy dismantling for access to the filter ; "Box" will be equipped with more and pump discharge condensing with automatic operation . - electronic devices for control - setup ( with the card ) and electrical appliances and a local external switch - insulator , or the appropriate length of cable with plug , as requested and / or required;
AUTO REGULATION – CONTROL by remote control in the wall connected by special cable to the indoor unit , to select the mode of operation , the temperature " set- point" , the various functions necessary for search and signaling failures and irregularities . The removal operation of hot and cold will happen automatically and the operation in the heat pump will be allowed to external temperature of -10 ° C. At the same price will be accepted that the clock card is in each indoor unit , including the price and the connection between the clock card and the clock ; REFRIGERANT CONNECTION between external and internal units implemented with copper pipe suitable for refrigeration devices, appropriately insulated with coat of expanded neoprene thickness of not less than 12 mm ( type Armacell , K - FLEX , etc. . , ecological) , with the final part, for the visible parts, made of aluminum sheet. Sizing and implementation of cooling lines will have to be carried out by all rules , along with considerate following of the instructions of the construction company and the use of materials and / or components supplied by the same construction company or in any case approved by the company. The pipes will need to be installed right , in order , with special supporters made of plastic . All connections will have to be performed by all regulations, excluding alloys with a high silver content , with all the preparatory operations of cleaning. The maximum total length of the line connecting between the outdoor and indoor unit shall be at least 45 meters for the smallest unit ; 65 meters for the biggest; maximum disparity between the outdoor and indoor unit will be at least 25 meters . Cooling fluid will be R410 - A . Charging with cooling fluid R - 410 A (included in the price system ) will have to be carried out according to the rules of refrigeration tecnique, with the prior creation of a vacuum in many occasions. Power supply will be brought to the outdoor unit , and indoor unit will receive power supply from it . Price includes lines Specifications: - power supply , single-phase 230 V ( + / - 10 % ) ; - control of the modulation speed of the compressor will be able to put down to 25 % of the nominal capacity of the system. - If necessary and / or required , the system will not include just one, but up to 4 indoor units , independent , each of which starts with a pipes , the outdoor unit . Price includes: - special parts and a variety of additional parts ; - various supporters, brackets and holders of air conditioning units and refrigeration lines ; - hydraulic and electrical connections , electrical lines to the external units and between external and internal units ; - miscellaneous consumable materials ; - manuals with instructions in Italian ; - and other necessities .
Split air conditioner - 1 indoor unit 2 outdoor unit - cooling capacity 5 kW - heating capacity 2.5 kW each
| CENTRAL PLANTS - AIR CONDITIONING |  | 1
| Total amount |  | 1
TOTAL REFRIGERATION SYSTEM AND DEVICES
TI | VENTILATION DEVICES
TI.610.A1 |  | each
SOUNDPROOF FAN
Construction and installation characteristics
device for air flow, centrifugal type, made of:
external shut-off registers consisting of frame and panels from galvanized steel coated with acoustic self-extinguishing material (minimum thickness 50mm) and internal impregnation with profiled sheets, together with connections for rectangular channels
Centrifugal fan, type with double aspiration ;
Electric motor directly connected, single-phase or three-phase, depending of need, with external terminal;
Not vibrating flexible joints.
Technical characteristics:
Voltage : 230 V or 400 V c.a. (+/- 10%);
Frequency 50Hz
Degree of motor protection: minimum IP 54 insulation class F;
Acoustic effect convenient for closing sound fed into the environment, according to the regulations and contractual obligations
Price includes:
equipments for competition
support and a variety of fixing;
electrical connection;
miscellaneous supplies
Soundproof boxed centrifugal fan, Q= 8000 mc/h, P=60 Pa
| CENTRAL PLANTS - VENTILATION |  | 2
| Total amount |  | 2
TI.611.A1 |  | each
CENTRIGUGAL FAN
Construction and installation characteristics
device for air flow, centrifugal type, made of:
external shut-off registers consisting of frame and panels from galvanized steel coated with acoustic self-extinguishing material (minimum thickness 50mm) and internal impregnation with profiled sheets, together with connections for rectangular channels
Centrifugal fan, type with double aspiration ;
The electric motor directly connected, single-phase or three-phase, depending on need, with external terminal;
Not vibrating flexible joints.
Technical characteristics:
Voltage : 230 V or 400 V c.a. (+/- 10%);
Frequency 50Hz
degree of motor protection: minimum IP 54 insulation class F;
acoustic effect convenient for closing sound fed into the environment, according to the regulations and contractual obligations
Price includes
equipments for competition
support and a variety of fixing;
electrical connection;
miscellaneous supplies
Boxed centrifugal fan, Q= 3000 mc/h, P=100 Pa
| CENTRAL PLANTS - VENTILATION |  | 1
| Total amount |  | 1
TOTAL VENTILATION DEVICES
TP | ELECTROPUMPS AND COMPRESSORS
TP.215.12F | CENTRIFUGAL ELECTRIC PUMP WITH LINE ENGINE BLOCK FOR HYDROTHERMAL INSTALLATION OF THE ELECTRONIC VARIABLE VELOCITY | each
CENTRIFUGAL ELECTRIC PUMP WITH LINE ENGINE BLOCK FOR HYDROTHERMAL INSTALLATION OF THE ELECTRONIC VARIABLE SPEED In accordance with standard: UNI ISO 9906 EN 12756 EN 1092-2 Construction and installation characteristics: device with a flow of hot, cold or refrigerated water, type for line installation on the pipes with direct connection on the motor engine or quiet operations, which makes: -driver (dynamically balanced) and pump body from the material very resistant to wear and corrosion, for example from bronze or cast iron, or the driver from stainless steel .
Pump body will also have connections with flanges together with oposite flanges, screws and seals, depending of that how much is necessary and / or specified; - shaft from the stainless steel; - electric motor with terminal, which is proteced and from outside ventilted and shaft from stainless steel (on which is driver connect with bulge) which is consisting from at least two self-lubricating pad or without maintenance; - with electronic system (mounted directly on the pump) with autoregulation microproccessor rotation velocity ( max 145 rad/min) on that way that automaticaly keep pressure to the values which slow growth, depending on the pre-established data by the user to reduce the flow relative to the maximum value of the project-; - device for ventilation and discharge; - device for elimination of axial pressure. The sealing will be of the mechanical type without need for the cooling or maintaining for the temperature of the fluid that goes to 120 ° C. The pumps must be installed on that way to avoide the possibility of condensation or dripping of compensations to the terminal. Pumps must be shared in order to function around the point of maximum effect
Technical characteristics : - maximal working pressure : 12 bar; - working temperature: -10°C - +120°C; - voltage : 230 V mono phase c.a. (+/- 10% ) for indicative current to 1 kW; 400 V three-phase c.a. . (+/- 10%) for indicative current larger than 1 kW; - Frequency: 50 Hz; - Isolation of the motor and the protection class F of not less than IP44. If the diameters of shutoff valves (or irreversible valve) are different from those of the mouth of a circulator, will be provided and included in the price circulator conical clamp (taper does not exceed 15%) valves with threaded ends or flanges (depending of connection type between circulator and valves ) . Price includes : - various equipment of opposite sets of flanges and bolts - potential carriers and / or supports with anchors; - minor consumable parts.
Electronically controlled glanded single pump, Q= 15 mc/h P= 80 kPa
| CENTRAL PLANTS - AIR CONDITIONING |  | 4
| Total amount |  | 4
TP.215.16F | CENTRIFUGAL ELECTRIC PUMP WITH LINE ENGINE BLOCK FOR HYDROTHERMAL INSTALLATION OF THE ELECTRONIC VARIABLE VELOCITY | each
CENTRIFUGAL ELECTRIC PUMP WITH LINE ENGINE BLOCK FOR HYDROTHERMAL INSTALLATION OF THE ELECTRONIC VARIABLE SPEED In accordance with standard: UNI ISO 9906 EN 12756 EN 1092-2 Construction and installation characteristics: device with a flow of hot, cold or refrigerated water, type for line installation on the pipes with direct connection on the motor engine or quiet operations, which makes: -driver (dynamically balanced) and pump body from the material very resistant to wear and corrosion, for example from bronze or cast iron, or the driver from stainless steel .
Pump body will also have connections with flanges together with oposite flanges, screws and seals, depending of that how much is necessary and / or specified; - shaft from the stainless steel; - electric motor with terminal, which is proteced and from outside ventilted and shaft from stainless steel (on which is driver connect with bulge) which is consisting from at least two self-lubricating pad or without maintenance; - with electronic system (mounted directly on the pump) with autoregulation microproccessor rotation velocity ( max 145 rad/min) on that way that automaticaly keep pressure to the values which slow growth, depending on the pre-established data by the user to reduce the flow relative to the maximum value of the project-; - device for ventilation and discharge; - device for elimination of axial pressure. The sealing will be of the mechanical type without need for the cooling or maintaining for the temperature of the fluid that goes to 120 ° C. The pumps must be installed on that way to avoide the possibility of condensation or dripping of compensations to the terminal. Pumps must be shared in order to function around the point of maximum effect
Technical characteristics : - maximal working pressure : 12 bar; - working temperature: -10°C - +120°C; - voltage : 230 V mono phase c.a. (+/- 10% ) for indicative current to 1 kW; 400 V three-phase c.a. . (+/- 10%) for indicative current larger than 1 kW; - Frequency: 50 Hz; - Isolation of the motor and the protection class F of not less than IP44. If the diameters of shutoff valves (or irreversible valve) are different from those of the mouth of a circulator, will be provided and included in the price circulator conical clamp (taper does not exceed 15%) valves with threaded ends or flanges (depending of connection type between circulator and valves ) . Price includes : - various equipment of opposite sets of flanges and bolts - potential carriers and / or supports with anchors; - minor consumable parts.
Electronically controlled glanded single pump, Q= 35 mc/h P= 80 kPa
| CENTRAL PLANTS - AIR CONDITIONING |  | 2
| Total amount |  | 2
TP.215.17G | CENTRIFUGAL ELECTRIC PUMP WITH LINE ENGINE BLOCK FOR HYDROTHERMAL INSTALLATION OF THE ELECTRONIC VARIABLE VELOCITY | each
CENTRIFUGAL ELECTRIC PUMP WITH LINE ENGINE BLOCK FOR HYDROTHERMAL INSTALLATION OF THE ELECTRONIC VARIABLE SPEED In accordance with standard: UNI ISO 9906 EN 12756 EN 1092-2 Construction and installation characteristics: device with a flow of hot, cold or refrigerated water, type for line installation on the pipes with direct connection on the motor engine or quiet operations, which makes: -driver (dynamically balanced) and pump body from the material very resistant to wear and corrosion, for example from bronze or cast iron, or the driver from stainless steel .
Pump body will also have connections with flanges together with oposite flanges, screws and seals, depending of that how much is necessary and / or specified; - shaft from the stainless steel; - electric motor with terminal, which is proteced and from outside ventilted and shaft from stainless steel (on which is driver connect with bulge) which is consisting from at least two self-lubricating pad or without maintenance; - with electronic system (mounted directly on the pump) with autoregulation microproccessor rotation velocity ( max 145 rad/min) on that way that automaticaly keep pressure to the values which slow growth, depending on the pre-established data by the user to reduce the flow relative to the maximum value of the project-; - device for ventilation and discharge; - device for elimination of axial pressure. The sealing will be of the mechanical type without need for the cooling or maintaining for the temperature of the fluid that goes to 120 ° C. The pumps must be installed on that way to avoide the possibility of condensation or dripping of compensations to the terminal. Pumps must be shared in order to function around the point of maximum effect
Technical characteristics : - maximal working pressure : 12 bar; - working temperature: -10°C - +120°C; - voltage : 230 V mono phase c.a. (+/- 10% ) for indicative current to 1 kW; 400 V three-phase c.a. . (+/- 10%) for indicative current larger than 1 kW; - Frequency: 50 Hz; - Isolation of the motor and the protection class F of not less than IP44. If the diameters of shutoff valves (or irreversible valve) are different from those of the mouth of a circulator, will be provided and included in the price circulator conical clamp (taper does not exceed 15%) valves with threaded ends or flanges (depending of connection type between circulator and valves ) . Price includes : - various equipment of opposite sets of flanges and bolts - potential carriers and / or supports with anchors; - minor consumable parts.
Electronically controlled glanded single pump, Q= 40 mc/h P= 90 kPa
| CENTRAL PLANTS - AIR CONDITIONING |  | 2
| Total amount |  | 2
TP.215.20H | CENTRIFUGAL ELECTRIC PUMP WITH LINE ENGINE BLOCK FOR HYDROTHERMAL INSTALLATION OF THE ELECTRONIC VARIABLE VELOCITY | each
CENTRIFUGAL ELECTRIC PUMP WITH LINE ENGINE BLOCK FOR HYDROTHERMAL INSTALLATION OF THE ELECTRONIC VARIABLE SPEED In accordance with standard: UNI ISO 9906 EN 12756 EN 1092-2 Construction and installation characteristics: device with a flow of hot, cold or refrigerated water, type for line installation on the pipes with direct connection on the motor engine or quiet operations, which makes: -driver (dynamically balanced) and pump body from the material very resistant to wear and corrosion, for example from bronze or cast iron, or the driver from stainless steel .
Pump body will also have connections with flanges together with oposite flanges, screws and seals, depending of that how much is necessary and / or specified; - shaft from the stainless steel; - electric motor with terminal, which is proteced and from outside ventilted and shaft from stainless steel (on which is driver connect with bulge) which is consisting from at least two self-lubricating pad or without maintenance; - with electronic system (mounted directly on the pump) with autoregulation microproccessor rotation velocity ( max 145 rad/min) on that way that automaticaly keep pressure to the values which slow growth, depending on the pre-established data by the user to reduce the flow relative to the maximum value of the project-; - device for ventilation and discharge; - device for elimination of axial pressure. The sealing will be of the mechanical type without need for the cooling or maintaining for the temperature of the fluid that goes to 120 ° C. The pumps must be installed on that way to avoide the possibility of condensation or dripping of compensations to the terminal. Pumps must be shared in order to function around the point of maximum effect
Technical characteristics : - maximal working pressure : 12 bar; - working temperature: -10°C - +120°C; - voltage : 230 V mono phase c.a. (+/- 10% ) for indicative current to 1 kW; 400 V three-phase c.a. . (+/- 10%) for indicative current larger than 1 kW; - Frequency: 50 Hz; - Isolation of the motor and the protection class F of not less than IP44. If the diameters of shutoff valves (or irreversible valve) are different from those of the mouth of a circulator, will be provided and included in the price circulator conical clamp (taper does not exceed 15%) valves with threaded ends or flanges (depending of connection type between circulator and valves ) . Price includes : - various equipment of opposite sets of flanges and bolts - potential carriers and / or supports with anchors; - minor consumable parts.
Electronically controlled glanded single pump, Q= 51 mc/h P= 70 kPa
| CENTRAL PLANTS - AIR CONDITIONING |  | 2
| Total amount |  | 2
TP.510.A5 | UNDERWATER ELECTRIC PUMPS WITH MULTISTAGE VERTICAL AXIS | each
UNDERWATER ELECTRIC PUMPS WITH MULTISTAGE VERTICAL AXIS Construction and installation characteristics : device for supply and distribution of water, vertical type, for underwater installation, made up of: -one or more actuators axial or half axial type, dynamically balanced, or static, made of anti-corrosion material such as a synthetic resin, polycarbonate, or stainless steel. Each degree have to be with reinforcing and wear rings of stainless steel; - shut-off shirt of body pump that is made from stainless steel or from brass ; -an electric motor with two half-submerged in a water bath-type short-circuit, with pressure compensator diaphragm bellows, shaft, stainless steel, supports rolling / rolled type to balance the axial pressure; Engine shut-off shirt made of steel; of anti-corrosion materials. The pump, however, will have to be accompanied by: - ​​a non-return valve; - Electrical cable of the correct length, but certainly will not be less than 20 meters.
Technical characteristics: working temeprature: 0°c - +40°C; - voltage : 230 V mono-phase c.a. (+/- 10%) for displayed energy by 1 kW; 400 V three-phase c.a. (+/- 10%) for displayed energy which is not larger than 1 kW; - Frequency: 50 Hz; - Isolation of the motor and the protection class F of not less than IP58 immersed in a water bath. Price includes a variety of equipments for completion; - Hydraulic and electrical connections; - Smaller supplies.
Pumping unit with 2 multistage borehole submersible-motor pump, vessel, inverter and switchboard, Q=55/35 mc/h, H= 600 kPa each
| CENTRAL PLANTS - AIR CONDITIONING |  | 1
| Total amount |  | 1
TOTAL ELECTROPUMPS AND COMPRESSORS
TQ | STORAGE AND WATER TREATMENT DEVICES
TQ.110.A10 | CYLINDRICAL RESERVOIR FOR THE FIRST COLLECTION OF WATER, STEEL INSIDE | each
CYLINDRICAL RESERVOIR FOR THE FIRST COLLECTION OF WATER, STEEL INSIDE in accordance with: D.M. 21/03/73 i DPR 777/82 with the next updates . UNI EN ISO 1461 (for the hot-dip galvanizing). Construction and installation characteristics: recipient of the first water collection, vertical type and cylindrical in shape with raised bottom and legs, made of black steel sheet, thickness not less than 4 mm, and the installation for internal building. Internal treatment (when necessary and / or specified in the typology) with organic enamel according to the regulations, will ensure eligibility for the storage of drinking water. A reservoir, in addition, will be accompanied by connections with the charge for the supply pipe diameters up to 3 " and flanged connections with larger diameters; the shaft at the top, with the flanges, screwed together with a lid, and with the valve tube; - indicator has reached the level of the tube from a suitable transparent material, together with the expansion valve and the discharge valve, resistant to shock, and the shape of the letter U, or the like;
- device power float (or certainly in accordance with the requirements ) a certain diameter, with a conical sealing valve, in the form of a "Y" and a unvibrating compound of rubber (between the valve and the float); -galvanized pipe from the overflow valve with a diameter of not less than the power, folded up "in the form of a pipe" with insect net, which leads to a funnel for collecting the siphon drain, which carries the nearest sewage ; connectors and ball drain valves at least 1 " with a hose; not vibrating rubber compounds used on each port; -Thermal isolation is performed (except for express different application) of the plates of the expanded elastomeric with a closed cell with a thickness not smaller than 19 mm, and has a thermal conductivity at a temperature of 40 ° C, and not greater than 0.040 W / mK (specified value university laboratories) and certificates for waterproof in the class "1".
Insulation will be completed with the completion of the aluminum outer sheet, which will be not less than 6/10 mm. Where specifically required by, and / or the following: - the tank to be made of stainless steel AISI 316L (in this case, the internal glazing is not required) and completely, as described above; maximum level (alarm) and minimum (pump seperationn for the withdrawal). Price includes: - hydraulic connections; - Various accessories; - Any materials to support and anchor; - Smaller supplies.
Water storage tank, galvanized steel, 1000 litres
| CENTRAL PLANTS - AIR CONDITIONING |  | 2
| Total amount |  | 2
TQ.230.A1 | COMPLEX OF CHEMICAL CONDITIONING FOR HEATING INSTALLATIONS CLOSED - LOOP | each
COMPLEX OF CHEMICAL CONDITIONING FOR HEATING INSTALLATIONS CLOSED-LOOP in accordance with UNI CTI 8065 i LG. 10/91 Construction and technical characteristics :complex for the completion of processing system of the water in the heating systems, consisting of: - device for conditioning suitable for installation on the hot water (heating) and chilled water with anticorrosive action, forming a protective film on the interior metal surfaces of the installation (whichever is the nature of the metal), which clog and that mitigate the potential of existing fullness. This, moreover, would be not dangerous or toxic, and will not contaminate the case in urban sewage discharge and will not damage any synthetic materials or materials from elastomers.
Its anti-corrosion effect will not be influenced by the possible presence of oxygen, or antifreeze (glycols) in the water. The dose will be measured at 1 kg per 200 liters (5kg/m3) and the device will be protected in the separate plastic containers, in an amount equal to the required plus 50% (Example 23 Combi Cillit HS); - introduction of a system that includes: * One pump for the introduction of air conditioning with it (which remains the property of the Purchaser, once when is executed load) with all the necessary equipment; connections to the thermal installation with ball valve for expansion, non-return valve which prevents water output from the installation, connector for connection to the pump for filling; - Kit for concentration control. Price includes: charging of device for processing; - Various accessories to complete; - Hydraulic connections; - Testing and calibration of entire system with the filling operation and the control of concentrations; smaller supplies.
Water treatment dosing system, closed circuit
| CENTRAL PLANTS - AIR CONDITIONING |  | 3
| Total amount |  | 3
TQ.418.A3 | CENTRIFUGAL SEPARATOR FOR WATER | each
CENTRIFUGAL SEPARATOR FOE WATER Centrifugal separator, skewed, made from carbonic steel Fe 360B, high efficiency for removal of deposited material, suitable for civil and industrial installation, which consists of: legs for support, chamber tangentially accelerating the fluidized zone, separating chamber and the collection, decantation and cleaning. Qualitative characteristics are: high efficiency separations, reduced losses, the absence of moving parts, constant use, minimal loss due to cleaning, ease of use, reduced operating losses. Usable with following the deposited materials: steel, aluminum, anthracite, bronze, dolomite, iron oxide, graphite, granite, gravel, marble, brass, lead, quartz, silica sand, glass, etc..
Separator corresponding to rule 174. Technical details: Flow min and max: 10 - 200 m3/h - Equipment in and out: DN 150 e DN 150 – Equipment for drain 1" – Separately granulometry: 22 µm - 10 mm – The percentage of sediment removal : 40 - 97% - Specific weight for sediment removal : 1,2 - 11,0 kg/dm3 – Working pressure min and max: 1 - 10 bar - Water temperature min and max: 5 - 30 °C - Room temperature min and max: 5 - 40 °C – Total dimension (hxlxp): 1700 x 1640 x 625 mm Tip Cillit-Tornado TMF600 or similar
Centrifugal separator, 10-20 mc/h
| CENTRAL PLANTS - AIR CONDITIONING |  | 3
| Total amount |  | 3
TOTAL STORAGE AND WATER TREATMENT DEVICES
TOTAL THERMOTECH - CENTRAL PLANTS
02 | THERMOTECH. - UNDERGROUND
TI | AIR TREATMENT DEVICES
TI.631.A1 | AXIAL FAN OF HIGH FLOW FOR THE CHANNEL | each
AXIAL FAN OF HIGH FLOW FOR THE CHANNEL Characteristics of production and installation : a device for launching air axial type with the ability to control , consisting of : - external register of hot galvanized steel, of circular cross-section and variable form depending on the length , flanged inlet and outlet ; propellers with blades (with the possibility of regulation) of aluminum die-cast aluminum ; - directly connected to the electric motor in an aluminum housing with the possibility of inversion of the flow (change of electrical circuits ) , suitable (if necessary) for operation with connection star / delta , or another system of reduction of peak current ; compounds with protection against vibration at the entrance and exit ; where provided in other project studies, fan will be antiknock .Technical features : standard operation between -20 ° C to +50 ° C ,continuously ; voltage of power supply 400 V ( + / - 10 % ) ; -frequency : 50 Hz ; - rotation speed : - not more than 950 rounds per minute ; degree of motor protection : not less than IP 55, insulation class F ; - level of protection of connecting terminal : minimum IP 54 ; adequate performance in relation to the level of noise produced in the internal and external environment, in accordance with applicable regulations and contractual provisions . Price includes: - additions for completion ; - elements for supporting and fixing ; - electrical and air connections ; - different consumable items.
Two stage axial duct fan, Q= 7000 mc/h, P=360 Pa
| UNDERGROUND LEVEL - VENTILATION |  | 1
| Total amount |  | 1
TI.631.A2 | AXIAL FAN OF HIGH FLOW FOR THE CHANNEL | each
AXIAL FAN OF HIGH FLOW FOR THE CHANNEL Characteristics of production and installation : a device for launching air axial type with the ability to control , consisting of : - external register of hot galvanized steel, of circular cross-section and variable form depending on the length , flanged inlet and outlet ; propellers with blades (with the possibility of regulation) of aluminum die-cast aluminum ; - directly connected to the electric motor in an aluminum housing with the possibility of inversion of the flow (change of electrical circuits ) , suitable (if necessary) for operation with connection star / delta , or another system of reduction of peak current ; compounds with protection against vibration at the entrance and exit ; where provided in other project studies, fan will be antiknock .Technical features : standard operation between -20 ° C to +50 ° C ,continuously ; voltage of power supply 400 V ( + / - 10 % ) ; -frequency : 50 Hz ; - rotation speed : - not more than 950 rounds per minute ; degree of motor protection : not less than IP 55, insulation class F ; - level of protection of connecting terminal : minimum IP 54 ; adequate performance in relation to the level of noise produced in the internal and external environment, in accordance with applicable regulations and contractual provisions . Price includes: - additions for completion ; - elements for supporting and fixing ; - electrical and air connections ; - different consumable items.
Two stage axial duct fan, Q= 7500 mc/h, P=360 Pa
| UNDERGROUND LEVEL - VENTILATION |  | 1
| Total amount |  | 1
TI.631.A3 | AXIAL FAN OF HIGH FLOW FOR THE CHANNEL | each
AXIAL FAN OF HIGH FLOW FOR THE CHANNEL Characteristics of production and installation : a device for launching air axial type with the ability to control , consisting of : - external register of hot galvanized steel, of circular cross-section and variable form depending on the length , flanged inlet and outlet ; propellers with blades (with the possibility of regulation) of aluminum die-cast aluminum ; - directly connected to the electric motor in an aluminum housing with the possibility of inversion of the flow (change of electrical circuits ) , suitable (if necessary) for operation with connection star / delta , or another system of reduction of peak current ; compounds with protection against vibration at the entrance and exit ; where provided in other project studies, fan will be antiknock .Technical features : standard operation between -20 ° C to +50 ° C ,continuously ; voltage of power supply 400 V ( + / - 10 % ) ; -frequency : 50 Hz ; - rotation speed : - not more than 950 rounds per minute ; degree of motor protection : not less than IP 55, insulation class F ; - level of protection of connecting terminal : minimum IP 54 ; adequate performance in relation to the level of noise produced in the internal and external environment, in accordance with applicable regulations and contractual provisions . Price includes: - additions for completion ; - elements for supporting and fixing ; - electrical and air connections ; - different consumable items.
Two stage axial duct fan, Q= 8500 mc/h, P=360 Pa
| UNDERGROUND LEVEL - VENTILATION |  | 1
| Total amount |  | 1
TOTAL AIR TREATMENT DEVICES
TOTAL THERMOTECH - UNDERGROUND
03 | THERMOTECH. - GROUND FLOOR AND UPPER FLOOR LEVELS
TG | CONDITIONING DEVICES AND SYSTEMS
TG.610.A3 | AIR CONDITIONING SYSTEM MONOSPLIT / MULTISPLIT, INVERTER, WITH HEAT PUMP | globally
AIR CONDITIONING SYSTEM MONOSPLIT / MULTISPLIT, INVERTER, WITH HEAT PUMP Compliance with standards: Directive 2002/31/CE . Construction and installation : air conditioning system temperature of one or more rooms, characterized by a high technological content , controlled by the inverter with the possibility of cooling the whole system , in order to achieve EER and COP (e.g. cooling of the liquid, on the output of condesator ) , is composed primarily of : OUTDOOR UNIT especially silent , made from strong galvanized steel and painted with epoxy paint ( or strong fiberglass or other material resistant to atmospheric agents ) , with the dismantling panels for access to internal parts . The unit will include : - hermetic electric compressor (installed on resilient mounts ) type " scroll" or " swing " maximum inaudible , with incorporated thermal protection ; - The condenser coil of copper tubing with aluminum blades , large areas ; axial electric fan ( one or more ) a maximum inaudible , with the engine speed, which varies with the level of protection not less than IP55; - network for the protection of the accident in front of the fan , from strong material, resistant to atmospheric agents ; - the cooling circuit from the copper pipe with thermal coating , filter driers , check and shut-off valves , four-way valve / valves , liquid receiver , solenoid / solenoid valves and everything else that is necessary; - Electronic expansion valves ; - Microprocessor system with an inverter to control the capacity of the compressor and system for controlling the fan speed ; probe pressure Manostats , card clock , etc. . ; - Local external switch - insulator and electrical components according to standard ; - holders and mounts of material resistant to atmospheric agents , excluding black iron , even if it is painted ; Indoor / E unit / E , as appropriate , and / or claim , it will be the type of installation from embedding ( with the channels or not , or type " box" ) or a type , in the wall ( hanging or floor ) or ceiling . Each indoor unit will be composed of a chassis from strong galvanized steel, and will include : - the evaporator coil of copper with aluminum blades ; - rlectric fan maximum inaudible , the bare two speeds ; - a container for collecting condensation from the water -resistant material ; access to the network for the ejection of condensation ; - renewable filter that can be cleaned , with easy access , performance at least G -3 ; replacement filter for each indoor unit ; - the version seen unassembled: the outer layer of precision sheet metal painted or made ​​of strong plastic material with drainage grates with adjustable blades and suction easy dismantling for access to the filter ; units - the "box " will of course be equipped with a diffuser outlet by 2/ 4 arms or 4 individually adjustable / removable arms , combined with the central grille with holes for inlet , easy dismantling for access to the filter ; "Box" will be equipped with more and pump discharge condensing with automatic operation . - electronic devices for control - setup ( with the card ) and electrical appliances and a local external switch - insulator , or the appropriate length of cable with plug , as requested and / or required;
AUTO REGULATION – CONTROL by remote control in the wall connected by special cable to the indoor unit , to select the mode of operation , the temperature " set- point" , the various functions necessary for search and signaling failures and irregularities . The removal operation of hot and cold will happen automatically and the operation in the heat pump will be allowed to external temperature of -10 ° C. At the same price will be accepted that the clock card is in each indoor unit , including the price and the connection between the clock card and the clock ; REFRIGERANT CONNECTION between external and internal units implemented with copper pipe suitable for refrigeration devices, appropriately insulated with coat of expanded neoprene thickness of not less than 12 mm ( type Armacell , K - FLEX , etc. . , ecological) , with the final part, for the visible parts, made of aluminum sheet. Sizing and implementation of cooling lines will have to be carried out by all rules , along with considerate following of the instructions of the construction company and the use of materials and / or components supplied by the same construction company or in any case approved by the company. The pipes will need to be installed right , in order , with special supporters made of plastic . All connections will have to be performed by all regulations, excluding alloys with a high silver content , with all the preparatory operations of cleaning. The maximum total length of the line connecting between the outdoor and indoor unit shall be at least 45 meters for the smallest unit ; 65 meters for the biggest; maximum disparity between the outdoor and indoor unit will be at least 25 meters . Cooling fluid will be R410 - A . Charging with cooling fluid R - 410 A (included in the price system ) will have to be carried out according to the rules of refrigeration tecnique, with the prior creation of a vacuum in many occasions. Power supply will be brought to the outdoor unit , and indoor unit will receive power supply from it . Price includes lines Specifications: - power supply , single-phase 230 V ( + / - 10 % ) ; - control of the modulation speed of the compressor will be able to put down to 25 % of the nominal capacity of the system. - If necessary and / or required , the system will not include just one, but up to 4 indoor units , independent , each of which starts with a pipes , the outdoor unit . Price includes: - special parts and a variety of additional parts ; - various supporters, brackets and holders of air conditioning units and refrigeration lines ; - hydraulic and electrical connections , electrical lines to the external units and between external and internal units ; - miscellaneous consumable materials ; - manuals with instructions in Italian ; - and other necessities .
Split air conditioner - 1 indoor unit 1 outdoor unit - cooling capacity 1.5 kW - heating capacity 1.5 kW
| GROUND FLOOR LEVEL - AIR CONDITIONING |  | 1
| Total amount |  | 1
TG.610.A4 | AIR CONDITIONING SYSTEM MONOSPLIT / MULTISPLIT, INVERTER, WITH HEAT PUMP Compliance with standards: Directive 2002/31/CE . Construction and installation : air conditioning system temperature of one or more rooms, characterized by a high technological content , controlled by the inverter with the possibility of cooling the whole system , in order to achieve EER and COP (e.g. cooling of the liquid, on the output of condesator ) , is composed primarily of : OUTDOOR UNIT especially silent , made from strong galvanized steel and painted with epoxy paint ( or strong fiberglass or other material resistant to atmospheric agents ) , with the dismantling panels for access to internal parts . The unit will include : - hermetic electric compressor (installed on resilient mounts ) type " scroll" or " swing " maximum inaudible , with incorporated thermal protection ; - The condenser coil of copper tubing with aluminum blades , large areas ; axial electric fan ( one or more ) a maximum inaudible , with the engine speed, which varies with the level of protection not less than IP55; - network for the protection of the accident in front of the fan , from strong material, resistant to atmospheric agents ; - the cooling circuit from the copper pipe with thermal coating , filter driers , check and shut-off valves , four-way valve / valves , liquid receiver , solenoid / solenoid valves and everything else that is necessary; - Electronic expansion valves ; - Microprocessor system with an inverter to control the capacity of the compressor and system for controlling the fan speed ; probe pressure Manostats , card clock , etc. . ; - Local external switch - insulator and electrical components according to standard ; - holders and mounts of material resistant to atmospheric agents , excluding black iron , even if it is painted ; Indoor / E unit / E , as appropriate , and / or claim , it will be the type of installation from embedding ( with the channels or not , or type " box" ) or a type , in the wall ( hanging or floor ) or ceiling . Each indoor unit will be composed of a chassis from strong galvanized steel, and will include : - the evaporator coil of copper with aluminum blades ; - rlectric fan maximum inaudible , the bare two speeds ; - a container for collecting condensation from the water -resistant material ; access to the network for the ejection of condensation ; - renewable filter that can be cleaned , with easy access , performance at least G -3 ; replacement filter for each indoor unit ; - the version seen unassembled: the outer layer of precision sheet metal painted or made ​​of strong plastic material with drainage grates with adjustable blades and suction easy dismantling for access to the filter ; units - the "box " will of course be equipped with a diffuser outlet by 2/ 4 arms or 4 individually adjustable / removable arms , combined with the central grille with holes for inlet , easy dismantling for access to the filter ; "Box" will be equipped with more and pump discharge condensing with automatic operation . - electronic devices for control - setup ( with the card ) and electrical appliances and a local external switch - insulator , or the appropriate length of cable with plug , as requested and / or required; | globally
AUTO REGULATION – CONTROL by remote control in the wall connected by special cable to the indoor unit , to select the mode of operation , the temperature " set- point" , the various functions necessary for search and signaling failures and irregularities . The removal operation of hot and cold will happen automatically and the operation in the heat pump will be allowed to external temperature of -10 ° C. At the same price will be accepted that the clock card is in each indoor unit , including the price and the connection between the clock card and the clock ; REFRIGERANT CONNECTION between external and internal units implemented with copper pipe suitable for refrigeration devices, appropriately insulated with coat of expanded neoprene thickness of not less than 12 mm ( type Armacell , K - FLEX , etc. . , ecological) , with the final part, for the visible parts, made of aluminum sheet. Sizing and implementation of cooling lines will have to be carried out by all rules , along with considerate following of the instructions of the construction company and the use of materials and / or components supplied by the same construction company or in any case approved by the company. The pipes will need to be installed right , in order , with special supporters made of plastic . All connections will have to be performed by all regulations, excluding alloys with a high silver content , with all the preparatory operations of cleaning. The maximum total length of the line connecting between the outdoor and indoor unit shall be at least 45 meters for the smallest unit ; 65 meters for the biggest; maximum disparity between the outdoor and indoor unit will be at least 25 meters . Cooling fluid will be R410 - A . Charging with cooling fluid R - 410 A (included in the price system ) will have to be carried out according to the rules of refrigeration tecnique, with the prior creation of a vacuum in many occasions. Power supply will be brought to the outdoor unit , and indoor unit will receive power supply from it . Price includes lines Specifications: - power supply , single-phase 230 V ( + / - 10 % ) ; - control of the modulation speed of the compressor will be able to put down to 25 % of the nominal capacity of the system. - If necessary and / or required , the system will not include just one, but up to 4 indoor units , independent , each of which starts with a pipes , the outdoor unit . Price includes: - special parts and a variety of additional parts ; - various supporters, brackets and holders of air conditioning units and refrigeration lines ; - hydraulic and electrical connections , electrical lines to the external units and between external and internal units ; - miscellaneous consumable materials ; - manuals with instructions in Italian ; - and other necessities .
Split air conditioner - 1 indoor unit 1 outdoor unit - cooling capacity 2.5 kW - heating capacity 1 kW
| GROUND FLOOR LEVEL - AIR CONDITIONING - UNIVERSITY |  | 1
| Total amount |  | 1
TG.610.A6 | AIR CONDITIONING SYSTEM MONOSPLIT / MULTISPLIT, INVERTER, WITH HEAT PUMP Compliance with standards: Directive 2002/31/CE . Construction and installation : air conditioning system temperature of one or more rooms, characterized by a high technological content , controlled by the inverter with the possibility of cooling the whole system , in order to achieve EER and COP (e.g. cooling of the liquid, on the output of condesator ) , is composed primarily of : OUTDOOR UNIT especially silent , made from strong galvanized steel and painted with epoxy paint ( or strong fiberglass or other material resistant to atmospheric agents ) , with the dismantling panels for access to internal parts . The unit will include : - hermetic electric compressor (installed on resilient mounts ) type " scroll" or " swing " maximum inaudible , with incorporated thermal protection ; - The condenser coil of copper tubing with aluminum blades , large areas ; axial electric fan ( one or more ) a maximum inaudible , with the engine speed, which varies with the level of protection not less than IP55; - network for the protection of the accident in front of the fan , from strong material, resistant to atmospheric agents ; - the cooling circuit from the copper pipe with thermal coating , filter driers , check and shut-off valves , four-way valve / valves , liquid receiver , solenoid / solenoid valves and everything else that is necessary; - Electronic expansion valves ; - Microprocessor system with an inverter to control the capacity of the compressor and system for controlling the fan speed ; probe pressure Manostats , card clock , etc. . ; - Local external switch - insulator and electrical components according to standard ; - holders and mounts of material resistant to atmospheric agents , excluding black iron , even if it is painted ; Indoor / E unit / E , as appropriate , and / or claim , it will be the type of installation from embedding ( with the channels or not , or type " box" ) or a type , in the wall ( hanging or floor ) or ceiling . Each indoor unit will be composed of a chassis from strong galvanized steel, and will include : - the evaporator coil of copper with aluminum blades ; - rlectric fan maximum inaudible , the bare two speeds ; - a container for collecting condensation from the water -resistant material ; access to the network for the ejection of condensation ; - renewable filter that can be cleaned , with easy access , performance at least G -3 ; replacement filter for each indoor unit ; - the version seen unassembled: the outer layer of precision sheet metal painted or made ​​of strong plastic material with drainage grates with adjustable blades and suction easy dismantling for access to the filter ; units - the "box " will of course be equipped with a diffuser outlet by 2/ 4 arms or 4 individually adjustable / removable arms , combined with the central grille with holes for inlet , easy dismantling for access to the filter ; "Box" will be equipped with more and pump discharge condensing with automatic operation . - electronic devices for control - setup ( with the card ) and electrical appliances and a local external switch - insulator , or the appropriate length of cable with plug , as requested and / or required; | globally
AUTO REGULATION – CONTROL by remote control in the wall connected by special cable to the indoor unit , to select the mode of operation , the temperature " set- point" , the various functions necessary for search and signaling failures and irregularities . The removal operation of hot and cold will happen automatically and the operation in the heat pump will be allowed to external temperature of -10 ° C. At the same price will be accepted that the clock card is in each indoor unit , including the price and the connection between the clock card and the clock ; REFRIGERANT CONNECTION between external and internal units implemented with copper pipe suitable for refrigeration devices, appropriately insulated with coat of expanded neoprene thickness of not less than 12 mm ( type Armacell , K - FLEX , etc. . , ecological) , with the final part, for the visible parts, made of aluminum sheet. Sizing and implementation of cooling lines will have to be carried out by all rules , along with considerate following of the instructions of the construction company and the use of materials and / or components supplied by the same construction company or in any case approved by the company. The pipes will need to be installed right , in order , with special supporters made of plastic . All connections will have to be performed by all regulations, excluding alloys with a high silver content , with all the preparatory operations of cleaning. The maximum total length of the line connecting between the outdoor and indoor unit shall be at least 45 meters for the smallest unit ; 65 meters for the biggest; maximum disparity between the outdoor and indoor unit will be at least 25 meters . Cooling fluid will be R410 - A . Charging with cooling fluid R - 410 A (included in the price system ) will have to be carried out according to the rules of refrigeration tecnique, with the prior creation of a vacuum in many occasions. Power supply will be brought to the outdoor unit , and indoor unit will receive power supply from it . Price includes lines Specifications: - power supply , single-phase 230 V ( + / - 10 % ) ; - control of the modulation speed of the compressor will be able to put down to 25 % of the nominal capacity of the system. - If necessary and / or required , the system will not include just one, but up to 4 indoor units , independent , each of which starts with a pipes , the outdoor unit . Price includes: - special parts and a variety of additional parts ; - various supporters, brackets and holders of air conditioning units and refrigeration lines ; - hydraulic and electrical connections , electrical lines to the external units and between external and internal units ; - miscellaneous consumable materials ; - manuals with instructions in Italian ; - and other necessities .
Split air conditioner - 1 indoor unit 1 outdoor unit - cooling capacity 6 kW - heating capacity 1.5 kW
| SECOND FLOOR LEVEL - AIR CONDITIONING |  | 1
| Total amount |  | 1
TG.610.B2 | AIR CONDITIONING SYSTEM MONOSPLIT / MULTISPLIT, INVERTER, WITH HEAT PUMP Compliance with standards: Directive 2002/31/CE . Construction and installation : air conditioning system temperature of one or more rooms, characterized by a high technological content , controlled by the inverter with the possibility of cooling the whole system , in order to achieve EER and COP (e.g. cooling of the liquid, on the output of condesator ) , is composed primarily of : OUTDOOR UNIT especially silent , made from strong galvanized steel and painted with epoxy paint ( or strong fiberglass or other material resistant to atmospheric agents ) , with the dismantling panels for access to internal parts . The unit will include : - hermetic electric compressor (installed on resilient mounts ) type " scroll" or " swing " maximum inaudible , with incorporated thermal protection ; - The condenser coil of copper tubing with aluminum blades , large areas ; axial electric fan ( one or more ) a maximum inaudible , with the engine speed, which varies with the level of protection not less than IP55; - network for the protection of the accident in front of the fan , from strong material, resistant to atmospheric agents ; - the cooling circuit from the copper pipe with thermal coating , filter driers , check and shut-off valves , four-way valve / valves , liquid receiver , solenoid / solenoid valves and everything else that is necessary; - Electronic expansion valves ; - Microprocessor system with an inverter to control the capacity of the compressor and system for controlling the fan speed ; probe pressure Manostats , card clock , etc. . ; - Local external switch - insulator and electrical components according to standard ; - holders and mounts of material resistant to atmospheric agents , excluding black iron , even if it is painted ; Indoor / E unit / E , as appropriate , and / or claim , it will be the type of installation from embedding ( with the channels or not , or type " box" ) or a type , in the wall ( hanging or floor ) or ceiling . Each indoor unit will be composed of a chassis from strong galvanized steel, and will include : - the evaporator coil of copper with aluminum blades ; - rlectric fan maximum inaudible , the bare two speeds ; - a container for collecting condensation from the water -resistant material ; access to the network for the ejection of condensation ; - renewable filter that can be cleaned , with easy access , performance at least G -3 ; replacement filter for each indoor unit ; - the version seen unassembled: the outer layer of precision sheet metal painted or made ​​of strong plastic material with drainage grates with adjustable blades and suction easy dismantling for access to the filter ; units - the "box " will of course be equipped with a diffuser outlet by 2/ 4 arms or 4 individually adjustable / removable arms , combined with the central grille with holes for inlet , easy dismantling for access to the filter ; "Box" will be equipped with more and pump discharge condensing with automatic operation . - electronic devices for control - setup ( with the card ) and electrical appliances and a local external switch - insulator , or the appropriate length of cable with plug , as requested and / or required; | globally
AUTO REGULATION – CONTROL by remote control in the wall connected by special cable to the indoor unit , to select the mode of operation , the temperature " set- point" , the various functions necessary for search and signaling failures and irregularities . The removal operation of hot and cold will happen automatically and the operation in the heat pump will be allowed to external temperature of -10 ° C. At the same price will be accepted that the clock card is in each indoor unit , including the price and the connection between the clock card and the clock ; REFRIGERANT CONNECTION between external and internal units implemented with copper pipe suitable for refrigeration devices, appropriately insulated with coat of expanded neoprene thickness of not less than 12 mm ( type Armacell , K - FLEX , etc. . , ecological) , with the final part, for the visible parts, made of aluminum sheet. Sizing and implementation of cooling lines will have to be carried out by all rules , along with considerate following of the instructions of the construction company and the use of materials and / or components supplied by the same construction company or in any case approved by the company. The pipes will need to be installed right , in order , with special supporters made of plastic . All connections will have to be performed by all regulations, excluding alloys with a high silver content , with all the preparatory operations of cleaning. The maximum total length of the line connecting between the outdoor and indoor unit shall be at least 45 meters for the smallest unit ; 65 meters for the biggest; maximum disparity between the outdoor and indoor unit will be at least 25 meters . Cooling fluid will be R410 - A . Charging with cooling fluid R - 410 A (included in the price system ) will have to be carried out according to the rules of refrigeration tecnique, with the prior creation of a vacuum in many occasions. Power supply will be brought to the outdoor unit , and indoor unit will receive power supply from it . Price includes lines Specifications: - power supply , single-phase 230 V ( + / - 10 % ) ; - control of the modulation speed of the compressor will be able to put down to 25 % of the nominal capacity of the system. - If necessary and / or required , the system will not include just one, but up to 4 indoor units , independent , each of which starts with a pipes , the outdoor unit . Price includes: - special parts and a variety of additional parts ; - various supporters, brackets and holders of air conditioning units and refrigeration lines ; - hydraulic and electrical connections , electrical lines to the external units and between external and internal units ; - miscellaneous consumable materials ; - manuals with instructions in Italian ; - and other necessities .
Split air conditioner - 1 indoor unit 2 outdoor unit - cooling capacity 3.5 kW - heating capacity 2 kW each
| FIRST FLOOR LEVEL - AIR CONDITIONING |  | 1
| Total amount |  | 1
TG.625.A1 |  | each
AUTONOMOUS AIR PRECISE BUILT AIR CONDITIONING TYPE "UNDER" WITH CONDENSATION UNIT SEPARATED FROM THE AIR ACCORDING TO CED
Compliance with standards:
- Certificate on checking the correctness and Declaration on Compliance with European directives with aim to mark CE products;
- Certificate EUROVENT .
Construction and installation:
Precise air conditioners with direct expansion, the structure of galvanized steel sheet, attached with rivets with double side coating to ensure a higher compressive strength. Tamping is envisaged with the units (space compressor).
The front panel is installed on the seals to allow easier access; can be opened by acting on the rapid closing lock. Rear panel and side panels are screwed behind supporter. You can access the section of the compressor during operation of the unit, removing front panel and protective tamping. The panels are coated on the inside with the thermal and acoustic insulation material class 1, according to UNI 8457/9174. Main characteristics:
Ventilation
Centrifugal fans, statistically and dynamically balanced with individual suction propeller with blades tilted back (BCF) of aluminum and with directly coupled electric motor;
coils section
The cold coil high front surface of copper pipes and aluminum blades, treated with a protective hydrophilic resins against bacterial growth, low loss and high SHR ("Sensible Heat Ratio" The ratio sensitive to heat), with a stainless bowl with flexible pipe for drainage of condensation;
Compressors
Compressors type Scroll, Copeland, high COP, high MTBF ("Mean Time Between Failure" Mean Time Between Failures), with incorporated thermal protection and non-vibrating supporters with low noise emission, the degree of protection IP54, with internal thermal protection, low starting current (equalizing internal pressure), eco compatible refrigerant fluid R410a.
filter section
Standard filters Filter-type "box" installed in the interior of the device, always above the body ventilation and thermic exchange. The degree of filtration G4 (CEN EN 779, which corresponds to the EU4 Eurovent EU4 / 5). Pleated filter structure allows high efficiency filtration and low loss of cargo. The used filtering material is in the form of a cell type of synthetic fibers. The structure is made of cardboard
electric control panel
Made in accordance with CEI standards . Located on the front of the space isolated from the flow of air and covered with sump to protect the parts that are supplied with voltage higher than 24V . Units are set for operation on : 230/1/50 or 400 V/3/50 Hz + N + T depending on the model . Thermal-magnetic circuit switchers are supplied with the protection of any electrical components . It is designed for single-phase transformer supplying power to the secondary circuit on 24 V. General switch with the handle to block the door is installed serial on safety sump to prevent its removal when the switch is in the position of operating. Models are run automatically after a possible delay due to lack of power supply and additional discipline for running remotely and restore some operating conditions (fans and compressors) or connect additional devices ( Liquistat , Firestat , Smokestat , clogged filters) , which are prepared in a serial terminal head of electrical control panel.
Control with microprocessor
Temperature control with a microprocessor Ico, with a 3D card on the edge of the device. A detailed description on multiple languages of operating parameters and alarms, memorizing environment parameters for the last 16 days, and the list of the last 400 events that have occurred in the system. Using protection in the form of code, allows switching on and off the unit, visualization and programming operating parameters and alarms, calibration sensors. Main functions: stand-by (automatic start of another unit in case that the first one breaks or that thermal burden exceeds the capacity of one unit), daily automatic rotation, scale (load distribution across multiple units over the division of the proportional band). Networking via ethernet network, compound Y-shaped, requires a fixed IP address. Monitoring: connecting to an ethernet network to a PC makes it possible to show working condition of the units; if an access to IP address is provided from the outside, it is possible to show through Internet working condition of the units.
Extensive connectivity to external BMS on protocols (with the serial card, if desired):
integrited on card RS485
- BACnet
- LONworks
- Metasys
- TREND
- SNMP
- TCP/IP
One back-up battery allows the maintainance of data recording system and an alarm after a power failure. In addition, it also provides local monitoring of the system (up to 32 units connected to the network), over various options of protocol convertor (Hirolink), which allows connection to various monitoring systems, MODBUS etc..
Air-cooled condenser for remote installation with the following characteristics:
Single-mode power supply 230V/50Hz; increased version for high outdoor temperature ( t= 45° C ).
The structure of the sheet of aluminum-magnesium with movable protection on the sides of terminal head and cooling connections, also with legs for support and with a frame;
Aluminum-copper battery with one circuit tested in a pressure of 30 bar and supplied at a pressure of 2 bar.
Axial electric fans with 4 poles with external rotor. Engines made in accordance with VDE 0530/11.72 with protection level IP44 and insulation class F. The protective grids painted with paint against corrosion and designed in accordance with safety standards DIN 31001. Electrical connection between the fan and the terminal head IP55 implemented with electric cables for external insulation. The main switch IP65. With: Manostat for condensation control with adjustable fan speed. Equipment installation with vertical air flow. Connections for gas.
Pre-insulated copper pipes for curcuit of cooling gas R410a for remote connection of condensors- internal precise air-conditioning, including the filling with cooling gas project and all its special reinforcement
Supporting frame for installation on floating floor ;
Exhaust grid at the top of the unit;
Fan speed regulator;
VARICOND pressure control of condensation;
checking the correctness of the devices by a company for supply;
switches for operating and maintainance, installed at a distance of less than 3 meters for each unit, either internal or external.
Additional parts such as spare filters, various holders and supporters, hydraulic connections, condensation discharge, electrical connections, miscellaneous consumable material, and smaller parts for the completeness of the device and its operation according to current regulations.
Monoblock unit for indoor installation and underfloor conditioning - cooling capacity: tot/sens 7/6.5 kW
| GROUND FLOOR LEVEL - AIR CONDITIONING |  | 2
| Total amount |  | 2
TOTAL CONDITIONING DEVICES AND SYSTEMS
TI | AIR TREATMENT DEVICES
TI.120.A1 | CENTRAL FOR PROCESSING AIR - AIR CHAMBER WITH SECTIONS THAT CAN BE PUT TOGETHER; EXTERNAL EXECUTION; COATING 40 mm (MINIMUM) PERALUMAN - PERALUMAN ; SIDE TECHNICAL AREA ; ELECTRICAL AND REGULATING DEVICE ON THE EDGE OF THE DEVICE | each
CENTRAL FOR PROCESSING AIR - AIR CHAMBER WITH SECTIONS THAT CAN BE PUT TOGETHER; EXTERNAL EXECUTION; COATING 40 mm (MINIMUM) PERALUMAN - PERALUMAN ; SIDE TECHNICAL AREA ; ELECTRICAL AND REGULATING DEVICE ON THE EDGE OF THE DEVICE Compliance with standards: UNI EN 1886 ; UNI EN 13,053 Construction and installation in accordance with the indications in the specification and / or other documents of a project here briefly summarized : - The structure of aluminum profiles with thermal cutting and sandwich plate panels of internal Peraluman - mineral or glass wool apretirana 40 mm (minimum ) with a density of not less than 60 kg / mc (or other material , upon approval of the company ) - Peraluman outer sheet ; screws entirely of stainless steel ; Side technical area of the door which can be opened to restrict the additional components , made ​​in the same manner as the structure ; exterior painting panel is optional (optional company ) but in any case included in price; - Class minimal mechanical resistance tread : D2 ( R) ; - Class of sealing air L2 , either parts of decompression or pressure filter from G1 to F9 ; L1 filter larger than F9 ; - Thermal class : T2 ; - Class of thermal bridges : TB2 ; - Index estimates Rw sound leakage Wall : 30 dB ; - Removable battery of copper - aluminum ; - Class of by -pass filter 1% filter from G1 to F8 ; 0.5 % greater than for filters F8 ; - Small roof for protection from rain ; - Side- technical space with doors that open structure analogous to that of plants, to limit electrical appliances , regulating devices , valves , etc. . ; - Electrical control panel for power and command - control - setup ; control devices ( Servo valves with actuator , sensors, transmitters, etc. . ) and regulating electric cabling , all to the edge of the device ; - Thermometers for air ( inert gas , and the capillary ) to the lower part of each section of the processing for each channel and the entry-exit device ; - Thermometers Water ( for inert gases and globe thermometer ) at each terminal of the battery ; - Pressure gauges with three connectors and valves to stop the water in each battery ; - A number of spare filters ; - Metal plates with all the main data device ; - Power supply voltage 400 V ( + / -10 % ) ; - Frequency of 50 Hz . Price includes: - parts for assembly thereto; - A variety of mounts , mounts , supports; - Electrical connections and hydraulic and air connectivity ; - Various supplies .
AHU1, see drawing 926_Te_001 for details
| SECOND FLOOR LEVEL - VENTILATION |  | 1
| Total amount |  | 1
TI.120.A2 | CENTRAL FOR PROCESSING AIR - AIR CHAMBER WITH SECTIONS THAT CAN BE PUT TOGETHER; EXTERNAL EXECUTION; COATING 40 mm (MINIMUM) PERALUMAN - PERALUMAN ; SIDE TECHNICAL AREA ; ELECTRICAL AND REGULATING DEVICE ON THE EDGE OF THE DEVICE | each
CENTRAL FOR PROCESSING AIR - AIR CHAMBER WITH SECTIONS THAT CAN BE PUT TOGETHER; EXTERNAL EXECUTION; COATING 40 mm (MINIMUM) PERALUMAN - PERALUMAN ; SIDE TECHNICAL AREA ; ELECTRICAL AND REGULATING DEVICE ON THE EDGE OF THE DEVICE Compliance with standards: UNI EN 1886 ; UNI EN 13,053 Construction and installation in accordance with the indications in the specification and / or other documents of a project here briefly summarized : - The structure of aluminum profiles with thermal cutting and sandwich plate panels of internal Peraluman - mineral or glass wool apretirana 40 mm (minimum ) with a density of not less than 60 kg / mc (or other material , upon approval of the company ) - Peraluman outer sheet ; screws entirely of stainless steel ; Side technical area of the door which can be opened to restrict the additional components , made ​​in the same manner as the structure ; exterior painting panel is optional (optional company ) but in any case included in price; - Class minimal mechanical resistance tread : D2 ( R) ; - Class of sealing air L2 , either parts of decompression or pressure filter from G1 to F9 ; L1 filter larger than F9 ; - Thermal class : T2 ; - Class of thermal bridges : TB2 ; - Index estimates Rw sound leakage Wall : 30 dB ; - Removable battery of copper - aluminum ; - Class of by -pass filter 1% filter from G1 to F8 ; 0.5 % greater than for filters F8 ; - Small roof for protection from rain ; - Side- technical space with doors that open structure analogous to that of plants, to limit electrical appliances , regulating devices , valves , etc. . ; - Electrical control panel for power and command - control - setup ; control devices ( Servo valves with actuator , sensors, transmitters, etc. . ) and regulating electric cabling , all to the edge of the device ; - Thermometers for air ( inert gas , and the capillary ) to the lower part of each section of the processing for each channel and the entry-exit device ; - Thermometers Water ( for inert gases and globe thermometer ) at each terminal of the battery ; - Pressure gauges with three connectors and valves to stop the water in each battery ; - A number of spare filters ; - Metal plates with all the main data device ; - Power supply voltage 400 V ( + / -10 % ) ; - Frequency of 50 Hz . Price includes: - parts for assembly thereto; - A variety of mounts , mounts , supports; - Electrical connections and hydraulic and air connectivity ; - Various supplies .
AHU2, see drawing 926_Te_001 for details
| ROOF LEVEL - VENTILATION |  | 1
| Total amount |  | 1
TI.120.A3 | CENTRAL FOR PROCESSING AIR - AIR CHAMBER WITH SECTIONS THAT CAN BE PUT TOGETHER; EXTERNAL EXECUTION; COATING 40 mm (MINIMUM) PERALUMAN - PERALUMAN ; SIDE TECHNICAL AREA ; ELECTRICAL AND REGULATING DEVICE ON THE EDGE OF THE DEVICE | each
CENTRAL FOR PROCESSING AIR - AIR CHAMBER WITH SECTIONS THAT CAN BE PUT TOGETHER; EXTERNAL EXECUTION; COATING 40 mm (MINIMUM) PERALUMAN - PERALUMAN ; SIDE TECHNICAL AREA ; ELECTRICAL AND REGULATING DEVICE ON THE EDGE OF THE DEVICE Compliance with standards: UNI EN 1886 ; UNI EN 13,053 Construction and installation in accordance with the indications in the specification and / or other documents of a project here briefly summarized : - The structure of aluminum profiles with thermal cutting and sandwich plate panels of internal Peraluman - mineral or glass wool apretirana 40 mm (minimum ) with a density of not less than 60 kg / mc (or other material , upon approval of the company ) - Peraluman outer sheet ; screws entirely of stainless steel ; Side technical area of the door which can be opened to restrict the additional components , made ​​in the same manner as the structure ; exterior painting panel is optional (optional company ) but in any case included in price; - Class minimal mechanical resistance tread : D2 ( R) ; - Class of sealing air L2 , either parts of decompression or pressure filter from G1 to F9 ; L1 filter larger than F9 ; - Thermal class : T2 ; - Class of thermal bridges : TB2 ; - Index estimates Rw sound leakage Wall : 30 dB ; - Removable battery of copper - aluminum ; - Class of by -pass filter 1% filter from G1 to F8 ; 0.5 % greater than for filters F8 ; - Small roof for protection from rain ; - Side- technical space with doors that open structure analogous to that of plants, to limit electrical appliances , regulating devices , valves , etc. . ; - Electrical control panel for power and command - control - setup ; control devices ( Servo valves with actuator , sensors, transmitters, etc. . ) and regulating electric cabling , all to the edge of the device ; - Thermometers for air ( inert gas , and the capillary ) to the lower part of each section of the processing for each channel and the entry-exit device ; - Thermometers Water ( for inert gases and globe thermometer ) at each terminal of the battery ; - Pressure gauges with three connectors and valves to stop the water in each battery ; - A number of spare filters ; - Metal plates with all the main data device ; - Power supply voltage 400 V ( + / -10 % ) ; - Frequency of 50 Hz . Price includes: - parts for assembly thereto; - A variety of mounts , mounts , supports; - Electrical connections and hydraulic and air connectivity ; - Various supplies .
AHU3, see drawing 926_Te_001 for details
| SECOND FLOOR LEVEL - VENTILATION |  | 1
| Total amount |  | 1
TI.120.A4 | CENTRAL FOR PROCESSING AIR - AIR CHAMBER WITH SECTIONS THAT CAN BE PUT TOGETHER; EXTERNAL EXECUTION; COATING 40 mm (MINIMUM) PERALUMAN - PERALUMAN ; SIDE TECHNICAL AREA ; ELECTRICAL AND REGULATING DEVICE ON THE EDGE OF THE DEVICE | each
CENTRAL FOR PROCESSING AIR - AIR CHAMBER WITH SECTIONS THAT CAN BE PUT TOGETHER; EXTERNAL EXECUTION; COATING 40 mm (MINIMUM) PERALUMAN - PERALUMAN ; SIDE TECHNICAL AREA ; ELECTRICAL AND REGULATING DEVICE ON THE EDGE OF THE DEVICE Compliance with standards: UNI EN 1886 ; UNI EN 13,053 Construction and installation in accordance with the indications in the specification and / or other documents of a project here briefly summarized : - The structure of aluminum profiles with thermal cutting and sandwich plate panels of internal Peraluman - mineral or glass wool apretirana 40 mm (minimum ) with a density of not less than 60 kg / mc (or other material , upon approval of the company ) - Peraluman outer sheet ; screws entirely of stainless steel ; Side technical area of the door which can be opened to restrict the additional components , made ​​in the same manner as the structure ; exterior painting panel is optional (optional company ) but in any case included in price; - Class minimal mechanical resistance tread : D2 ( R) ; - Class of sealing air L2 , either parts of decompression or pressure filter from G1 to F9 ; L1 filter larger than F9 ; - Thermal class : T2 ; - Class of thermal bridges : TB2 ; - Index estimates Rw sound leakage Wall : 30 dB ; - Removable battery of copper - aluminum ; - Class of by -pass filter 1% filter from G1 to F8 ; 0.5 % greater than for filters F8 ; - Small roof for protection from rain ; - Side- technical space with doors that open structure analogous to that of plants, to limit electrical appliances , regulating devices , valves , etc. . ; - Electrical control panel for power and command - control - setup ; control devices ( Servo valves with actuator , sensors, transmitters, etc. . ) and regulating electric cabling , all to the edge of the device ; - Thermometers for air ( inert gas , and the capillary ) to the lower part of each section of the processing for each channel and the entry-exit device ; - Thermometers Water ( for inert gases and globe thermometer ) at each terminal of the battery ; - Pressure gauges with three connectors and valves to stop the water in each battery ; - A number of spare filters ; - Metal plates with all the main data device ; - Power supply voltage 400 V ( + / -10 % ) ; - Frequency of 50 Hz . Price includes: - parts for assembly thereto; - A variety of mounts , mounts , supports; - Electrical connections and hydraulic and air connectivity ; - Various supplies .
AHU4, see drawing 926_Te_001 for details
| ROOF LEVEL - VENTILATION |  | 1
| Total amount |  | 1
TI.120.A5 | CENTRAL FOR PROCESSING AIR - AIR CHAMBER WITH SECTIONS THAT CAN BE PUT TOGETHER; EXTERNAL EXECUTION; COATING 40 mm (MINIMUM) PERALUMAN - PERALUMAN ; SIDE TECHNICAL AREA ; ELECTRICAL AND REGULATING DEVICE ON THE EDGE OF THE DEVICE | each
CENTRAL FOR PROCESSING AIR - AIR CHAMBER WITH SECTIONS THAT CAN BE PUT TOGETHER; EXTERNAL EXECUTION; COATING 40 mm (MINIMUM) PERALUMAN - PERALUMAN ; SIDE TECHNICAL AREA ; ELECTRICAL AND REGULATING DEVICE ON THE EDGE OF THE DEVICE Compliance with standards: UNI EN 1886 ; UNI EN 13,053 Construction and installation in accordance with the indications in the specification and / or other documents of a project here briefly summarized : - The structure of aluminum profiles with thermal cutting and sandwich plate panels of internal Peraluman - mineral or glass wool apretirana 40 mm (minimum ) with a density of not less than 60 kg / mc (or other material , upon approval of the company ) - Peraluman outer sheet ; screws entirely of stainless steel ; Side technical area of the door which can be opened to restrict the additional components , made ​​in the same manner as the structure ; exterior painting panel is optional (optional company ) but in any case included in price; - Class minimal mechanical resistance tread : D2 ( R) ; - Class of sealing air L2 , either parts of decompression or pressure filter from G1 to F9 ; L1 filter larger than F9 ; - Thermal class : T2 ; - Class of thermal bridges : TB2 ; - Index estimates Rw sound leakage Wall : 30 dB ; - Removable battery of copper - aluminum ; - Class of by -pass filter 1% filter from G1 to F8 ; 0.5 % greater than for filters F8 ; - Small roof for protection from rain ; - Side- technical space with doors that open structure analogous to that of plants, to limit electrical appliances , regulating devices , valves , etc. . ; - Electrical control panel for power and command - control - setup ; control devices ( Servo valves with actuator , sensors, transmitters, etc. . ) and regulating electric cabling , all to the edge of the device ; - Thermometers for air ( inert gas , and the capillary ) to the lower part of each section of the processing for each channel and the entry-exit device ; - Thermometers Water ( for inert gases and globe thermometer ) at each terminal of the battery ; - Pressure gauges with three connectors and valves to stop the water in each battery ; - A number of spare filters ; - Metal plates with all the main data device ; - Power supply voltage 400 V ( + / -10 % ) ; - Frequency of 50 Hz . Price includes: - parts for assembly thereto; - A variety of mounts , mounts , supports; - Electrical connections and hydraulic and air connectivity ; - Various supplies .
AHU5, see drawing 926_Te_001 for details
| SECOND FLOOR LEVEL - VENTILATION |  | 1
| Total amount |  | 1
TI.120.A6 | CENTRAL FOR PROCESSING AIR - AIR CHAMBER WITH SECTIONS THAT CAN BE PUT TOGETHER; EXTERNAL EXECUTION; COATING 40 mm (MINIMUM) PERALUMAN - PERALUMAN ; SIDE TECHNICAL AREA ; ELECTRICAL AND REGULATING DEVICE ON THE EDGE OF THE DEVICE | each
CENTRAL FOR PROCESSING AIR - AIR CHAMBER WITH SECTIONS THAT CAN BE PUT TOGETHER; EXTERNAL EXECUTION; COATING 40 mm (MINIMUM) PERALUMAN - PERALUMAN ; SIDE TECHNICAL AREA ; ELECTRICAL AND REGULATING DEVICE ON THE EDGE OF THE DEVICE Compliance with standards: UNI EN 1886 ; UNI EN 13,053 Construction and installation in accordance with the indications in the specification and / or other documents of a project here briefly summarized : - The structure of aluminum profiles with thermal cutting and sandwich plate panels of internal Peraluman - mineral or glass wool apretirana 40 mm (minimum ) with a density of not less than 60 kg / mc (or other material , upon approval of the company ) - Peraluman outer sheet ; screws entirely of stainless steel ; Side technical area of the door which can be opened to restrict the additional components , made ​​in the same manner as the structure ; exterior painting panel is optional (optional company ) but in any case included in price; - Class minimal mechanical resistance tread : D2 ( R) ; - Class of sealing air L2 , either parts of decompression or pressure filter from G1 to F9 ; L1 filter larger than F9 ; - Thermal class : T2 ; - Class of thermal bridges : TB2 ; - Index estimates Rw sound leakage Wall : 30 dB ; - Removable battery of copper - aluminum ; - Class of by -pass filter 1% filter from G1 to F8 ; 0.5 % greater than for filters F8 ; - Small roof for protection from rain ; - Side- technical space with doors that open structure analogous to that of plants, to limit electrical appliances , regulating devices , valves , etc. . ; - Electrical control panel for power and command - control - setup ; control devices ( Servo valves with actuator , sensors, transmitters, etc. . ) and regulating electric cabling , all to the edge of the device ; - Thermometers for air ( inert gas , and the capillary ) to the lower part of each section of the processing for each channel and the entry-exit device ; - Thermometers Water ( for inert gases and globe thermometer ) at each terminal of the battery ; - Pressure gauges with three connectors and valves to stop the water in each battery ; - A number of spare filters ; - Metal plates with all the main data device ; - Power supply voltage 400 V ( + / -10 % ) ; - Frequency of 50 Hz . Price includes: - parts for assembly thereto; - A variety of mounts , mounts , supports; - Electrical connections and hydraulic and air connectivity ; - Various supplies .
AHU6, see drawing 926_Te_001 for details
| SECOND FLOOR LEVEL - VENTILATION |  | 1
| Total amount |  | 1
TOTAL AIR TREATMENT DEVICES
TOTAL THERMOTECH - GROUND FLOOR AND UPPER FLOOR LEVELS
TOTAL THERMOTECH