Construction of Sewage Network and Waste Water Treatment Plant (WWTP) in the Municipality of Berane

Volume 3-1 Employer’s Requirements

Section 2 Particular Design and Process Requirements

June 2015

# Table of Contents

1	PROJECT DESCRIPTION AND SCOPE	12

1.1	Project Background	12

1.2	Project Objective	12

1.3	Contracting Authority	13

1.4	WWTP Location and Prevailing Site Conditions	13

1.4.1	WWTP Location	13

1.4.2	Site Topography	14

1.4.3	Site Geology and Seismicity	14

1.4.4	Climate	16

1.4.5	Existing Utilities	19

1.5	Existing Sewerage & Water Supply Systems	19

1.5.1	Water Supply	19

1.5.2	Sewerage	20

1.6	Wastewater Disposal Concept	20

1.7	WWTP Treatment Capacities	22

1.8	Scope of Works	22

1.9	Outline Programme for Execution of Works	29

2	TENDER DESIGN	30

2.1	General	30

2.2	CONTENT OF TENDER DESIGN	30

3	DOCUMENTS TO BE SUBMITTED BY THE CONTRACTOR	31

3.1	Work Programme	31

3.2	Reports on Additional Investigation Works	33

3.2.1	Topography	33

3.2.2	Levels and Benchmarks	33

3.2.3	Setting out of the Works	33

3.2.4	Geotechnical Investigations	34

3.2.5	Existing Utility and Other Services or Buried Structures	35

3.3	Design Documentation	35

3.3.1	General	35

3.3.2	Detailed Design (Glavni projekat)	36

3.4	Start-up, Operation & Maintenance Manual	38

3.5	As-Built Documents	39

3.6	Materials Safety Data Sheet	40

3.7	Submission and Approval of Contractor’s Documents	40

3.7.1	Procedures for Submission and Approval of Detailed Design and other Contractor’s Documents	40

3.7.2	Detailed Design Approval and Review	40

3.7.3	Schedule for submission of Documents	41

4	GENERAL DESIGN REQUIREMENTS	45

4.1	General	45

4.2	Design horizons and wastewater flows and loads	45

4.2.1	Design Horizons	45

4.2.2	Hydraulic and Pollutant Loads	46

4.3	Technical Conditions for Design and Construction of WWTP	47

4.4	Minimum Design Life	48

4.5	Design and Construction Standards and Codes	49

4.6	General Layout	50

4.7	Requirements for Operation Stability and Reliability	50

4.8	Requirements for Operation and Maintenance	51

4.9	Hydraulic Design Requirements	52

4.10	Pipe-work	52

4.11	Force Mains	53

4.12	Road, Water Course and other Utility Crossings	53

4.13	Noise Emission Standards	53

4.14	Flow Measurement and Control	53

4.15	Discharge of Effluent	53

5	PROCESS AND MECHANICAL DESIGN REQUIREMENTS	54

5.1	General	54

5.2	Description of Works	55

5.3	Basic Design Criteria	55

5.3.1	Population Equivalent	55

5.3.2	Design Flows	56

5.3.3	Effluent Quality Standards	57

5.4	WWTP Facilities	58

5.4.1	Inlet chamber	58

5.4.2	Coarse screens	60

5.4.3	Lifting Pumping station	61

5.4.4	Fine Screens	62

5.4.5	Aerated Grit Chamber	64

5.4.6	Influent Flow and Quality Measurement	66

5.4.7	Equalization Tank	66

5.4.8	SBR Feeding Pumping Station	67

5.4.9	Biological Treatment Processes	68

5.4.10	Blower Station	72

5.4.11	Effluent Sampling	72

5.4.12	Effluent discharge pipeline	72

5.4.13	Sludge BufferTank	73

5.4.14	Sludge Thickening	73

5.4.15	Septic Sludge Reception Station	75

5.4.16	Sludge Dewatering	75

5.4.17	Odour Control Plant	77

5.4.18	Hazardous Area Study	78

5.4.19	Vehicles and Miscellaneous Operational Equipment	78

5.5	Process guarantee	78

5.5.1	Introduction	78

5.5.2	Definitions	78

5.5.3	Process Guarantee Conditions	79

5.5.4	Guaranteed Operational Costs	81

6	ELECTRICAL, INSTRUMENTATION AND CONTROL DESIGN REQUIREMENTS	85

6.1	Scope of Works	85

6.2	MV Power Supply	85

6.3	Transformer Station	86

6.3.1	MV Switchgear	86

6.3.2	Power transformer	87

6.3.3	Bus bar System	88

6.3.4	Main LV distribution board	88

6.3.5	Reactive power compensation	89

6.4	Standby power supply	89

6.5	Electrical Distribution System	89

6.6	Motor Control Centres	90

6.7	Outdoor lighting	90

6.8	Earthing System	90

6.9	Lightning Protection	91

6.10	Package Plant	91

6.11	Building Services	92

6.11.1	General	92

6.11.2	Internal Lighting	93

6.11.3	Heating Ventilation and Air conditioning (HVAC)	93

6.11.4	Small Power	93

6.11.5	Computer home network	93

6.11.6	Telephone installation	93

6.11.7	Fire Detection and Alarms	93

6.11.8	Intruder Alarms	94

6.12	Instrumentation	94

6.13	Control Philosophy	94

6.13.1	General	94

6.13.2	Automatic Operation	95

6.13.3	Manual Operation	95

6.13.4	Duty and Standby Control	95

6.14	SCADA System	95

6.14.1	System Overview	95

6.14.2	Signals	96

6.14.3	SCADA System Requirements	96

6.14.4	Scope of Work	96

6.15	Plant Maintenance Software	97

6.16	Telecommunication	98

6.16.1	Telecommunication Connection	98

6.16.2	WWTP Telecommunication infrastructure	98

7	CIVIL ENGINEERING DESIGN REQUIREMENTS	98

7.1	General	98

7.2	Flood protection	99

7.2.1	General description	99

7.2.2	Geotechnical requirements for WWTP Plateau Construction	100

7.3	WWTP	103

7.3.1	Administration and Control Building	104

7.3.2	Workshop and Stores Building	109

7.3.3	Waste Materials Storage	110

7.3.4	Wash water System	110

8	ROADS DESIGN AND LANDSCAPING REQUIREMENTS	111

8.1	Main Access Road	111

8.2	Internal Site Roads and Car Parking	111

8.3	Perimeter Fencing and Entrance Gates	111

8.4	Flood Protection to WWTP Site	112

8.5	Exterior Lighting	112

8.6	Landscaping and Green Belt Setting	112

8.7	Signs	112

9	COMMISSIONING AND TESTING	113

9.1	General	113

9.2	Inspection and Testing during Manufacturing	114

9.3	Quality Control and Testing during Construction	114

9.3.1	Responsibilities and Procedures	114

9.3.2	Quality Control Plan	115

9.3.3	Material Samples and Testing	115

9.3.4	Site Records and Test Certificates	116

9.3.5	Reports on Tests & Inspections	116

9.4	Tests on Completion	116

9.4.1	General	116

9.4.2	Instruments, Materials and Consumables for Testing	118

9.4.3	Functional “Dry” Tests of Equipment	118

9.4.4	Hydraulic Tests	118

9.4.5	Start-up and WWTP Performance Testing	119

9.4.6	Performance Testing of Particular Equipment	121

9.4.7	Performance Testing of Sub-Systems	122

9.5	Tests after Completion	123

9.5.1	General	123

10	PLANT OPERATION AND TRAINING	124

10.1	Plant operation	124

10.2	Plant Attendance/Manning Requirements	124

10.3	Training	124

10.3.1	Training Programme	125

10.3.2	Execution of Training	127

10.3.3	Contractor's Training Personnel	127

10.4	Operation and Maintenance Manual	127

10.5	Process Monitoring	128

List of Tables

Table 1-1 Earthquake parameters	15

Table 1-2 Characteristic geotechnical model of the site GMT-5	15

Table 1-3 – Main seismic characteristics of the Project Area	15

Table 1-4  – Overview of the geotechnical characteristics of the WWTP site	16

Table 1-5 – Categorization of the receiving water course	21

Table 1-6 - Required effluent quality	21

Table 1-7- Plant Design Loads	22

Table 1-8- Design Flows	22

Table 1-9 – Documentation required for obtaining Building Permit	27

Table 1-10: Outline program of works	29

Table 3-1: Outline Work Programme - explanations	32

Table 3-2: Schedule of Documents to be submitted for Approval	41

Table 4-1:Phasing of the WWTP	45

Table 4-2: Typical hydraulic loadings for WWTP	46

Table 4-3: Typical pollutant loadings and concentrations for WWTP	47

Table 4-4: List of relevant technical conditions for design of WWTP	47

Table 4-5: Minimum Design Life	48

Table 5-1:  Population Equivalent Projections (rounded)	55

Table  5-2:  Selected Wastewater flows for the project horizons	56

Table 5-3: Design loads, concentrations, effluent standards	57

Table 5-4: Required effluent quality	57

Table 5-5: Physical features of the main sewer inlet into the WWTP inlet chamber	59

Table 5-6:  Coarse screens – basic design requirements	61

Table 5-7: Inlet Pumping Station – basic design criteria	62

Table 5-8: Design parameters for fine screen block	63

Table 5-9: Design Criteria for Aerated Grit Chamber	64

Table 5-10:  Flow measurement – basic design criteria	66

Table 5-11:  Equalization Tank – basic design criteria	67

Table 5-12: SBR Feeding Pumping Station – basic design criteria	67

Table 5-13:  Activated sludge process – basic design criteria	68

Table 5-14:  SBR – basic design criteria	70

Table 5-15:  Criteria for Phosphorous removal	70

Table 5-16:  Excess sludge pump – basic design criteria	71

Table 5-17:  Aeration system – basic design criteria	71

Table 5-18:  Waste Sludge Storage Tank – basic design criteria	73

Table 5-19:  Sludge Thickening – basic design criteria	73

Table 5-20: Septage Sludge Reception Station – basic design criteria	75

Table 5-21:  Sludge Dewatering Facility – basic design criteria	76

Table 5-22:  Required Air exchange rates (ATV-M 204)	77

Table 5-23:  Vehicles for operation of WWTP	78

Table 5-24: Design Flow and Load Parameters for Process Guarantees	79

Table 5-25: Effluent Standards for Process Guarantees	80

Table 5-26: Sludge Treatment Requirements for Process Guarantees	80

Table 7-1: Requirements for the Administration and Control Building	104

Table 7-2: Furniture and Fittings for the Administration and Control Building	105

Table 7-3: List of Laboratory Equipment to be provided	106

Table 7-4: Requirements for the Workshop and Stores Building	109

Table 7-5: Indicative Equipment and Fittings for the Workshop and Stores Building	109

Table 10-1: List of process monitoring parameters	128

List of Figures

Figure 1-1 – General position of the WWTP Berane (Donji Talum location)	14

Figure 1-2 – Panoramic view of the WWTP location	14

Figure 1-3 – Seasonal variations of average air temperature in Berane	17

Figure 1-4 - Average rainfall graph for Berane	18

Figure 1-5 – Wind rose for Berane	18

Abbreviations

| % | shall mean | per cent |
| --- | --- | --- |
| AC | shall mean | Asbestos-cement |
| ASS | shall mean | Aerobic Sludge Stabilization Tank |
| ATV-DVWK | shall mean | German Association for the Water, Wastewater and Waste |
| BOD5 | shall mean | 5-day Biochemical Oxygen Demand |
| c | shall mean | Centre |
| CA | shall mean | Contracting Authority |
| CD | shall mean | Commencement Date |
| CESWI | shall mean | “Civil Engineer(Engineer(Engineer))ing Specification for the Water Industry”, 5th Edition” published by UKWIR Ltd., WRc plc, Franklin Road, Blagrove, Swindwon, Wiltshire, SN5 8YF |
| COD | shall mean | Chemical Oxygen Demand |
| Day | shall mean | Calendar Day |
| DD | shall mean | Detailed Design |
| DIN | shall mean | German Standard |
| DN | shall mean | nominal diameter |
| DNP | shall mean | Defects Notification Period |
| DO | shall mean | Dissolved Oxygen |
| TS | shall mean | Transformer Station |
| EIB | shall mean | European Investment Bank |
| EN | shall mean | European Standard |
| FM | shall mean | Flowmeter |
| GRP | shall mean | Glass Reinforced Plastic |
| h | shall mean | hour |
| HDPE | shall mean | High density extruded polyethylene |
| HVAC | shall mean | Heating, Ventilation and Air-conditioning |
| IPC | shall mean | Interim Payment Certificate |
| ISO | shall mean | International Standards Organization. |
| kg | shall mean | kilogram |
| km | shall mean | kilometre |
| kV | shall mean | kilo Volt (1000 Volts) |
| kW | shall mean | kilo Watt (1000 Watts) |
| l | shall mean | litre |
| LPU | shall mean | Lightning Protection Units |
| L.S. | shall mean | lump sum |
| m | shall mean | meter |
| m/d | shall mean | man-day |
| m² | shall mean | square meter |
| m³ | shall mean | cubic meter |
| m.a.s.l. | shall mean | Meters above sea level |
| M & E | shall mean | Mechanical and Electrical |
| MLSS | shall mean | Mixed Liquor Suspended Solids |
| mm | shall mean | millimetre |
| mm² | shall mean | square millimetre |
| Month | shall mean | 30/31 Calendar Days |
| MSDS | shall mean | Material Safety Data Sheet |
| MV | shall mean | Medium-voltage |
| O&M | shall mean | Operations & Maintenance |
| pcs | shall mean | pieces |
| PE | shall mean | Population Equivalent |
| P & I | shall mean | Process & Instrumentation |
| PLC | shall mean | Programmable Logic Control(ler) |
| PM | shall mean | Project Manager |
| PN | shall mean | Nominal Pressure |
| PROCON | shall mean | National Implementation Unit in the Field of Communal Infrastructure and Environment Protection |
| PUC | shall mean | Public Utility Company |
| PVC | shall mean | Polyvinyl chloride |
| QA | shall mean | Quality Assurance |
| QAS | shall mean | Quality Assurance System |
| QC | shall mean | Quality Control |
| RC | shall mean | Reinforced Concrete |
| RoM | shall mean | Republic of Montenegro |
| SBR | shall mean | Sequencing Batch Reactor |
| SCADA | shall mean | Supervisory Control and Data Acquisition |
| SDR | shall mean | Standard Dimension Ratio (pipe specification; ratio of diameter to wall thickness) |
| SVI | shall mean | Sludge Volume Index |
| t | shall mean | tone (1000 kg) |
| TA | shall mean | Technical Assistance |
| TKN | shall mean | Total Kjeldahl Nitrogen |
| TN | shall mean | Total Nitrogen |
| TP | shall mean | Total Phosphorous |
| TR | shall mean | Technical Requirements |
| TSS | shall mean | Total Suspended Solids |
| VFD | shall mean | Variable Frequency Drive |
| WAS | shall mean | Waste Activated Sludge |
| WP | shall mean | Work Programme |
| WWTP | shall mean | Wastewater Treatment Plant |

# PROJECT DESCRIPTION AND SCOPE

Project Background

The Municipality of Berane is one of the biggest towns in the north-east part of Montenegro. The town of Berane is located close to the border with the Republic of Serbia (around 30km to the north - east), Albania (50km to the south) and Kosovo (approximately 20km to the east). It is situated approximately 70 km north of Podgorica and 30km east of Kolašin. The Municipality, with its 5 surrounding settlements, has a population of around 35,000 inhabitants and a total surface area of 717km2. The population of around 11,000 is in the town of Berane itself. The town of Berane is the administrative, economic, cultural, educational and the religious centre of the municipality.

The sewerage system in Berane is designed as a separate system, i.e. rainwater and wastewater are collected and discharged separately. At present, there are some irregularities, and wastewater and stormwater drainage systems are cross-linked randomly. There are a few direct connections of stormwater drainage to the sewerage system but the lack of stormwater sewers in a number of streets leads to surface water entering the sewers through manholes. There is also considerable infiltration from springs and groundwater.

Within the overall Berane Wastewater Project it is planned to carry out extensive works on the sewerage network rehabilitation and extension. Two main sewers are to be built up to the planned WWTP location. One of the main sewers shall serve the area along the left bank of the Lim River, while the second main sewer shall serve the areas along the right bank of the Lim River. Both main sewers are supposed to operate by gravity and transfer collected communal wastewaters to the inlet lifting pumping station at the WWTP location.

Planned wastewater treatment facility is one of major components of the wastewater system. The wastewater collection system is planned to cover almost entire urban and suburban zone, and complete municipal wastewater is to be transferred to the future WWTP site.

Being one of key wastewater system components, the WWTP should provide effluent quality in accordance with the relevant environmental national and EU regulations, reducing pollution of surface and ground waters, reducing risks to public health and significantly improving wastewater collection and treatment services in the project area.

This Lot covers design preparation, equipment supply, construction and commissioning of the centralized WWTP for Berane (urban and suburban areas), including appurtenant infrastructural connections as specified hereinafter. It also comprises the Plant trial-run period of 6 months including staff training and one year of Defects Notification Period.

Project Objective

Main project objectives, specifically related to implementation of the WWTP in Berane, can be summarized as follows:

- Complete service coverage of the urban and suburban zones of Berane (Berane agglomeration) with contemporary communal wastewater treatment;

- Environmental protection by means of pollution reduction of the Lim River catchment, all downstream river catchments  and affected ground waters;

- Ensuring full compliance with the relevant national requirements related to urban wastewater treatment and disposal, compliance with the applicable EU regulations;

- Creating prerequisites for sustainable local and regional economic development;

- Improvement of operational capacities of the local PUC - system operator in the area of communal wastewater management

Contracting Authority

This contract will be procured in accordance with the PRAG2014, and the Contracting Authority is the Directorate of Public Works, Podgorica.

Being the owner of the existing water and sewerage systems assets the Municipality of Berane is the main beneficiary of the works to be implemented under the Contract.

Future operation and maintenance of the WWTP will be the responsibility of the local municipal PUC Vodovod i kanalizacija, Berane.

The PUC employs trained personnel with experience in constructing, maintaining and repairing of water supply and distribution systems, operation and maintenance of the sewerage systems. The Contractor is required to provide and execute comprehensive training program for the staff nominated by the beneficiaries for operation and maintenance of the works and equipment included in this contract. The purpose of the training is to provide nominated Operating Company staff with up-to-date knowledge of best practices and practical skills in operation of the concerned WWTP.

WWTP Location and Prevailing Site Conditions

### WWTP Location

Selected location for the WWTP in Berane is north of the town at the micro-location called Donji Talum, next to the Lim River and just off the main road Berane - Bijelo Polje.

The location has been defined/confirmed in the earlier reference documents. such as:

- Berane Wastewater Project, Feasibility Study, WYG International, 2010

- Spatial-urban Plan of the Municipality of Berane, Urbanprojekt-Mont, 2012

- Local Location Study for WWTP, Urbanprojekt-Mont, 2012WWTP Berane – Preliminary Design, AGRECO, 2013

General position of the plot planned for construction of the WWTP Berane is shown in Figure 1-1.

According to the relevant Urban-technical conditions reference No. 04-2472/1 of 16th October 2012 the location of the WWTP is situated in accordance with the Local Location Study in the area called Donji Talum, within the urban planning land plot No. UP1.

Proposed site surface area is 25.880 m2 (around 2,6ha) and it includes individual cadastral land plots 76, 38, 35, 31, 73, 75, 74, 34 and 24 which all belong to the cadastral zone  Dolac. The WWTP plot  is located on the left bank of the River Lim at 100-200m distance from the regional road M2 Bijelo Polje - Berane.

The site area is dominantly flat with elevations 658 - 660masl. The proposed WWTP site is app. 900m north from the centre of the Berane Town.

Figure 1-1 – General position of the WWTP Berane (Donji Talum location)

Road Berane – B.Polje

WWTP

site

Lim

River

### Site Topography

The site planned for the WWTP construction is within the alluvial zone of the Lim River. The site is characterized with rather flat topography, with natural ground elevations ranging from app. 658-660masl (please refer to Volume 5, DWG WWTP-03 – Topographic-cadastral Plan).

Notwithstanding the information presented, the Contractor shall carry out any supplementary topographic survey and data processing, as required for preparation of the designs and execution of works in accordance with this contract.

Figure 1-2 – Panoramic view of the WWTP location

### Site Geology and Seismicity

This section outlines basic geotechnical features of the selected WWTP in accordance with the information and documentation available.

Within the scope of WWTP Preliminary Design (2013) a Geotechnical Study of the proposed WWTP site was prepared.

According to the map of seismic micro-zoning of the urban area of the municipalities Berane and Andrijevica belong to zones C1 and N. The project area, between alluvium plain and the regional road belongs to zone C1, based on Quaternary sediments, whereas the area planned for construction of the WWTP belongs to zone N, with unstable surface comprised of sand dust of uniform grain size due to periodical floods and liquefaction.

The project area is characterized by seismicity magnitude of 8°, which correlates with static seismic analyses giving maximum momentum magnitude of 8.1° MCS within 100 year return period and probability of 63%.

The return period, magnitude and maximum expected acceleration of the basic rock (ao) is presented in the following table:

Table 1-1 Earthquake parameters

| Return period, years | Magnitude, MCS | Acceleration g |
| --- | --- | --- |
| 50 | 7.6 | 0.12 |
| 100 | 8.1 | 0.157 |
| 200 | 8.5 | 0.185 |

*(Source: Geotechnical Study, Preliminary Design of WWTP, 2013)

Characteristic geotechnical model of the site is presented in the following table:

Table 1-2 Characteristic geotechnical model of the site GMT-5

| H (m) | Vp (m/s) | Vs (m/s) | γ (kN/m3) | Composition |
| --- | --- | --- | --- | --- |
| 2.0 | 450 | 175 | 18.0 | Sand dust |
| 8.0 | 1000 | 380 | 19.0 | Sand and gravel |
|  | 2700 | 1250 | 24.5 | DRF |

*(Source: Geotechnical Study, Preliminary Design of WWTP, 2013)

Seizmic characteristics for construction within zone C1 for diferent return periods are presented in the following table.

Table 1-3 – Main seismic characteristics of the Project Area

| Typical Seismological zone | Return period (years) | Acceleration basic rocks ao (g) | Max. ground acceleration amax (g) | Seismic coefficient Ks |
| --- | --- | --- | --- | --- |
| C1 | 50 | 0.120 | 0.216 | 0.054 |
|  | 100 | 0.157 | 0.283 | 0.071 |
|  | 200 | 0.185 | 0.33 | 0.083 |

*(Source: Geotechnical Study, Preliminary Design of WWTP, 2013)

According to Geotechnical Study, the area of the site planned for construction of the WWTP is based on the Jurassic, Oligo-Miocene and Quaternary sediments and belongs to Lim tectonic suture.

Based on Geotechnical analyses the following geotechnical parameters are recommended for geo-static calculations:

Table 1-4  – Overview of the geotechnical characteristics of the WWTP site

| Geotechnical strata | Parameters |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | γ (kN/m3) | φ (°) | c (kN/m2) | Ms (kN/m2) | Qu (kN/m2) |
| Alluvium | 19 | 30 | 0 | 8000 | - |
| Diluvium | 19.5 | 24 | 10 | 4500 | - |
| Terrace | 20 | 28 | 10 | 6500 | - |
| Diabaig Formation | 23 | 30 | 80 | - | 1000 |
| Marl | 24 | 32 | 100 | - | 1500 |

The set of geotechnical investigations works were carried out at the planned WWTP location, which is summarised in the Geotechnical report attached in the Volume 5 of this tender.

The Contractor shall assess the adequacy, quality and applicability of the provided data/reports and carry out all necessary additional geotechnical investigations in accordance with the relevant national regulations and as necessary for completing the design and construction of all facilities included in this contract.

### Climate

The climate of Berane is dominantly continental with Mediterranean influences in small ravines and valleys, modified sub-mountainous in mid altitude zones and mountainous in the highest areas. The average annual temperature in Berane is 8.5°C, where the warmest months are July and August, while the coldest are December and January.

Figure 1-3 – Seasonal variations of average air temperature in Berane

The warmest month of the year is August with an average temperature of 19.8 °C. In January, the average temperature is -0.5 °C. It is the lowest average temperature of the whole year.

The average annual rainfall is 936.4l/m2. Precipitation is typically greater in spring and winter than in summer, peaking in November (maximal average temperature of 371l/m2). The average number of rainy days is 136.

Relative air humidity is usually high and ranges between 60-85% with the highest recorded in December – 86%.

In summer and early autumn higher temperatures and longer sunny spells result in increased levels of evaporation – it is higher than the rainfall. This leads to drying up of the soils. Summer rainfalls are rather low and do not have any significant effect on groundwater table, whereas heavier autumn rains cause an immediate sharp rises of water levels. Intensive winter and spring rainfalls produce high and long lasting annual maximum water discharges and groundwater levels. In addition to the rainfall, snowmelt in spring leads to flooding in large areas of the municipality. An average annual snow depth in the project area reaches 38.7cm annually.

Figure 1-4 - Average rainfall graph for Berane

With regard to winds at the project location strong winds are recorded 14 days annually on average, usually in November and December with wind intensity reaching in excess of 20 m/s. The highest average wind intensity is from the southwest (SW) direction, then from the south (S) and then from the northwest (NW). The following figure shows the rose of winds for the project location.

Figure 1-5 – Wind rose for Berane

Dominant wind directions in Berane are defined as follows:

- From the north - 14%

- From the north-east -12%

- From the south-west 10%

- From the south - 9%

- From the north-west - 7%

- From the south-east - 3%

- From the east - 3%

- From the west - 2%

- Periods with no wind - 41%

### Existing Utilities

- Based on the available information obtained from the Municipality of Berane, no utilities are present on the concerned WWTP site.

As a part of design preparation activities and in any case before any construction works on the site can start, the Contractor shall carry out detail survey of the site and shall detect/confirm exact status of the utilities. The Contractor shall compile official report on detection of the utilities and submit it to the Engineer for consideration. Based on the findings, the Engineer shall instruct the Contractor about further measures to be taken with that regard.

Existing Sewerage & Water Supply Systems

### Water Supply

Potable water supply of Berane is provided from the spring called Merica vrelo, which is located at the elevation of 960 masl. The raw water pipeline takes water from the intake chamber and conveys it by gravity to the break pressure tank at an elevation of 774masl, close to the town. Excess water from the spring overflows into the nearby creek.

The raw water pipeline DN 400mm starts at the intake chamber, after 590m it reduces to 350mm and after 550m to 300mm, and after 1290m to 250mm diameter. Measured flow in the pipeline is 174 l/s.

Raw water is compliant with the drinking water standards. However, periodic water quality analyses show occasional increase of turbidity due to snow melting or heavy rain.

Raw water is disinfected by chlorine in the brake pressure tank, from where it is distributed into the distribution network. The BPT provides sufficient contact time for chlorination. There are three pipes at the tank outlet, at different elevations, providing water supply for the Municipality.

At the moment there is no water supply to the WWTP site. According to conditions issued by PUC Vodovod i kanalizacija Berane 21.11.2014, the connection to the water supply system is technically possible on the pipe DN350 in the manhole in Dušana Vujoševića street, instead of the existing connections for settlements Šaćina Bara and Beranselo. Available pressure at the connection point is 5.3 to 5.5 bar.

The route of the new pipe overlaps the existing AC pipeline along 187m from the connection point to the division chamber, and further 80 m along the street M. Tomčića until the Hospital, where 143m of the pipeline should pass over the yard along the border fence of the Hospital. The existing AC pipeline is of diameter 100mm and should be replaced with  new one; of PE DN160 PN10.

The following 180m along the street D. Radevića  AC Ø100 shall also be replaced by HDPE DN160 PN10, while 590m until the bridge shall be replaced by HDPE DN110 PN10. The last 720m from the bridge until the WWTP site shall be constructed of HDPE DN110 PN10.

The Contractor shall construct app. 600m water supply pipeline PE DN160 PN10 and app.1300m pipeline PE DN110 PN10, including reconnection of the existing branch connections and the road reinstatement works.

For the aforesaid water supply connection to the town distribution network, the Contractor is supposed to prepare all necessary technical designs in accordance with relevant national regulations and implement/construct this connection as a part of the WWTP Berane project. Indicative general layout of the proposed water supply connection is attached in Volume 5 of this Tender.

The proposed route of the water supply line is defined by the final beneficiary and it goes dominantly through the paved areas.

### Sewerage

The existing wastewater collection system in Berane serves the entire town area including suburban settlements of Beran Selo, Dolac, Donje Luge and parts of Pesca. Currently, there are around 11.900 residents connected to the sewerage system. Communal wastewaters are discharged directly into the Lim River and its tributaries through 6 outfalls. Total length of the existing sewerage system is 19.8 km.

Within the overall Berane Wastewater Project, apart from the implementation of the WWTP, it is planned to carry out extensive upgrade and extension of the existing wastewater system. This sewerage extension is supposed to provide full service coverage in terms of wastewater collection in the town of Berane and neighbouring suburban areas. The system is to be implemented as fully separate, with two main sewers transferring collected wastewater to the WWTP, one of them serving the users along the left bank of the Lim River, while the other one shall collect and transfer wastewater in residential parts along the right bank of the Lim River.

The sewerage system with its extensions is planned as fully gravitational, i.e. no sewage pumping stations are envisaged in the system.

The left bank main sewer is of DN500, while the right bank main sewer is of DN400. Both main sewers are designed and shall be implemented by using GRP sewerage pipes.

With regard to the sewerage system configuration it should be noted that there is going to be river crossing under the Lim River of the right-bank main sewer towards the WWTP site.

As a result, depth of the abovementioned main sewers at the WWTP inlet is quite considerable, with pipe invert elevations of the main sewers designed as follows:

- Left bank main sewer – pipe invert elevation 657.16 masl

- Right bank main sewer – pipe invert elevation 655.77 masl

It should be noted that the natural ground elevation at the location of the planned WWTP inlet is 659.50masl, while the final elevated WWTP plateau elevation which shall ensure adequate flood protection is defined at 662.50masl.

With regard to planned implementation of the sewerage system upgrade and extension, the beneficiaries arranged for preparation of the corresponding detailed design in accordance with the national regulations. This detail design can be inspected, upon request, in the premises of the final beneficiaries – Municipality of Berane.

The most downstream inspection manhole of the right-bank and of the left-bank main sewers represents the upstream limit of works for the design and construction for the WWTP Contractor, i.e. for the works included in this tender.

Wastewater Disposal Concept

The recipient of treated effluent is the river Lim. The river Lim is the biggest tributary of the River Drina. It flows from the Lake Plavsko, through Andrijevica, Berane and Bijelo Polje in Montenegro, and further in Serbia through Prijepolje and Priboj until the confluence with the Drina River. The overall length of the Lim River is approximately 234 km.

Due to slope of the river bed in Berane sub-catchment, the Lim River is fast moving, torrential stream, with periodical (snow melting and heavy rain events) and sudden appearance of vast discharge in river bed with high concentration of hard phase that floods the lower land, including location in Talum where construction of WWTP is planned. Floods in Berane occur one average within 3-4 year return period.

In order to protect structures within the WWTP site, construction of the embankment along the site is foreseen, including removal of the existing surface layer of soil followed by backfilling with compacted gravel.

Regulation on Classification and Categorization of Surface and Groundwater (official Gazette of Montenegro 2/07) governs the classification and categorization of the surface and ground waters on the land and coastal sea waters in the Republic of Montenegro based on limit values of water quality parameters allowable for specific use of water.

In order to protect and improve water quality, the ground and surface bodies are divided into categories which fulfil the following conditions:

- I Category—fresh water class A1, S and K1, and sea water class Š

- II Category—classes A2, C and K2

- III Category—class A3, and others not included in this class and used for other purposes stated in this regulation.

According to the water quality which is to be maintained or provided in order to achieve good water status, the surface water bodies, depending on their ecological and chemical status and ecological potential, and the ground water bodies, depending on their quantity and chemical status, are divided into the following classes and categories:

Table 1-5 – Categorization of the receiving water course

| River / lake/ sea | Water body | Class | Category |
| --- | --- | --- | --- |
| Lim | Upstream of Berane | A1, S, K1 | I |
|  | From Berane to the Serbian border | A2, C, K2 | II |

Following Decision on water conditions no. 060-327/08-02011-154 from 12.10.2012, issued by Water Directorate based on articles 114 and 115 of Law on Water (official Gazette of Montenegro 27/07, 32/11 and 47/11), treated effluent shall comply with the national Regulations.

Since classification of sensitive areas in Montenegro is not established, class and category of the Lim River Lim upstream of Berane are followed as the guidance criteria for required treated effluent quality.

Therefore, in accordance with the By-Law on effluent quality and sanitary conditions for discharge of wastewater into natural water bodies and sewerage, methods and minimum number of wastewater quality analyses (official Gazette of Montenegro 45/08, 9/10 and 26/12) and EEC Directive 91/271, the wastewater treatment shall include biological treatment with nutrient removal.

Required effluent quality from the WWTP that can be discharged into the river Lim River is defined as follows:

Table 1-6 - Required effluent quality

| Parameter | Unit | Value |
| --- | --- | --- |
| BOD5 | mg O2/l | 25 |
| COD | mg O2/l | 125 |
| Total suspended solids | mg/l | 35 |
| Total Nitrogen (total organic plus inorganic) | mg/l | 15 |
| Total Phosphorous | mg/l | 2 |

WWTP Treatment Capacities

The Contractor is required to design the WWTP for the final capacity of 27,000 PE (Phase II), while Phase I of 20,000 PE shall be constructed within this contract.

Table 1-7- Plant Design Loads

| Design WWTP load | Unit | Phase I | Phase II |
| --- | --- | --- | --- |
| Population load | PE | 20,000 | 27,000 |
| BOD5 | kg /d | 1,200 | 1,620 |
| COD | kg /d | 2,400 | 3,240 |
| Suspended solids | kg /d | 1,400 | 1,890 |
| TKN | kg /d | 220 | 297 |
| Total Phosphorous | kg /d | 40 | 54 |

Table 1-8- Design Flows

| Design flow | Unit | Phase I | Phase II |
| --- | --- | --- | --- |
| Average daily Flow | m³/d | 4,559 | 5,704 |
| Peak dry weather flow | m³/h | 307 | 393 |
| Peak wet weather flow | m³/h | 613 | 786 |

Scope of Works

The Scope of the Works includes design (in accordance with the MNE Law on Spatial Planning and Construction, Official Gazette no. 51/08 and its amendments) and construction of the following elements:

- WWTP Berane, Detailed Design for the ultimate, Phase II capacity of 27.000 PE. Construction of the WWTP facilities, as defined herein.

  - All necessary Investigation Works (topographic survey, geotechnical, etc.);

  - Site grading and landscaping;

  - Treated effluent pipeline and outfall to the Lim River;

  - All WWTP process structures and inter-connecting pipelines;

  - Equipment supply, installation and testing;

  - Testing and commissioning of the WWTP;

  - Trial run of the WWTP during minimum 180 days;

  - Training and education of nominated operator’s staff at the WWTP-s in operation;

  - Defects Notification Period of one year upon completion of works.

- Flood protection and preparation/grading of the site from Lim River and Makva River waters, within the zone of the WWTP providing prescribed level of flood protection for the WWTP site and facilities

- Access road to the WWTP from the main road Berane – Bijelo Polje

- Water supply line from the main town distribution line to the WWTP site

- Power supply to the WWTP site

- Tele-communication line to the WWTP site

The WWTP will comprise wastewater treatment units and sludge handling facilities. WWTP should be designed and built to accept and treat municipal wastewater within the frame of defined design period, in accordance with the relevant Montenegrin and European regulations.

In the first implementation phase, included in the scope of this tender, the WWTP shall provide the complete wastewater treatment for the design load equal to 20,000 PE. The inlet pumping station, preliminary treatment, odour removal facilities, by-pass line, treated water line, outfall shall be constructed for capacity of the Phase II, while other facilities (biological and sludge treatment) shall be constructed for the capacity of the Phase I. All hydraulic structures, interconnections, distribution chambers, etc., and treatment units not suitable for later extension shall be both designed and constructed for the peak hydraulic load of the Phase II.

The wastewater treatment process shall be based on the activated sludge process with nutrients removal including aerobic sludge stabilization in accordance with the Tender requirements.

The recipient of treated effluent is the Lim River.

Construction of the Phase I comprises, but it is not limited to the following structures:

- Inlet chamber

- By-pass line including treated effluent line and outfall (for Phase II capacity)

- Coarse screens and lifting pumping station (for Phase II capacity)

- Buildings/structures for installation of preliminary treatment facilities sized for the capacity of the Phase II, including:

  - fine screens,

  - screenings washing and compaction facilities,

  - blowers for aeration of subsequent aerated grit chambers,

  - aerated grit chambers for grit and grease removal

  - grit classifier,

  - temporary storage containers

- Odour removal facilities, capacity of the Phase II

- Influent flow measurement and sampling

- Equalisation tank

- SBR feeding pumping station

- SBR for biological treatment including nutrient removal and aerobic sludge stabilization, capacity of the Phase I

- Blower Station

- Effluent flow measurement and sampling

- Excess sludge handling facilities including excess sludge extraction pumps, intermittently mixed balance tank, mechanical pre-thickening and sludge dewatering facilities including polymer preparation and dosing.

- Septic sludge reception facility

- Transformer Station

- Interface structures and facilities to be used in second stage

- Site stabilization, levelling all works related to flood protection

- Access, internal roads and landscaping

All structures where odorous air may be generated shall be covered and provided with air extraction equipment with sufficient air exchange rate, while odorous air shall be treated on the odour removal facility.

The following main buildings within the WWTP are to be foreseen:

- Preliminary treatment building

- Blowers station

- Sludge treatment building

- Transformer Station

- Administration & Control building with Laboratory

- Workshop and stores

- Parking place and vehicle washing area

- Guardhouse

In addition to the main works, there are a number of ancillary structures to be provided for full operation of the plant:

- Drainage system to facilitate tank emptying and general site drainage needs

- Associated pipe work and ancillary equipment connecting the various process units

- Access and internal road infrastructure

- Site drainage system

- External lighting

- Security system

- Site boundary fence and entrance gate

- Landscaping

- Miscellaneous, such as labelling panels, markers and similar.

Apart from the WWTP itself, the works and equipment to be implemented/installed at the site, the scope of this tender includes a number of elements that are necessary for normal finalisation and future safety, operation, maintenance and access to the WWTP Berane. These elements are the following:

- Flood protection and preparation/grading works from the Lim River and of the Makva River waters within the WWTP zone, as defined in the corresponding Preliminary Design, HydroGIS Podgorica, 2014

- Access road to the WWTP site from the main road Berane – Bijelo polje, as defined in the Preliminary Design, 2014

- Water supply line for the WWTP – water supply pipeline connecting the WWTP to the town distribution network

- Power supply to the WWTP site

- Tele-communication line for the WWTP

Site Flood Protection and Grading

The WWTP site is potentially endangered by flooding of both nearby water courses including the Lim River and the Makva River/Creek which intersects the site.

It is therefore necessary to elevate the WWTP plateau at the elevation that provides required level of flood protection as well as to carry out river regulation and banks stabilization works on the abovementioned water courses within the zone of WWTP site.

The WWTP shall be protected from the floods of 100-year recurrence interval, which is, in accordance with the Detailed Design of the Lim River regulation (2011) for this section 835 m3/s.

Along the Lim River section next to the WWTP – so-called section D, longitudinal grade of 3‰ (0.003), which is equivalent to the regulated grade adopted for the upstream section (Detailed design of 2011).

Regulated cross-section of the river is to be of trapezoidal form of 60m width and with slope of 20‰. For the embankments the slope of 1:2 is designed. The embankments are to be constructed along both river banks to the elevations defined in the Preliminary Design, providing required level of flood protection.

At the WWTP profile designed elevation of the embankment is 661.85masl, whereas the plateau of the WWTP itself is to be elevated to the elevation of 662.50 masl.

Further details regarding the river regulation and flood protection works are presented in Volume 5 of this tender.

At the moment the Makva River intersects the WWTP site and should be therefore relocated and regulated in order to ensure flood protection of the WWTP from this water course. The regulated water course is to be constructed just upstream of the WWTP plot with cross-sectional width of 8m, longitudinal slope of 5‰, while the slope of embankments is 1:2. Similarly to the Lim River regulation, the elevation of the embankments is to be at 661.85 masl.

In addition to the abovementioned flood protection works it is also necessary to protect the WWTP from waters that can be generated on the hilly terrains to the west of the WWTP. For that purpose, the canal encircling the WWTP site and discharging into the Lim River is to be constructed. Longitudinal slope of the canal is to be 6‰, the width of the cross section is 4m, while the designed side slope is 1:2. Similarly to the flood protection works described before, the design elevation of the embankment is set at 661.85 masl.

Access road to the WWTP

The WWTP location is situated in the alluvial plan next to the Lim River and 100-200m from the main road Berane – Bijelo Polje, M2. The location is also considerably lower (around 20m) compared to the elevation of the main road. At the moment, temporary access to the proposed WWTP site is provided via the local earthen road through the settlement of Gornji Talum, which is inadequate for long-term requirements of the WWTP.

The concept and requirements for the WWTP access road have been developed in the Preliminary Design of the access road to the WWTP Berane, within the scope of the Local Location Study “Donji Talum”. This design has been prepared based on the Urban-technical conditions ref. 07-351-514/1 of 26th September 2014, issued by the Municipality of Berane and based on the topographic survey results presented on a 1:250 layout map.

The access road is to be constructed from the main road Berane - Bijelo Polje M-2 to the WWTP plateau. The proposed solution of the access road enables its further extension (not within the scope of this tender), in accordance with the aforesaid Local Location Study.

In accordance with the proposed technical solution, the access road consists of two main sections:

- Section A – from the main road to the section B, 106.30m long including a horizontal bend of radius R=53m;

- Section B – from the section A to the WWTP, 281.16m long, including three horizontal bends of the following characteristics: R1=150m, R2=128m, R3=146.mm.

The technical solution includes the embankment of stone material, as well as removal of humus layer which is app. 0.5m thick.

At the PA-9 cross-section a circular culver of DN1.500 is to be constructed, which matches the existing culvert under the main road. At the PB-8 section there is going to be a box-culvert 1.0m x 1.8m aligned with the existing drainage canal route. The zone around the circular culvert should be reinforced by a support wall (from road chainage 0+089.13 to 0+097.63, i.e. 8.5m long)

Designed effective width of the road surface is 6m (2 travel lanes, 3m each), while width of the road shoulder strips on both are to be 1m each.

The road elevations have been conditioned by the elevations of the planned connections to the main road and to the WWTP plateau. Due to the significant difference of elevations of these two connection points, designed longitudinal slope of the access road is up to 10%. Except from the staring road section, cross-sectional slope of the access road should be 2.5%.

Longitudinal slopes of the section A are defined as follows: 2.48%, 2.06%, 2.11%, -9.49% and 2.50%.

Vertical bends of the section A are designed with the following radius: Rkv=-100m and Rkk=100m.

The following are longitudinal slopes of B section: -9.99% and -0.50%, while vertical bend of the same section is of the following radius Rkk=150m.

The access road structure has been defined as follows:

- Road wearing course -  of AB11,  4cm thick

- Road base-coarse (binder course) – of BNS22, 6 cm thick

- Road base – 30cm thick

Layout of the access road as well as typical sections are presented in Volume 5.

Water supply line for the WWTP

Since there is no potable water supply to the WWTP site, the Contractor shall design and construct adequate water supply line – connection of the WWTP site to the town water distribution network of adequate characteristics that shall satisfy all requirements for water supply of the WWTP.

Based on conditions issued by PUC, the connection to the water supply system is technically possible at the manhole around 1.900 m from the WWTP to the existing main distribution pipeline of DN350. Indicative technical characteristics of the planned supply line are given as follows: HDPE, OD160mm, PN10, L=600m and HDPE, OD110mm, PN10, L=1300m. Indicative normal working pressure at the connection point, as defined by the main beneficiary is 5.3-5.5bar.

For the aforesaid water supply connection to the town distribution network, the Contractor is supposed to prepare all necessary technical designs in accordance with relevant national regulations and implement/construct this connection as a part of the WWTP Berane project. Indicative general layout of the proposed water supply connection is attached in Volume 5 of this Tender.

The proposed route of the water supply line is defined by the final beneficiary and it goes dominantly through the paved areas.

Power supply to the WWTP site

Detail description considered in Chapter 6.2

Tele-communication line for the WWTP

Detail description considered in Chapter 6.16

The Contractor is required to carry out this Scope of Work, design and construction, fully in accordance with provisions of the relevant Legislation of the Republic of Montenegro.

As a prerequisite, the Contractor upon Contract award shall provide documentary on registration in the Central Registry of Montenegro, and certified licenses issued by the Engineers Chamber of Montenegro for each Engineer and legal entity involved in preparation of technical documentation (design documents), construction and installation works. Conditions and application forms for obtaining these Licences are given on the website of the Engineers Chamber of Montenegro (www.ingkomora.me).

As an illustration of the procedure, documentation required for obtaining of Building Permit, issuing authority and responsibilities in provision of documents is presented in the following table.

Table 1-9 – Documentation required for obtaining Building Permit

|  | Document | Normally issued by | To be provided by |
| --- | --- | --- | --- |
| 1 | Decision on Location and Urban technical condition | Ministry of sustainable development and tourism | Municipality Berane |
| 2 | Property ownership with copy of a plan | Directorate for real estate | Municipality Berane |
| 3 | Detailed design (Glavni projekat) | The Contractor | The Contractor |
| 4 | Decision on appointment of Technical control (review) of Detailed design | Municipality Berane | Municipality Berane |
| 5 | Record on completed Technical control of Detailed design | Municipality Berane | Municipality Berane |
| 6 | Excerpt from Central Registry of Montenegro | Central Registry of Montenegro | The Contractor |
| 7 | Licences for legal entity and personnel for preparation of technical documentation and execution of works | Engineers Chamber of Montenegro | The Contractor |
| 8 | Decision on appointment of the responsible engineers | The Contractor | The Contractor |
| 9 | Declaration on possession of Licences issued by Engineering Chamber of Montenegro for the engineers involved in preparation of technical documentation | The Contractor | The Contractor |
| 10 | Declaration on compliance of technical documentation with Urban technical conditions, ToR, regulations, technical norms and standards | The Contractor | The Contractor |
| 11 | Report on Geotechnical Investigation Works with opinion issued by Ministry of Economy | The Contractor | The Contractor |
| 12 | Compliance on conditions for: |  |  |
|  | - Electricity | PC Elektroprivreda Crne Gore | Municipality Berane/the Contractor |
|  | - Water supply | PUC Vodovod i kanalizacija | Municipality Berane/the Contractor |
|  | - Fire fighting | Ministry of police | Municipality Berane/the Contractor |
|  | - Environmental | Ministry of sustainable development and tourism | Municipality Berane/the Contractor |
|  | - Transport | Municipal department for transport | Municipality Berane/the Contractor |

The Contractor shall provide the final beneficiary with full technical assistance (background documentation, parts of supporting technical reports, graphical documentation, etc.) as required by the beneficiaries in the administrative procedures of applying to and acquiring the approvals and permits pertaining to the project.

No construction works will be allowed to commence on site prior to all the required permits being in place, especially the Building Permit. The Contractor is required to fully comply with the legal requirements and perform all works in accordance with the Legislation of the Republic of Montenegro.

Outline Programme for Execution of Works

As Stated in the Appendix to Tender, the Time for Completion of the Works (Design and Construction period including the trial run period) is limited to 30 months.

Upon completion of the Works, including plant start-up and successfully performed trial run, and issuance of the Taking Over Certificate approved by the Engineer (and finally Operation Permit issued by the Authorities), commences one-year Defect Notification Period. The Contractor shall provide technical support to the Beneficiary, during the DNP, as specified herein below.

The following Table indicates the duration of the major sequences/phases of the working program anticipated by the Contracting Authority. The Contractor shall produce his own Working Program for the Project implementation and shall be contractually fully responsible for compliance with the submitted Time Schedule.

Obligatory duration of some sequences/phases are presented in the Table, others are just indicative and do not oblige in any way the Contractor.

Table 1-10: Outline program of works

| No | Item description | Duration, months | Ending at: Commencement Date (CD)+ n months |
| --- | --- | --- | --- |
| 0 | Commencement date | 0 | 0 |
| 1 | Design Phase until provision of the Building Permit (overall including 1.1 - 1.6) | 8 months | CD + 8 months |
| 1.1 | Preparation of Detailed design of the access road to the WWTP site including technical review and design adjustments | 2.5 months | CD + 2.5 months |
| 1.2 | Preparation of Detailed design for connection of the WWTP to public water supply system including technical review and design adjustments | 2 months | CD + 2 months |
| 1.3 | Preparation of Detailed design for connection of the WWTP to power supply system including technical review and design adjustments | 2 months | CD + 2 months |
| 1.4 | Preparation of Detailed design for the telecommunication line for the WWTP including technical review and design adjustments | 2 months | CD + 2 months |
| 1.5 | Preparation of Detailed design of the site regulation and flood protection works and river regulation for the purpose of WWTP flood protection including technical review and design adjustments | 3 months | CD + 3 months |
| 1.6 | Geodetic Survey and Geo-technical Investigation Works on WWTP site for the purpose of design preparation | 1 month | CD + 1 months |
| 1.7 | Preparation of Detailed design of the WWTP Berane | 4 months | CD + 5 months |
| 1.8 | Review of Detailed design (technical control by consultant licensed by the Engineers Chamber of Montenegro) and finalization of the design | 1 month | CD + 6 months |
| 1.9 | Obtaining approvals on issued utility conditions | 1 month | CD + 7 months |
| 1.7 | Processing and issuing Building Permit | 1 month | CD + 8 months |
| 2 | Construction including (2.1 and 2.2) | 22 months | CD + 30 months |
| 2.1 | Construction and installation works | 16 months | CD + 24 months |
| 2.2 | Commissioning and Trial run | 6 months | CD + 30 months |
| 3 | Defect Notification Period | 12 months | CD + 42 months |

# TENDER DESIGN

General

The Tender Design of the WWTP shall be prepared by the Contractor and shall be fully compliant with the Employer’s Requirements. The Tender Design, and all other consequent designs in the contract implementation phase, shall include both planned implementation phases of the WWTP, i.e. Phase I and Phase II.

The Tenderer shall submit only one technical solution within the Tender Design and shall base his financial offer on such technical solution.

The Tender design shall clearly present all provisions for safety and uninterrupted process operation with particular attention to flexibility in operation during extraordinary circumstances, in case of failure of upstream or downstream units or any other irregular situation.

CONTENT OF TENDER DESIGN

The Tenderer shall prepare the Tender Design in sufficient detail, as a basis for his financial offer and to allow proper evaluation of the submitted bid. The Tender Design shall include the information specified hereinafter. The Design shall demonstrate adequacy of the technical solution and the required performance of various treatment processes and of the individual items of plant/equipment proposed.

The Tender Design shall include a technical description of the processes and equipment proposed for the WWTP with adequate justification. The Tender Design shall contain, as a minimum the following:

- Detailed process description, including technical calculations and detailed specification of all required equipment and works;

- Detailed hydraulic calculations of the process line including the by-pass line to the outfall;

- Proposed civil works and layout arrangement of facilities;

- Mass-balance calculations for earthworks;

- Specifications and bill of major/principal quantities of civil works, piping installations, and M & E works per each facility/system;

- List of Vendors and proposed equipment, in detail, including vendor, type, model reference, performance characteristics, data on motor drive (installed/absorbed power, motor speed, motor start, etc), materials and other detail confirming compliance with given Employers Process, Mechanical or Electrical technical requirements;

- Calculation of operational costs (power and chemicals consumption and quantity of solid waste to be disposed off) to be guaranteed in process performance guarantee;

- Outline description of the process control and automation systems;

- Description of the wastewater treatment plant operation during the initial period of operation, required minimum load for the plant operation and mode of operation of each particular process unit during that period.

- Description of geotechnical works, specification and origin of materials to be used

Drawings to be included

- Process flow block diagrams

- Process and Instrumentation diagrams (P&ID)

- Electrical single line diagrams

- WWTP layout and main sections showing all process units, buildings, roads, main pipelines, finished ground levels with excavation lines;

- Hydraulic profile along the by-pass

- Hydraulic profile through the plant

- Outline general arrangement drawing for all process units, presenting the main items of equipment to be supplied

- Outline configuration diagrams of the plant control and automation systems (including SCADA system).

- Civil engineering and architectural general arrangements and outline drawings with plans and sections for each facility (showing proposed building finishes and materials);

- Layout of site working arrangements and installation facilities.

# DOCUMENTS TO BE SUBMITTED BY THE CONTRACTOR

Work Programme

The Contractor shall submit a detailed Work Programme to the Engineer within 28 days after receiving the Notice to Commence. The Work Programme shall fully comply with the Conditions of Contract (PCC clause 8.3).

Further to that, the Programme of Works shall present sufficient details with regard to Design phase of the Project implementation, comprising at least, without limitation to, the following:

- Work Breakdown Structure (WBS) showing design sequences per engineering disciplines and facilities as well as their interconnections. The Contractor shall be solely responsible for internal coordination and management of the design process;

- Indicating dates by which design work or drawings are to be finalized;

- Indicating important design milestones, taking into account time required for technical control of Detailed Design and provision of Building Permit and other permits required for commencement of construction works;

Activities for which duration is anticipated in Section 1.9, Outline Work Programme, should be understood as follows:

Table 3-1: Outline Work Programme - explanations

| Item | Description |
| --- | --- |
| Geodetic survey and Geotechnical Investigation works | Completion of all necessary additional surveys and investigation works, as required for preparation of the Detailed design (Glavni projekat) |
| Preparation of Detailed Design | Preparation of the Detailed design - completely in accordance with the applicable national regulations (Law on Spatial Planning and Construction and other) and Employer’s Requirements |
| Review of Detailed Design | The Engineer shall conduct review of the Detailed Design both in the capacity of the Engineer and as an official review of the design, in accordance with the national regulations. |
| Finalization of Detailed Design | After having received relevant review comments, the Contractor shall modify and issue the corrected design documentation within the schedule defined in the Work Programme, in order to obtain final approval from the Engineer. |
| Building Permit | The Main Beneficiary, the Municipality of Berane, shall (with full technical assistance of the Contractor, as required), submit the application for obtaining of the Building Permit from the competent authorities for all elements of the Project within the scope of this tender. During this period the Contractor shall provide any relevant technical assistance that may be needed in this procedure (technical information, drawings, etc.). During this period the Contract may proceed with some Contract obligations (e.g. preparation of Detailed Working program for Construction phase) |
| Construction period | This period includes: completion of the whole of the Works, and achieving the passing of the Tests on Completion and completing all works in accordance with the Contract for the purposes of the taking-over. |

After the Design Phase and at least 28 days before the start of the Construction Works, the Contractor shall prepare an update of the Work Programme, and issue it for the Engineer’s approval.

The programme for the Construction period shall elaborate all details needed for the Works execution taking into account the approved Detailed Design. The updated Work Programme shall be completely consistent with the Contractor’s Contract obligations and in line with initially submitted general working program.

More details regarding this update are described in Section 1 General Requirements for execution of Works.

The Employer shall provide 7 days notice to the Authorities in charge for the inspection of works and to the one issuing the Building Permit of the Contractor’s intention to commence the execution of the Works on the site. The Contractor shall not be permitted to commence any construction work until the Method Statements (MS) are approved by the Engineer for that part of the Works. The Contractor shall allow in his Programme reasonable amount of time for work to be carried out by Public Utility Services Authorities. The Beneficiary will provide all necessary assistance in liaising with such Authorities.

Reports on Additional Investigation Works

Available information on site conditions such as site boundary, topography, geotechnical conditions, etc. are provided in Volume 5, Annex A5.1.

The Contractor shall review and assess the quality of this general information and where considered necessary he shall gather all additional information necessary to complete all design activities, to comply with the relevant national regulations and consequently finalize construction work at his own cost. The Contractor shall assume responsibility for all such additional investigations and include these activities in the main schedule of activities.

### Topography

Preliminary topographical survey data are included in Volume 5 of this tender. The Contractor shall identify the national mapping benchmarks and establish control points which shall be used for construction activities. The attributes of the topographical control points shall be communicated to the Engineer.

The Contractor shall carry out a necessary supplementary topographical survey of the project sites prior to the start of any construction works to record the existing situation. The survey shall be completed by an independent surveyor to be approved by the Engineer. The results of the survey shall be presented to the Engineer as a record of the existing site condition.

### Levels and Benchmarks

The works shall be set out and tied to the local National Co-ordinate System. Except where otherwise specified all levels shall be in meters above mean sea level (m.a.s.l.) with accuracy of three decimals. The Contractor shall supply to the Engineer details of the value and location of the temporary benchmarks and reference points that he proposes to use.

The Contractor shall, before the construction commences, establish from the reference point’s and benchmark’s, an adequate system of control points and benchmarks at suitable locations on the site of the works, which shall be clearly marked, adequately referenced and properly recorded. Temporary benchmarks and survey stations shall, unless otherwise approved, be located clear of the construction works.

The Contractor shall establish, construct and project during the period of construction of the Works necessary additional benchmarks, which shall be checked periodically. The Contractor shall be solely responsible for carrying out these operations. He shall make the control points and benchmarks available to the Engineer together with the relevant records.

The Contractor shall submit for approval to the Engineer for approval drawings in duplicate showing the locations and levels or co-ordinates as appropriate of each and every temporary benchmark and survey station used for the setting out of the works.

The Contractor shall be responsible for constructing the works in accordance with the data on levels, benchmarks and other points of reference in the vicinity of the site(s) if they are not shown on the drawings.

### Setting out of the Works

The Contractor shall before commencing execution of any given section of the Works submit to the Engineer complete setting out details with supporting calculations and drawings (including drawings showing the locations and co-ordinates of the reference points used) in duplicate for approval.

The Contractor shall identify setting out dimensions for all structures by relating them to existing works and by interpretation of the drawings.

The locations of structures to be constructed as part of the works shall be identified by reference to steel pins set in concrete or other approved markers set up by the Contractor, who shall also determine the co-ordinates of the markers and their distances from adjacent existing structures.

The Contractor shall set out sections of the works at such times as may be directed by the Engineer to enable Utility Service Authorities to carry out temporary or permanent alterations to their equipment or buried services.

Data and information on levels, dimensions, alignments and gradients other than these to be determined by the Contractor when preparing his structural and detailed design drawings are to be shown on the drawings. Details not shown on the drawings shall be established by the Contractor during the execution of the works.

The Contractor shall employ well-qualified and experienced surveyors approved by the Engineer for the execution of the survey work and setting out as described in the Contract. The instruments and/or equipment shall be subject to the approval of the Engineer.

For all survey instruments used in the works the Contractor shall submit recent calibration certificates issued by competent authorities. Further calibration of the instruments shall be carried out every three (3) months. All field-books, calculations, maps, etc. of survey activities mentioned above shall be handed over to the Engineer immediately after completion of the survey work.

### Geotechnical Investigations

The available geotechnical investigations and corresponding reports related to locations either at or in the vicinity of the site are included in Volume 5 of this tender.

The Contractor shall assess the quality and applicability of the provided data and carry out all necessary geotechnical investigations he considers necessary for completing the design of all facilities included in this contract.

Geological, hydro-geological and geotechnical surveys shall be completed in accordance with the relevant national and other specified Standards (DIN EN ISO 22475), including subsoil tests and ground water analysis.

Additional geotechnical Investigations shall be carried out in compliance with the relevant national regulation; the Law on Geological Investigations, Official Gazette of Montenegro, No. 28/93, 27/94, 42/94 and 26/07.

Details of the number, location of the boreholes or trial pits and reference points that he proposes to use shall be submitted for approval to the Engineer.

The fieldwork to be carried out by the Contractor may comprise:

- Sampling and laboratory tests

- Penetration tests

- Plate bearing tests

- Permeability tests

- Ground water table and ground water quality determination

The site investigation work shall be carried out using modern methods and equipment and by fully competent staff under the Contractor's manager. The equipment employed shall be such as to provide the necessary data.

If any suspicion of soil pollution is evident, samples must be taken for laboratory soil tests or field testing shall be carried out. Pollution shall mean that the material is considered as “unsound” and has to be replaced by “sound” material. “Unsound” soil structures (gypsum, salt, sulphate, etc.) have to be treated by technical precaution measures to achieve the necessary characteristics or they have to be replaced with “sound” material.

The Contractor shall use the results of available and  his own site investigations to design in detail every aspect of the Works, permanent or temporary, which is affected by the subsoil. This design shall be entirely Contractor’ responsibility and it is a subject of Engineer's acceptance.

### Existing Utility and Other Services or Buried Structures

Before starting any work, the Contractor must carry out a survey of his work area to identify any services or structures which may be present and may interfere with his design and the Works. The Contractor’s design shall take into consideration the discovered utilities.

The Contractor shall take all necessary steps to inform himself and the Engineer, Beneficiary and Authorities responsible for water, sewerage, electricity and communications and from private companies the location of underground utilities/structures.

Design Documentation

### General

The design and other Contractor’s documents shall be prepared in accordance with the legislation in place in Montenegro. The following Laws and regulations are applicable to this Contract:

Law on Spatial Development and Construction of Structures, (Off. Gazette of Montenegro, No. 51/08, 34/11 and 35/13)

By-Law on Preparation, scale and  content of technical documentation (Off. Gazette of Montenegro, No. 35/13 and 23/2014)

The Rulebook on the Method of performing the review of Conceptual and Detailed Designs (Off. Gazette of Montenegro, no. 81/08)

The Rulebook on the Content of the Study of Preparatory Construction Works (Off. Gazette of Montenegro, no. 80/08)

Law on integrated pollution Prevention and Control (Off. Gazette of Montenegro, no. 80 / 05)

The Law on Water (Official Gazette of Montenegro no. 27/07, 32/11 and 47/11)

The Law on Environment Protection (Official Gazette of Montenegro no. 48/08)

The by-law on the wastewater quality and the sanitary technical conditions for the discharge into the recipient and public sewerage system, methods and minimum number for wastewater quality analyses and content of the report on wastewater quality (Official Gazette of Montenegro, No. 45/08 & No. 09/10 and no. 26/12)

The by-low on classification and categorization of surface and ground waters (Official Gazette of Montenegro, No. 2/07)

Regulation on the conditions to be met by municipal sewage sludge, the quantity, scope, frequency and methods of analysis of municipal sewage sludge for application on land and conditions to be met by land planned for its implementation (Official Gazette of Montenegro, No. 89/09)

Law on solid waste (Official Gazette of Montenegro, No. 64/11)

Regulation on solid waste classification and solid waste catalogue (Official Gazette of Montenegro, No. 35/12)

and/or any other national regulations, in order to obtain the required licenses, permits and approvals.

The design and other Contractor’s documents submitted by the Contractor shall be in both English and Montenegrin language, all as provided for in Section 3.7.3.

All engineering documents, prepared by the Contractor for approval of the review company, authorities of Montenegro and/or the Engineer, shall be adequate for the purpose, meeting required standards and fully in accordance with the national law and the Employer’s Requirements.

Preparation of the documents and drawings to be submitted by the Contractor shall be conducted by a Design Manager subject to the Regulation’s approval. The Design Manager shall, within 21 day after the Commencement Date, submit the general Content of the Detailed Design, including the general list of drawings for the Engineer’s approval.

### Detailed Design (Glavni projekat)

Notwithstanding the Tender Requirements provisions, the Detailed Design of the Plant shall be prepared in accordance with the Law on Spatial Development and Construction of Structures, (Off. Gazette of Montenegro, No. 51/08, 34/11 and 35/13) and By-Law on Preparation, scale and contents of technical documentation (Off. Gazette of Montenegro, No 35/13 and 23/2014). The Detailed Design shall also comply with the specific technical/design conditions issued by public utility companies and other relevant authorities and shall comprise all documentation necessary for obtaining of the building permit. The following technical conditions and baseline documents have been acquired by the Beneficiary/Employer from the competent national authorities:

- Local Location Study “Donji Talum” for construction of WWTP Berane

- Urban-technical conditions for construction of WWTP Berane, issued by the Ministry of Sustainable Development and Tourism

- Technical conditions for the power supply connection, issued by the power supply authority – Elektroprivreda Crne Gore

- Water conditions, issued by the Government of Montenegro, Water Directorate

- Technical conditions related to communication cables

The abovementioned technical conditions related to the WWTP design are available in the Montenegrin language with the Beneficiary – Municipality of Berane.

The wastewater treatment plant shall be designed to fully meet the tender Requirements including the Plant Process Performance Guarantee and in conformity with the best engineering practice. The design documents shall elaborate on all aspects required for execution of the Works considering both construction phases. The Contractor shall also prepare such additional reports, documents and designs on particular aspects of the Works as provided for in the Employer’s Requirements or as reasonable requested by the Engineer.

The content of design documents and drawings shall neither be limited to those listed hereunder or in other relevant parts of the Contract, nor shall such list relieve the Contractor from any of his contractual obligations:

Results of the topographical survey (if any) in form of a report and drawings, stating coordinates and elevations of the existing terrain; photo-documentation showing the existing situation (surface, vegetation, etc.);

Results of the geo-technical survey in form of a report, calculations, soil profiles, drawings, etc. with clear statements on soil characteristics, geo-technical design parameters, recommendations for excavation, bracing and sheeting, recommendations for keeping excavations free of groundwater, recommendations for foundations, expected settlement and measures for settlement reduction for every building, tank, etc.;

Process design and calculations (ref. section 5 of this document): process description and calculations for wastewater treatment, sludge treatment, power and chemicals consumption, sludge and residual to be disposed, water demand, etc.; detailed P&I diagrams; flow charts; bill of materials, equipment list and specification; detailed drawings of the process equipment with exact position on the layout and characteristic sections with interconnecting pipes, valves, fittings, supports, anchoring, static and dynamic loads, etc.;

Hydraulic design and calculations throughout the plant structures for different hydraulic conditions, hydraulic profiles for wastewater and sludge, overflows and internal wastewater collection, storm water collection and management, etc.;

WWTP site layout (based on the approved surveys, investigations and detailed process design and calculations) showing location of all tanks, channels, inspection manholes, buried pipes, buried cable ducts, buried cables, site lighting, position of outdoor instrumentation and installations, outdoor earthing and lightning protection, remote data transmission cables, roads, footpaths, fence, gates, etc., providing its coordinates and absolute elevations;

Mechanical design: calculations and drawings for mechanical equipment and pipe installations, static and dynamic loads, supports, fittings, suspensions, etc.; list of valves and materials with detailed specification; erection sequence including ALL details needed for erection, etc.;

Electrical design: calculations and drawings (based on the approved detailed process design and calculations and detailed mechanical designs); control philosophy and automation chart; single line, circuit and wiring diagrams; cable lists; power consumer lists and calculations; simultaneous peak power demand; instrumentation lists, etc.;

Design and calculations for heating, ventilation, air condition (HVAC) and sanitary installation: (based on the approved detailed process design and calculations and detailed mechanical designs) in tabular form; equipment data sheets with detailed specification, equipment and materials to be supplied and erection sequence; etc.;

Design for civil work, tanks, chambers, channels, and buildings: earthworks drawings with indicated excavation lines for the phases I and II; architectural drawings (based on the approved detailed process design and calculations, detailed mechanical, electrical and HVAC and sanitary installation designs) showing machine and pipe installations, gratings, handrails, ladders, floor, walls, wall covering, insulation, ceilings, roofs, doors, windows, sanitary installations, heating, air conditioning, ventilation installations, interior furnishing, switchboards, building installations (lighting, socket outlets etc.), cable trays/conduits, telephone systems, remote data transmission, etc., providing co-ordinates and absolute elevations;

The process, mechanical, electrical and HVAC and sanitary installation equipment must fit in with the construction measures.;

Structural and foundation calculations for all tanks, chambers, channels, and buildings: based on the approved geotechnical report, architectural drawings, site layout and sections presenting excavation lines. The class or zone of earthquake shall be clearly indicated;

Formwork and reinforcement drawings, based on the approved architectural drawings and structural calculations for all tanks, chambers, channels, and buildings, including:

  - formwork plans

  - bar bending schedules for the steel reinforcement,

  - pre-cast concrete units including the cast-in units such as fasteners, jointing materials lifting provisions. etc., and

  - all steel work constructions including anchor-bolts, templates, etc.;

Longitudinal sections of all buried WWTP pipe-work, all force mains, including manholes, structures, etc. stating absolute elevations;

Structural calculations for all buried pipe work based on the approved geo-technical investigations, site layout, and its longitudinal sections;

Working drawings for bracing and sheeting for trenches and excavations;

Working drawings for keeping trenches and excavations free of groundwater;

Technical specifications;

Detailed Priced Bill of Quantities (legal requirement). Separate BPQPW (the Bill of Principal Quantities for Permanent Works) per facility as well as for the entire Permanent Works is to be prepared. The Bill of Quantities for civil engineering works should be prepared by using the standardised method of measurement as set out in the latest edition of the Civil Engineering Standard Method of Measurement by the UK Institution of Civil Engineers;

Fire fighting report as per relevant by-law;

Health and safety sections;

Environment mitigation measures during construction section

- and all other documentation pertaining to the Detailed Design according to By-Law on Procedure of Technical Documentation Preparation and its Contents.

- The Contractor is obliged to have certified licenses issued in Montenegro, for carrying out the design works under this contract. These licenses are issued separately to a legal entity and to engineers performing design services.

Start-up, Operation & Maintenance Manual

The Contractor shall prepare and submit for the approval of the Engineer Start-up, Operating and Maintenance Manuals in English and Montenegrin language, which shall describe the complete functions and requirements for start-up, operation, system control, wastewater quality control, maintenance, safety, record keeping, emergency response and shut down.

The manuals shall deal with operation and separately with maintenance and shall cover the WWTP as whole as well as individual sections. The manuals shall be arranged to provide separate volumes for each principal section of the Works.

All information in these manuals shall apply specifically to the equipment being supplied. The documentation shall be free from irrelevant matters that might be contained in the manufacturer’s general literature. Manuals shall relate to as-built conditions and shall include all necessary drawings and diagrams for a proper understanding of the Plant.

The Start-up, Operating and Maintenance manuals shall include as minimum the following information:

- Descriptive overview of the whole of the Treatment Plant;

- Description of complete process including wastewater and sludge treatment, as well as management of side streams, with relevant design and operating parameters;

- Detailed description of each system installed (process, mechanical or electrical equipment, as well as auxiliary systems such as water supply, drainage, internal sewerage, heating, ventilation and air conditioning, etc.) including each particular installation of the system, testing in dry conditions and/or wet installation, shutdown and start-up procedure (first start-up, shutdown due to failure and restart after repair);

- Description of all equipment supplied including manufacturers catalogues, technical data sheets (with performance curves if applicable) and instruction manuals, which are to be scheduled for easy reference;

- Procedures to deal with breakdown and emergencies;

- Safety requirements;

- Full maintenance instructions for all equipment including planned maintenance schedules or charts giving daily, weekly, monthly, quarterly, half yearly, annually and overhaul instructions, together with recommended lubricants and spares. These should also include details of routine maintenance work that will be within the competence of the Plant’s maintenance staff, and notification of maintenance work that has to be done by the manufacturer, his agent or other specialist operator;

- Step by step procedure for the dismantling, repair and re-assembly of all items of equipment which shall be complemented by photographs and exploded diagrams;

- List of spare parts;

- Certified suppliers drawings of all equipment supplied, which are to be scheduled for easy reference;

- Record as-build drawings of all systems installed, including general arrangements, detailed layout and sectional drawings with pipes and cables, air and water systems flow schemes, wiring diagrams, control schematics and valve charts, etc.;

- List of settings of all parameters (operation terminals of the PLC) for Plant automation and control at the time of handing over the Plant to the Beneficiary.

- Schedule of all equipment suppliers (and their local agents) including names, addresses, telephone, e-mail and fax numbers;

The “Provisional Start-up, Operation and Maintenance Manuals” shall be submitted as provided for in Section 3.7.3, 3 months prior of the Tests on Completion, all according to clause 5.7 of the Contract Conditions.

The “Final Operation and Maintenance Manuals”, shall be prepared in accordance with the requirements, taking into account any changes made during the Tests on Completion. The Manuals shall be submitted as provided for in Section 3.7.3 before the issuing of the Taking Over Certificate, all according to clause 5.7 of the Contract Conditions.

Each folder of any separate volume shall be durable and permanently bound within a stiff binder of a design to be approved by the Engineer for approval.

The Contractor shall provide in addition to the complete set of the start-up, operating and maintenance manuals the corresponding computer editable files (AutoCAD, MS Office, etc.) on CD.

As-Built Documents

All Design Book, each clearly marked as “As-Built” shall be submitted as provided for in Section 3.7.3 and procedures described in clause “5.6 As-Built Documents” of the Contract Conditions.

The Contractor shall prepare the “As-built design” which shall be prepared according to the By-law on Preparation, scale and contents of technical documentation, Official Gazette MNE, 23/2014.

Among others, the “As-built design” is required for the Technical Acceptance and obtaining of the Use Permit for the Plant and issuing of the Taking Over Certificate.

Materials Safety Data Sheet

Any product or substance used by the Contractor or its Subcontractors which is a toxic or hazardous substance shall be identified to the Engineer by the Contractor’s submission of a Material Safety Data Sheet (MSDS). The following MSDS or a manufacturer’s standard form shall be submitted to the Engineer to advise him of the use of such material during the project before the material is brought on site.

Submission and Approval of Contractor’s Documents

### Procedures for Submission and Approval of Detailed Design and other Contractor’s Documents

All drawings and documents shall be prepared by the Contractor within the time specified in the approved Program of Works and shall be submitted for examination and approval to the Engineer. Within his authorities, the Engineer is responsible for examination and approval/rejection of the Contractor’s Documents including the Detailed Design as well as for obtaining the Engineer’s prior approval/rejection whenever needed.

In any case, Engineer’s approval of any documentation shall not relieve the Contractor of any of his responsibilities under the Contract.

The Conditions of Contract, clause 5.2 “Contractor’s Documents” describes in general the procedures for submission and approval of all documents issued by the Contractor and as such shall be followed by the Contractor.

The below listed items are additional more detailed requirements, and shall be applied unless otherwise stated in section 3.7.2 below.

  - All Contractor’s drawings or documents shall be initially submitted to the Engineer in 4 hardcopies in English, 4 hardcopies in Montenegrin and 1 editable digital version in both English and Montenegrin.

  - The Engineer shall issue his written Approval, Approval with Comments or Rejection to the Contractor, within the examination period of 21 days.

  - The Contractor will promptly modify the documents in accordance with the Engineer’s comments and re-submit them in the same number of copies; applying procedures 1-2 above. However, examination period for the Engineer shall be 14 days.

  - No additional costs and/or the time extension shall be granted for the Contractor’s modifications of any document.

  - In the case of documents that are subject to statutory approvals, the Engineer shall include the statutory comments in his written answer to the Contractor.

  - In case of documents subject to statutory approvals, the Examination period shall be in accordance with relevant By-law + 7 days. If this is the case, contract condition clause 5.2 “Contractor’s Documents”, para. 6.(a), (iii) shall not be applicable.

### Detailed Design Approval and Review

Particular procedure is envisaged by Montenegrin Law in terms of approval of the Detailed Design. This procedure must be followed strictly, and it is assumed that the Contractor is familiar with the relevant By-Laws (at least but not limited to those listed in Section 3.3.1) and common procedures regarding the Review, Verification and Approval of the Detailed Design.

As explained in Section 1.9 the Contractor shall prepare the Detailed Design within 5 months after Commencement Date, followed by 1 month for the Engineer’s Final Review.  Within 1 month after receiving comments and remarks made by the Engineer (including those from all relevant Authorities), the Contractor shall finalize the Detailed Design accordingly and resubmit it for the Final Approval (packed and copied in sufficient number of copies as stated in Section 3.7.3).

As described in Section 3.1, the preliminary review and control of the DD preparation is foreseen during initial period of 4 months. The Contractor shall organize several coordination meetings between his Design team and the Reviewers.

### Schedule for submission of Documents

The schedule in the Table given below gives an overview of the most important contractual, design, construction, technical and planning documents that shall be submitted for the approval of the Engineer in accordance with the contract. The overall list of documents to be submitted by the Contractor is not limited to the list below.

Table 3-2: Schedule of Documents to be submitted for Approval

| Item | Document | Comments | Number of Copies (No. in ENG + No. in MNE + No. DIGITAL) | Submission time | Examination period |
| --- | --- | --- | --- | --- | --- |
| A | General |  |  |  |  |
| A1 | Work Programme (ref. CC 8.3; Vol. 3-1 Sec.2) | Detailed program | 4 + 4 + 1 | CD +2 days | 21 days |
| A2.1 | Updated Work Programme (ref. Vol. 3-1 Sec.2) | For Construction activities | 4 + 4 + 1 | 21 days before scheduled Commencement of construction works; | 21 days |
| A2.2 | Monthly updates of Work Programme | For Construction activities | 4 + 0 + 1 | Monthly updates to be attached to IPC | 7 days |
| A3 | Health & Safety Plan (ref. Vol. 3-1 Sec.1) | Subject to Engineers/ Statutory approval | 4 + 4 + 1 | 28 days before scheduled Commencement of Construction Works | 21 days |
| A4 | Study on Preparatory Works | Subject to Engineer’s/ Statutory approval | 4 + 4 + 1 | 28 days before scheduled Commencement of Construction Works | 21 days |
| A5 | Construction Environmental Management Plan (ref. Vol. 3-1, Sec.1) |  | 4 + 4 + 1 | 28 days before scheduled Commencement of Construction Works | 21 days |
| A6 | Full QA/QC Plan (ref. Vol.3-1, Sec1) |  | 4 + 4 + 1 | CD +28 days | 21 days |
| B | Detailed Design (ref. Vol.3-1, Sec.2) | In full compliance with Montenegrin Construction Law and respective by-laws, | 1 + 5 + 5 1 + 6 + 6 | CD + 2-5 months depending on the element (for review) CD + 6 months (for final approval & for requesting Building Permit | MD submission + 1 month |
| B1 | Detailed Design Report | Extract of Technical descriptions, BoQ-s, calculations | 5 + 0 + 5 | CD + 5 months (for review) CD + 6 months (for final approval) | MD submission + 1 month |
| B2 | Additional Topographical Survey Report (ref. Vol.3-1, Sec.1) | Forms part of the DD | 1 + 6 + 1 | One month after Investigation works completion | MD submission + 1 month |
| B3 | Additional Geo-technical Report (ref. Vol.3-1, Sec.1) | Forms part of the DD | 1 + 6 + 1 | One month after Investigation works completion | MD submission + 1 month |
| B 4.1 | As-built records (draft As-built drawings) (ref. CC-5.6) |  | 2 + 1 + 1 | 7 days before commencement of the Test on Completion | n/a |
| B 4.2 | As-built design (ref. Vol.3-1. Sec.2) |  | 2 + 6 + 1 | according to Montenegrin law, at least 3 weeks before issue of Taking Over Certificate |  |
| C | Construction |  |  |  |  |
| C1 | Method Statements (ref. Vol.3-1, Sec.1) |  | 4 + 4 + 1 | 28 days prior to Commencement of respective Works | 14 days |
| C2 | Approval of Goods and Materials for Works (ref. Vol 3-1. Sec.1) |  | 4 + 4 + 1 | 21 days prior to Purchase Order placement | 14 days |
| C3 | Test Certificates (ref. Vol. 3-1) | For goods and materials | 4 + 4 + 0 | As per ER; latest On Delivery of Goods | 21 days |
| C4 | Contractor’s Equipment (CC 4.17; Vol.3-1, Sec.1) | List | 4 + 4 + 1 | 14 days prior to Commencement of respective Works | 7 days |
| C5 | Program of specific tests (ref. Vol.3-1, Sec.2) | Detailed inspection and testing | 4 + 4 + 1 | As per ER, but latest 28 days prior to Commencement of respective tests | 21 days |
| D | O&M and Training |  |  |  |  |
| D1.1 | Provisional O&M Manual (ref. Vol.3-1, Sec.2) |  | 2 + 2 + 1 | 3 months prior to Test on Completion | 42 days |
| D1.2 | Final O&M Manual (final) (ref. Vol.3-1, Sec.2) |  | 2 + 6 + 1 | 3 weeks before Takeover of works | 14 days |
| D1.3 | Updated Final O&M Manual (final) (ref. Vol.3-1, Sec.2) | Update after Operation Service Period | 2 + 6 + 1 | 3 months prior to Taking Over Certificate | 42 days |
| D2 | Maintenance Plan (ref. Vol.3-1, Sec.2) |  | 2 + 6 + 1 | 3 weeks before Takeover of works | 14 days |
| D3 | Training Plan (ref. Vol.3-1, Sec.2) |  | 2 + 4 + 1 | 12 months before scheduled start of Tests on Completion | TBD |
| E | Reporting |  |  |  |  |
| E1 | Monthly Progress Reports (ref. Vol. 3-1. Sec.1) |  | 4 + 4 + 1 | Monthly, attached to IPC | With IPC approval (ref. CC 14.7) |
| E2 | Construction Diary (ref. Vol. 3-1, Sec.1) |  | Statutory | Statutory | Statutory |
| E3 | Construction Log Book (ref. Vol.3-1, Sec.1) |  | 4 + 4 + 1 | Monthly, attached to IPC | With IPC approval (ref. CC 14.7) |
| E4 | Plant and Labour Returns |  | 4 + 4 + 1 | Monthly, attached to IPC | n/a |

Abbreviations:

- CD: 		Commencement Date

- CC: 		Conditions of Contract

- ER:	 	Employer’s Requirements

- DD: 		Detailed Design

- O&M: 		Operation & Maintenance
IPC: 		Interim Payment Certificate

- QA/QC:	Quality Assurance/Quality Control

- WP:		Work Programme

# GENERAL DESIGN REQUIREMENTS

General

The wastewater treatment plant shall be designed to fully meet the Tender Requirements including the Plant Process Performance Guarantee and in conformity with contemporary best engineering practice. Particular attention shall be given to the following aspects:

- The local climatic conditions

- Durability of the plant and the required minimum design life

- Protection of soil below the  treatment facilities

- Full accordance with the planned extension of the wastewater collection system, particularly with the main city sewer entering the WWTP site

- Flexibility in dealing with varying flow and load regimes resulting from demand and wastewater loads variations

- Convenient and effective way of operating and maintaining the Plant, appurtenant facilities and achieving minimal operating costs

- Making of all necessary provisions for convenient future extension of the Plant in Phase II

- Health & safety, environmental provisions in the construction phase

- Health & safety, environmental provisions in the operation phase

- Special care should be taken to achieving required reduction of odours and noise

- Overall site security in both construction and operation phases

- Operational attendance, one shift per day, for 8 hours per shift, 7 days per week

The design shall fully comply with the Tender requirements (overall process needs, the wastewater flow rates, design capacities, design criteria, and technical specifications).

Design horizons and wastewater flows and loads

### Design Horizons

The estimated design horizons for the Wastewater Treatment Plant are until the year 2035 and from 2035 onward. The flows & loads respectively expected, as given in the tables of the sub-section 4.2.2.

Table 4-1:Phasing of the WWTP

| Implementation phase | Description of main activities |
| --- | --- |
| Phase I – capacity of 20,000 PE | Includes design and construction of the specified WWTP elements, as per this Employer’s requirements, including construction of some components for the Phase II capacity (27.000 PE) |
| Phase II – capacity of 27,000 PE | Includes design of specified WWTP elements, as per this Employer’s requirements |

### Hydraulic and Pollutant Loads

The following tables present typical hydraulic and pollutant loadings for planned implementation of the WWTP .

Table 4-2: Typical hydraulic loadings for WWTP

| Item | Description | Unit | Phase I | Phase II |
| --- | --- | --- | --- | --- |
| 1 | Population Equivalent | PE | 20,000 | 27,000 |
| 2 | Wastewater Flows |  |  |  |
| 2.1 | Domestic Wastewater Flow, QD | m³/d | 2,431 | 3,375 |
| 2.2 | Industrial wastewater flow, OIND | m³/d | 812 | 1,013 |
| 2.4 | Wastewater flow without infiltration, Qww | m³/d | 3,243 | 4,388 |
|  |  | l/s | 37 | 51 |
| 2.5 | Infiltration Flow QINF | m³/d | 1,297 | 1,316 |
|  |  | m³/h | 54 | 55 |
|  |  | l/s | 15 | 15 |
| 2.6 | Wastewater flow with infiltration QDW=QD+QIND+QINF | m³/d | 4,540 | 5,704 |
|  |  | l/s | 53 | 66 |
| 2.7 | Peak dry weather flow Q DW, max | m3/h | 294 | 380 |
|  |  | l/s | 82 | 105 |
| 2.8 | Peak wet weather flow to WWTP, Q WetW, max | m³/h | 615 | 820 |
|  |  | l/s | 171 | 228 |

Table 4-3: Typical pollutant loadings and concentrations for WWTP

| Item | Description | Unit | Phase I | Phase II |
| --- | --- | --- | --- | --- |
| 1 | WWTP Load |  |  |  |
| 1.1 | Population Equivalent |  | 20,000 | 27,000 |
| 1.2 | BOD5 | kg/day | 1,200 | 1,620 |
| 1.3 | COD | kg/day | 2,400 | 3,240 |
| 1.4 | TSS | kg/day | 1,400 | 1,890 |
| 1.5 | TN | kg/day | 220 | 297 |
| 1.6 | TP | kg/day | 36 | 49 |
| 2 | Average concentrations |  |  |  |
| 2.1 | BOD5 | mg/l | 264 | 284 |
| 2.2 | COD | mg/l | 29 | 568 |
| 2.3 | TSS | mg/l | 308 | 331 |
| 2.4 | TN | mg/l | 48 | 52 |
| 2.5 | TP | mg/l | 8 | 9 |

The wastewater characteristics correspond to the average characteristics of municipal sewage with industrial contribution. However, apart from those pollutant loadings, the Contractor shall consider in his design possible variations of wastewater characteristics (flows, concentrations and proportions of substrate/nutrients, etc.).

Population Equivalents are calculated on the basis of connected population, population growth projections , as well as considering current and foreseen industrial pollution.

Indicative sewage temperatures are expected to be in the range of summer 20°C to winter 12°C.

Technical Conditions for Design and Construction of WWTP

The Municipality of Berane obtained Urban-technical conditions for technical design preparation and construction of the WWTP at subject location UP1 (“Donji Talum”) included in Study on Location for (Issued by Ministry of sustainable development and tourism on 16.10.2012, Ref. No. 04-2472/1).

The following table includes a list of technical design conditions acquired so far by the Municipality of Berane for the purpose of WWTP design preparation. These design conditions, in addition to other tender requirements, should represent a basis for the WWTP design preparation. The list of available design conditions acquired by the Municipality is presented in the table below.

Table 4-4: List of relevant technical conditions for design of WWTP

| No. | Title | Date | Issued by |
| --- | --- | --- | --- |
| 1 | Urban-technical conditions for design and construction of WWTP system and WWTP | 16.10.2012 | Ministry of sustainable development and tourism |
| 2 | Water Management conditions | 12.10.2012 | Water Directorate |
| 3 | Opinion on necessity of EIA Study | 04.10.2012 | Ministry of sustainable development and tourism |
| 4 | Conditions for installation of communication cables, cables for cable distribution and common areal system | 15.10.2012 | Ministry of sustainable development and tourism |
| 5 | Conditions for connection to power supply network | 25.11.2014. | Power supply company Elektroprivreda Crne Gore |
| 6 | Conditions for connection to water supply network | 21.11.2014 | PUC Vodovod i kanalizacija Berane |

Minimum Design Life

Materials shall be selected and the Plant designed for a minimum overall design life of 50 years. The following table gives the minimum design life for various components of the treatment plant before major refurbishment is required:

Table 4-5: Minimum Design Life

| Description | Design Life (Years) |
| --- | --- |
| Civil Works and Buildings Process Structures | 50 |
| Pipes & sewers | 50 |
| Buildings | 50 |
| Roads | 50 |
| HVAC equipment | 20 |
| Building Services | 20 |
| Process, Mechanical and Electrical Plant Process Equipment | 20 |
| Mechanical equipment | 20 |
| HV switchgear and transformers | 40 |
| LV Motor Control Centres | 20 |
| Electrical Installations | 20 |
| Instrumentation, Control and Automation equipment | 15 |
| SCADA and PLC systems | 15 |

Design and Construction Standards and Codes

SI units (Système International d'Unités) of measurement shall be used throughout this Contract. All calculations and technical information shall be in SI units. The Contractor shall transfer all information and data originating in another system into the SI System.

In general, the requirements for the design, construction, manufacture, inspection and testing of the works shall meet the standards stated in the Specifications or the applicable codes and standards used in Montenegro. The Contractor is permitted to use other internationally recognised standards and codes (e.g. of the European Community - EN, German technical standards - DIN) provided that the design, the constructed facilities, the installed equipment and the treatment plant end-product meets, or exceeds, the minimum specified requirements. Any reference made, in the Employer’s Requirements and in the Civil/Mechanical/Electrical Specifications, to specific codes or standards shall be read as: “or any other equivalent and approved (by the Engineer) code or standard”. References made to the published standards shall be understood to be references to the edition applicable on the Base Date, unless stated otherwise.

All the laws and regulations of Montenegro appertaining to the planning & design preparation, construction, environmental protection, safety and fire protection must be complied with. All applicable laws shall be those prevailing at the moment the works or sections are taken over by the Employer under Clause 10, [Employer’s  Taking Over] of the General Conditions of Contract (clause 5.4).

Process Design shall be based on:

- ATV-DVWK-Standard A 131: Dimensioning of Single Stage Activated Sludge Plants, May 2000;

- ATV DVWK Standard A 134: Planning and Construction of Wastewater Pumping Stations, June 2000;

- ATV DVWK Standard M 210: Dimensioning of Sequencing Batch Reactor Plants, July 2009;

- DWA Report Workgroup KA 5 “Sedimentation Processes” – Grease and Grit Chambers; Requirements, Systems and Design, May 2008

- DWA M 368: Sludge Stabilization

The concreting works specified for the wastewater treatment facilities shall be designed and constructed to Euro-code 2: Design of Concrete Structures – Part 4: Liquid retaining and containing structures (or equivalent national or international standards).

Except where otherwise specified, all materials and workmanship shall comply with the requirements of the latest editions of European, German and Montenegrin Standards and Codes of practice and with any other Standards referred to in the Employer ‘s Requirements.

If necessary, equivalent National Standards may substitute the Standards referred to in the Employer ‘s Requirements, provided the Contractor shall have justified such substitution to the Engineer. These Standards shall only be applied after written approval has been obtained from the Engineer.

If for any materials and/or workmanship the reference to the specific Standards or relevant Codes of practice is lacking in the Specifications, the Contractor shall propose applicable ones for the Engineer’s approval. The proposed Standards shall be such requiring top quality of goods and a first class work.

General Layout

The layout of the WWTP shall consider the following minimum design requirements:

- The site location is generally plain next to the Lim River and the available area planned for the WWTP facilities is limited as indicated in the general layouts in the Volume 5;

- Since construction of the wastewater treatment facilities is planned will be constructed in two phases, adequate provisions must be made for Phase II development;

- The overall arrangement of the process units shall enable efficient and convenient construction and connection of Phase II units without disturbance to normal WWTP operation;

- Length of pipes, channels, and cables between the process units shall be optimized,

- Accessibility shall be provided to all buildings and major structures by all-weather roads,

- All structures, electrical and mechanical equipment shall be protected from physical damage by flooding through the use of appropriate drainage and pumping systems,

- The WWTP site shall be provided by adequate stormwater drainage facilities,

- The direction of prevailing winds shall be considered in finalising the WWTP layout,

- General site elevations shall be determined in accordance with the minimal required level of protection in terms of flooding; the site must be higher than the water level for 1 in 100 years flood event, plus a freeboard of 1m.

Requirements for Operation Stability and Reliability

The whole Plant shall be designed for maximum operation stability, reliability and flexibility at the least operation/maintenance and capital costs considering:

- Application of safety factors wherever necessary in order to cover unpredictable situations and conditions, especially concerning variations of wastewater flow, pollution loads, and sludge characteristics (sludge volume index etc.),

- provision of alarm systems indicating early warning of irregular/unpredictable situations and conditions like inflow of substances into the WWTP disturbing or inhibitory the treatment process,

- provisions to manage particular operation conditions like start-up, regular shut-down, emergency shut-down, operation with reduced number of process units, etc.,

- provisions to manage normally expectable particular operation conditions like low hydraulic loading, overloading and shock load (in-flowing wastewater, sludge waters etc.), without any deterioration of the effluent quality,

- provisions to manage normally expectable failures in operation like bulking sludge, foaming, etc. for any process unit, without any deterioration of the effluent quality, provision of by-passes of all principal process units so that each process unit can be put out of operation without stopping the whole treatment process,

- in general provision of fix-piped installation of stand-by pumps, machines and aggregates, ready to be put into operation is required (“n-i” rule, whereas i = 1 for n ≤ 4 and i = 2 for n > 4), unless otherwise specified elsewhere in the General Specifications. In this requirement i stands for a number of stand-by units, while n-i stands for a number of operational units and n is the total number of units.

- provision of connection points sufficient in number and capacity for easy installation of additional and spare pumps, machines, aggregates,

- where fixed installation is economically not feasible, provision of not fixed-piped installation for spare pumps, machines, aggregates in sufficient number, easy to install,

- simplification and unification of equipment to allow for utmost interchange ability of pumps, machines, aggregates and to ease regular maintenance,

- free adjustable and wide range of controlled variables to cover possible operation conditions (for further details refer to the Employer’s Requirements).

- emergency power supply (for further details refer to  the Employer’s Requirements).

- provision shall be made for suitable steps, platforms and hand railing to allow safe and easy access for the operation and maintenance of all items of plant according to European and Montenegrin Standards.

Requirements for Operation and Maintenance

The design shall incorporate every reasonable precaution and provision for the safety of all those concerned in the operation and maintenance of the works.

To guarantee access to all mechanical and electrical parts of the whole Plant for cleaning, maintenance and repair, the following is of importance:

- Space between the process units (tanks, chambers, channels, pipe, machines, pumps, aggregates etc.) shall be big enough to guarantee acceptable accessibility for the working personnel to facilitate inspection, cleaning and repairs, especially when working with lifting units.

- Assembly orifices and access facilities such as doors and gates shall be provided. Access to assembly orifices must be guaranteed.

- All covers such as gratings for channels or assembly orifices shall be constructed in such way that they can be opened by one person only without danger.

- All railings and security installations shall be arranged in that way that they can be removed easily and quickly in the case of assembly, disassembly, maintenance or repair of mechanical or electrical units.

- All tanks and reservoirs, etc., shall be provided with platforms and gangways if they are not readily accessible.

- All tanks and chambers shall be designed in that way that easy emptying is possible, either by providing a washout for each tank or a pump sump.

- The arrangement of the individual pieces of apparatus, pipelines and operational monitoring device must be such that the operation of the installation can be carried out unhindered and that any necessary repairs which may arise can be carried out without difficulty and without hindering the running of the other parts. Special care must be taken that the control systems and monitoring instruments are arranged so as to be easily visible.

- Accessible means shall be provided for the easy lubrication of all bearings, mechanisms and moving parts, with applying particular measures in order to avoid further contamination of plant, soil or (process) water

- Enable enough hydrants for cleaning purposes

Hydraulic Design Requirements

The hydraulic design of the whole Plant shall be prepared taking into account the following requirements:

- All hydraulic structures, interconnections, distribution chambers, etc., and treatment units not suitable for later extension shall be designed and constructed for the peak wet weather flows/hydraulic load of the WWTP Phase II;

- Regarding hydraulic losses, all hydraulic structures, pipes and channels shall be designed to keep losses within reasonably low limits;

- The “n-1” rule for two or more tanks of a treatment stage: the hydraulic capacity of any weir, collection trough, pipe, channel, chamber, tank shall be sufficient for the maximum flow increased by the factor n/(n-1), whereas n = number of tanks;

- Plant components to be arranged for maximum flexibility of operation for all treatment lines (no disruption of flows is allowed when one line is taken out of operation);

- Distribution chambers are sized and constructed to permit future units to be easily connected. Allowances are to be made for interconnections with the future Phase II Plant extension;

- Pump sumps and chambers shall be designed with space for installation of future pumps;

- Arrangement of any weir, collection trough, pipe, channel, chamber, tank in that way that later extension is possible without any major alteration works, and sized for the peak flow in each unit;

- Sufficient hydraulic uncoupling shall be accomplished by free overflows (sharp-crested weirs and V-notch weirs). Free overflow is defined herein as the case that the energy level of the tail water is lower or equal than the weir crest level;

- Cross-connections of flows before and after process units;

- Sufficient freeboard in all channels and pipes shall be allowed;

- The minimum and maximum flow speeds according to international standards should not be fallen short, respectively exceeded in channels and pipes;

- Pressure pipe bends points shall have a minimum radius of 1.5 x pipe diameter. Changes in direction of gravity pipe bends have to be executed with manholes. Then the minimum radius to the centre line of the chute shall be 2.0 x pipe diameter. Benches shall be built up the top of the pipe;

- Pipes subject to clogging (sludge, polymer, lime pipes, etc.) shall be provided with flush valves in sufficient number and diameter;

- Connections between treatment units shall be designed as pressure pipelines (gravity or pumping mains), partially full pipelines (free-surface flow), or open channels with uniform or non-uniform flow. Additional hydraulic elements include non-submerged weirs, submerged weirs and submerged orifices.

Pipe-work

All underground pipe work shall be designed, installed and tested as specified in the relevant Employer’s Requirements .

Force Mains

If required twin pipes shall be installed to improve operational flexibility. According to ATV-DVWK A 134 the velocity in the mains flow must be 0.5 m/s ≤ v ≤ 2.5 m/s depending on the daily period of operation. Furthermore for design of force mains ATV-DVWK M 275 has to be considered.

Low flow speed leads to sedimentation inside the pipes, which can significantly reduce the hydraulic capacity and cause operational problems. On the other hand friction head loss shall be minimized in order to reduce power costs.

The Contractor is free to determine the diameter of the force mains as long as the design criteria and the operation requirements as set out in the documents are satisfied. Pipe Material shall be as specified in the relevant Employer’s Requirements .

Road, Water Course and other Utility Crossings

The Contractor shall fully comply with all requirements of the relevant authorities and owners, for all road and water course crossings and for crossing and working in close proximity to utility installations, including those of the respective Water Supply and Sewerage Company.

The Contractor shall during design process comply with the conditions for connecting to utility services provided by respective authorities and with all other relevant sections of the Employer ‘s Requirements.

Noise Emission Standards

The works shall be designed to ensure that the maximum noise level at the Site boundaries shall not exceed an equivalent continuous sound level of 55 dB (A). In addition, the noise level at a distance of 1 m from each sound-producing piece of mechanical equipment shall not exceed 85 dB (A).

Flow Measurement and Control

Wastewater flows to the treatment facilities, final effluent and excess sludge flows shall be measured with either in-line flow meters (for pipes) or open channel flow meters for large water flows.

Operation of overflow weirs, pump rates, excess and return sludge, etc (as measured) shall be within ±5% of the flows specified within the respective sections of the Employer ‘s Requirements.

Discharge of Effluent

Treated effluent shall be discharged into the nearby Lim River via the effluent discharge pipe. The effluent discharge pipe, including the outfall structure, is within the scope of works of this tender including design and construction.

The effluent discharge pipe shall be designed and constructed as a gravity sewer of capacity equivalent to the Phase II peak wet-weather flow.

The design of the outfall structure shall consider the flow conditions of the river for the relevant high-water level at 660.85 masl (100-year recurrence interval) as well as low-water levels. It shall be designed in such a way that prevents erosion/damages of the river bed and banks at the discharge point.

# PROCESS AND MECHANICAL DESIGN REQUIREMENTS

General

Tenderers are required to prepare complete process design for all project elements as specified in the Tender. Process design shall be in line with the DWA/ATV standards or equivalent internationally accepted standards and shall include both construction phases: phase I (20,000 PE) and phase II (27,000 PE).

The specifications presented hereinafter define the minimum Employer ‘s Process Design Requirements. The Tenderer may propose higher or stricter criteria as he deems necessary within required treatment efficiency.

The Tenderers are required to comply with the Employer ‘s requirements and propose activated sludge process based on SBR technology with aerobic sludge stabilization. Any alternative technical solution with regard to treatment process will not be evaluated.

The design proposals shall be in line with the DWA/ATV standards and shall in particular consider hereinafter stipulated design requirements for the main process units of the WWTP.

The sludge generated by the wastewater treatment process shall be aerobically stabilized and dewatered at the WWTP site, transported and disposed on the landfill. The sludge disposal concept for the WWTP foresees availability of sufficient and appropriate sludge disposal facilities located outside of the WWTP area.

The Tenderer shall submit only one technical solution and will base his financial offer on such Tender design. Accordingly, the Price Schedules as presented in Volume 4 Section 1 must be completed, with additional items added if necessary.

The Tenderer shall prepare design documentation in sufficient details, as a basis for his financial offer and such to allow a proper evaluation of the submitted Tender. The documentation shall include the below listed information, which shall prove (considering both design horizons) the adequacy of the design and the performance of the various treatment processes comprised as well as of the individual items of plant/equipment proposed.

The Tender Design documentation shall include an outline technical description of the processes and equipment proposed for the Phase I and for the Plant extension in the Phase II, together with sufficient evidence for its justification. The design documentation shall contain, but is not limited to:

- Inlet chamber

- Bay-pass line including effluent line and outfall

- Coarse screens

- Lifting Pumping station

- Fine Screens with screenings washing and compaction

- Aerated grit chamber with grit classifier

- Influent flow measurement and sampling

- Odour removal facilities

- Equalization tank

- SBR feeding pumping station

- SBR for biological treatment including nutrient removal and aerobic sludge stabilization

- Blower station

- Effluent flow measurement and sampling

- Excess sludge handling facilities including excess sludge extraction pumps, intermittently mixed balance tank, mechanical pre-thickening and sludge dewatering facilities including polymer preparation and dosing

- Septic sludge reception facility

- Transformer station

- Interface structures and facilities to be used in second stage

- Site stabilization, levelling all works related to flod protection

- Access, internal roads and landscaping

- Administration building with laboratory and control room

- Workshop and stores

- Guardhouse

Description of Works

The Works to be performed by the Contractor under Lot 1 include preparation of the Detailed design, construction, materials supply, equipment delivery and erection, site installation, testing and commissioning and putting into reliable service of all Works as necessary to meet the design and performance requirements. In addition to these, the Contractor is required to provide training and education of staff nominated to operate the Plant.

The Detailed design shall be provided in accordance with Employer’s requirements, Urban technical conditions issued by Ministry of sustainable development and tourism, and other conditions and opinions issued by Ministry, public companies, etc. as required by Law on Spatial planning and construction of structures.

Layout arrangement drawings given in Volume 5 are only indicative, providing information on size of the site and possible arrangement of structures required for treatment of wastewater. The Contractor is required to update hydraulic profile in accordance with final elevation of the site and elevations of the incoming collector and treated effluent outfall, and propose his own solution and arrangement of process units in accordance with the updated hydraulic profile. The Contractor shall foresee all provisions to achieve the specified Process Guarantees and shall consider proposed design as his only responsibility with no additional costs to the Employer/Beneficiary during execution of the Contract.

The design shall include all process, hydraulic and service facilities and structures for capacity of Phase II.

Considering limited available space at the WWTP site location, the Contractor is required to propose cost-effective technical solution for future extension of the Plant for Phase II.

Basic Design Criteria

### Population Equivalent

Population Equivalents are calculated on the basis of connected population, population growth projections for the next 20 years, as well as current and foreseen industrial pollution.

Table 5-1:  Population Equivalent Projections (rounded)

| Parameter | Phase I | Phase II |
| --- | --- | --- |
| Population equivalent | 20,000 | 27,000 |

### Design Flows

The assessed total quantities of wastewater within the project horizons are shown in the table below.

Table  5-2:  Selected Wastewater flows for the project horizons

| Parameter | Unit | Phase I | Phase II |
| --- | --- | --- | --- |
| Domestic Wastewater Flow, QD | m³/d | 2,431 | 3,375 |
| Industrial wastewater flow, QIND | m³/d | 812 | 1,013 |
| Wastewater flow without infiltration, Qww | m³/d | 3,243 | 4,388 |
|  | l/s | 37 | 51 |
| Infiltration Flow QINF | m³/d | 1,297 | 1,316 |
|  | m³/h | 54 | 55 |
|  | l/s | 15 | 15 |
| Wastewater flow with infiltration QDW=QD+QIND+QINF | m³/d | 4,540 | 5,704 |
|  | l/s | 53 | 66 |
| Peak dry weather flow, Q DW, max | m3/h | 294 | 380 |
|  | l/s | 82 | 105 |
| Peak wet weather flow to WWTP, Q WetW, max | m³/h | 615 | 820 |
|  | l/s | 171 | 228 |

The Contractor shall check all the data, from the information made available by the Contracting Employer/Beneficiary, regarding existing flows and loads to treatment, before preparing the detail design.

The process water from the sludge treatment causes additional hydraulic and organic load of the wastewater treatment process. The quantity of this load depends on the sludge treatment process chosen, and it shall be taken into account for dimensioning of the equipment and facilities.

For the hydraulic calculation of the facilities within WWTP, 3 % of the process wastewater shall be added to the inlet wastewater flows and as such shall be considered as basic design criteria for sizing of structures, installations and equipment.

Consequently, the Contractor shall allow in his design additional 3 % of the inflow loads, from liquors arising from the sludge thickening and dewatering processes, which shall be returned to the inlet channel, upstream fine screens.

After preliminary treatment of septic delivered onsite, including removal o coarse material and solids of diameter ≥ 6mm, septic sludge shall be discharged by pump into head of the WWTP. Due to high solid content pumping capacity shall not exceed 2 % of average inflow to the WWTP.

The total load discharged into the WWTP comprises the sum of the loads from domestic inhabitants, commercial and industrial pollutants. The influent concentrations of the WWTP have been derived from daily loads and water quantities.

The Wastewater Treatment Plant shall be designed to accommodate the flows and loads given in the tables below and be able to meet the consent standards defined in the Plant Process Performance Guarantee.

Table 5-3: Design loads, concentrations, effluent standards

| Parameter | Unit | Phase I | Phase II |
| --- | --- | --- | --- |
| Population Equivalent | PE | 20,000 | 27,000 |
| BOD5 | kg/day | 1,200 | 1,620 |
| COD | kg/day | 2,400 | 3,240 |
| TSS | kg/day | 1,400 | 1,890 |
| TN | kg/day | 220 | 297 |
| TP | kg/day | 36 | 49 |
| Average pollutant concentrations in wastewater |  |  |  |
| BOD5 | mg/l | 264 | 284 |
| COD | mg/l | 529 | 568 |
| TSS | mg/l | 308 | 331 |
| TN | mg/l | 48 | 52 |
| TP | mg/l | 8 | 9 |
| Wastewater temperature | °C | 20/12 |  |

The influent reference loads are daily average, at the plant inlet. The plant must be capable of treating normal variations and peaks up to ± 10 % throughout the day. Peak hourly flow shall be the design criteria for hydraulic dimensioning.

During the Plant performance tests (see section 10) the Contractor shall simulate the design horizon operating conditions to demonstrate that the performance requirements will be met.

### Effluent Quality Standards

The treated effluent from the planned WWTP will be discharged into the river Lim. According to Council Directive 91/271/EEC concerning urban waste water treatment, Annex II Criteria for identification of sensitive and less sensitive areas, and water quality analyses this area can be identified as sensitive area due to current status and use as source for water supply of downstream settlements.

In accordance with By-Law on effluent quality and sanitary conditions for discharge of wastewater into natural water bodies and sewerage, methods and minimum number of wastewater quality analyses (official Gazette of Montenegro 45/08 9/10 and 26/12) and EEC Directive 91/271 treated wastewater shall provide as a minimum biological treatment with nutrient removal.

Table 5-4: Required effluent quality

| Parameter | Unit | Value |
| --- | --- | --- |
| BOD5 | mg O2/l | 25 |
| COD | mg O2/l | 125 |
| Total suspended solids | mg/l | 35 |
| Total Nitrogen (total organic plus inorganic) | mg/l | 15 |
| Total Phosphorous | mg/l | 2 |

WWTP Facilities

The indicative drawings for WWTP design presented in Volume 5 are based on activated sludge process with simultaneous aerobic sludge stabilization in SBR (Sequencing Batch Reactor). The Contractor is required to submit a technical solution in accordance with the Employer’s Requirements. Any alternative technical solutions for the wastewater treatment process will not be considered. However, the Contractor’s design must also consider planning for the final design horizon for phase II, all in accordance with the Employer’s Requirements (particular reference is made to the Wastewater disposal concept, General and Process design requirements, respectively provided for in sub-section 1.7 and sections 4 and 5 of this document.

The Contractor’s design shall show that there shall be sufficient process streams, units, equipment and control functions to ensure flexibility of operation and such that the Plant is capable of satisfactory operation with any critical process unit out of service.

The Contractor is required to perform supplementary geotechnical investigation works prior to preparation of Detailed design, in accordance with the Law on Spatial Development and Construction of Structures (51/08, 40/10, 34/11, 47/11, 35/13, 39/13 and 33/14).

### Inlet chamber

Wastewater from the Project Area shall be transferred to the WWTP through the main city gravity sewers, as described early.

The left bank main sewer is of DN500, while the right bank main sewer is of DN400. Both main sewers are designed and shall be implemented by using GRP sewerage pipes.

With regard to the sewerage system configuration it should be noted that there is going to be river crossing under the Lim River of the right-bank main sewer towards the WWTP site.

As a result, depth of the abovementioned main sewers at the WWTP inlet is quite considerable, with pipe invert elevations of the main sewers designed as follows:

- Left bank main sewer – pipe invert elevation 657.16 masl

- Right bank main sewer – pipe invert elevation 655.77 masl

It should be noted that the natural ground elevation at the location of the planned WWTP inlet is 659.50masl, while the final elevated WWTP plateau elevation which shall ensure adequate flood protection is defined at 662.50masl.

With regard to planned implementation of the sewerage system upgrade and extension, the beneficiaries arranged for preparation of the corresponding detailed design in accordance with the national regulations. This detail design can be inspected, upon request, in the premises of the final beneficiaries – Municipality of Berane.

The most downstream inspection manhole of the right-bank and of the left-bank main sewers represents the upstream limit of works for the design and construction for the WWTP Contractor, i.e. for the works included in this tender.

The inlet chamber is to be provided in the vicinity of the aforesaid most downstream inspection manhole of the main town sewers.

Physical features of the sewer inlet into the WWTP inlet chamber are presented in the following table:

Table 5-5: Physical features of the main sewer inlet into the WWTP inlet chamber

| Feature description | Value | Comment |
| --- | --- | --- |
| Pipe invert elevation | 655.70 masl |  |
| Natural ground elevation | app. 659.65 masl |  |
| Water level in the sewer/inlet chamber under regular operational condition | 655.77-657.66 masl | Regular operational conditions assume normal operation of the WWTP, by-pass not activated |
| Maximum allowable water level in the sewer under irregular operational condition | 658.70 masl | Irregular operational conditions assume that the WWTP is out of operation, by-pass line is activated, water level in the Lim River ≤ 658.00 masl |

Main purpose of the WWTP inlet chamber shall be to divert incoming wastewater towards the WWTP process line in regular operational conditions. However, if for justifiable reasons the main process line operates at a reduced capacity, or cannot operate at all (for instance long periods without power supply) there shall be a provision for safe transfer of incoming wastewater directly to the by-pass line and further towards the main outfall, provided that water level in the Lim River is below 658.00 masl.

From the inlet chamber wastewater is directed towards the coarse screens and subsequent lifting pumping station. The line towards the coarse screens shall be equipped with isolating sluice gate valve both manually and electrically actuated.

At the same time there shall be a by-pass line starting from the WWTP inlet chamber and connecting to the effluent discharge pipeline downstream of the effluent flowmeter. Between the main sewer inlet and outlet towards the by-pass line there shall be partition wall with a sharp-edged weir on top. This overflow weir should basically serve as a safety measure to prevent flooding in the area if, for any reason, the WWTP cannot accommodate incoming wastewater flows. This weir shall be equipped with stop-logs providing full water-tightness, i.e. preventing back-flow which for any reason may occur towards the incoming sewers.

There shall be a continuous water level measurement in the WWTP inlet chamber with an alarm that shall be activated when the water level approaches safety overflow elevation. At the same time this level measurement shall enable measurement of wastewater flows over the safety overflow weir by calculating flow based on recorded head on weir.

In the bottom part of the aforesaid partition wall there shall be an isolating sluice gate valve (invert level equal to invert level of the by-pass line) which should enable activation of the by-pass line by the WWTP operator whenever necessary. This isolating valve shall be both manually and electrically actuated.

The WWTP inlet chamber shall be constructed of reinforced water-tight concrete with adequate access covers and ventilation. Hydraulic capacity of the line between the inlet chamber and coarse screens must be equivalent to the Phase II peak wet-weather flow of 228 l/s.

Required features of the aforesaid safety overflow weir in the WWTP inlet chamber are defined as follows:

- Type - sharp-crested, hydraulically non-submerged for the water elevation in the Lim River of 658.00 masl)

- Maximum head on weir – 658.70 masl

- Typical (maximum) hydraulic loading - 228 l/s (Phase II maximum wet-weather flow)

    - By-pass pipeline

A by-pass pipeline is to be designed and constructed from the WWTP inlet chamber to the connection point with the effluent discharge pipe and to the outfall to the Lim River. Design capacity of the by-pass pipeline corresponds to the Phase II maximum wet-weather flow of 228 l/s.

Main functions of the by-pass pipeline are defined as follows:

- By-pass cannot be put in operation before commissioning of the WWTP:

- After the WWTP is commissioned and becomes operational main function of the by-pass line would be to transfer any surplus wastewater that cannot be accommodated by the WWTP in emergency/irregular operational regimes;

- The most downstream section of the by-pass pipeline shall be common with the effluent discharge pipeline.

The by-pass pipeline should be designed as a sewer, with free-surface flow most of the time, i.e. as long as the water level at the outfall does not cause backwater effect with partially pressurized flow in the pipe. The by-pass pipeline should be designed so as to provide free-surface flow with no backwater effect for all water levels at the outfall ≤ 658.00 masl.

The by-pass line must be designed so that for the water level at the outfall of 658.00 masl consequent water level downstream of the safety overflow weir does not exceed 658.50 masl, i.e. safety overflow weir is not submerged.

The by-pass pipeline and the effluent pipeline shall connect in a separate effluent chamber. The inlet of the by-pass pipeline into the effluent chamber shall be equipped with an isolating sluice gate valve, to be both manually and electrically actuated. During normal WWTP operation this isolating valve is closed.

The Contractor shall foresee convenient emptying and flushing of the by-pass line, in order to prevent septic conditions, and accumulation of sediment.

The by-pass line must be equipped with a separate flow-metering device, so that any discharge occurring in the by-pass line can be measured and recorded.

### Coarse screens

The inlet section of the wastewater lifting pumping station shall incorporate automatic cleaning coarse screens that shall remove coarse debris transported with incoming wastewater. The screens shall be equipped with cleaning mechanism – racks that shall operate automatically, based on differential head on the screen. The screenings after simple straining shall be automatically deposited into a 1m3 container for which a spare unit shall be provided.

This section shall comprise a receiving and distribution channel with installation channels for the screen units and effluent channel to the wastewater lifting pumping station. Raw sewage shall be introduced into the receiving and distribution channel and then evenly distributed into the individual installation chambers/channels of the screens. The screens shall be for open channel installation.

The channels are to be designed as open concrete channels of monolithic design with installation platforms. Isolating channel penstocks upstream and downstream of the screens as well as a complete covering with inspection manholes, access ladder and service platform with lifting devices for heavy equipment shall be provided. All channels shall be profiled in such a way that sedimentation of coarse matters is prevented. Sufficient flushing facilities (technical water) shall be provided.

With regard to the scope of works in this tender includes the following:

- Complete design for all types of works and equipment for Phase II capacity;

- Complete civil engineering works and equipment for the final, Phase II capacity;

- Installation of automatic screens in the channels with all appurtenant equipment and devices as required;

Table 5-6:  Coarse screens – basic design requirements

| Parameter | Unit | Phase I | Phase II |
| --- | --- | --- | --- |
| Population equivalent | PE | 20,000 | 27,000 |
| Peak dry weather flow, Q DW, max | m3/h | 294 | 380 |
|  | l/s | 82 | 105 |
| Peak wet weather flow to WWTP, Q WetW, max | m³/h | 615 | 820 |
|  | l/s | 171 | 228 |
| Number of units |  | 2 | 2 |
| Type of screens |  | Climber screen/grab-bar type, reciprocating /step screen or equivalent | Climber screen/grab-bar type, reciprocating /step screen or equivalent |
| Nominal design capacity of a single screen | (l/s) | 114 | 114 |
| Size of clear opening | mm | 30 | 30 |
| Flow velocity: 1) upstream of screen 2) between bars | m/s | ≥ 0.5 ≤ 1.2 | ≥ 0.5 ≤ 1.2 |
| Number of conveyors |  | 1 per screen line | 1 per screen line |
| Type of conveyor |  | Screw or belt conveyor | Screw or belt conveyor |
| Installation |  | Inlet channel upstream Lifting Pumping Station | Inlet channel upstream Lifting Pumping Station |
| Number of containers |  | 1+1 | 1+1 |
| Size of container | m3 | 1 | 1 |

### Lifting Pumping station

The lifting Pumping Station shall be constructed and fully equipped for the Phase II design capacity, i.e. for the ultimate design horizon.

The Pumping Station shall be equipped with submersible wastewater pumps transferring incoming wastewater into the fine-screens block and other downstream process units. The Pumping Station shall be equipped state of the art switchboards and frequency converters for all installed pumps. There should be a minimum of 2 operational pumps of equal characteristics in the Pumping Station delivering its full design capacity, plus one additional stand-by pump (of the same characteristics) that can be activated at any time in case one of operational pumps is out of order, being maintained, or similar. Operational range of each pump unit shall be 40 to 100% of their nominal capacity.

Operation/design of the inlet pumping station must not generate backwater effect, submergence, flooding or any other unfavourable effects on the upstream wastewater collection system in Berane.

The Contractor shall make provisions in order to verify all boundary conditions of importance for positioning and design of the Pumping Station, in particular as-built/design status of the incoming main gravity sewer.

The inlet Pumping Station shall be able to transfer the maximum design wet weather flow to the downstream process inlets. The following table includes basic design criteria for the inlet Pumping Station.

Table 5-7: Inlet Pumping Station – basic design criteria

| Parameter | Unit | Phase II |
| --- | --- | --- |
| Population equivalent | PE | 27,000 |
| Peak dry weather flow Q DW, max | m3/h | 380 |
|  | l/s | 105.5 |
| Peak wet weather flow to WWTP, Q WetW, max | m³/h | 821 |
|  | l/s | 228 |
| Nominal (total) design capacity of the pumping station | l/s | 228 |
| Number of units |  | 2+1 (min. 2 duty and 1 stand-by) |
| Type of pumps |  | Wastewater, Submersible |
| Pump control |  | By means of frequency convertors |

Operation control of the pumps shall be by means of frequency converters (FC) in relation to hydraulic conditions at the inlet, and in relation to the WWTP requirements. Individual pumps shall be switched “ON/OFF”, depending on operational requirements, in case of pump failure and also in order to equalize hours of operation hours of individual pumps an automatic changeover “Duty/Standby” shall be provided. Water level measurement in the wet-well shall be established as a continuous ultrasonic measurement (or equal), with transmission to the local PLC. In addition, each pump shall have its individual dry-run protection system. The local PLC shall be interlocked with the main operation control of the plant.

Apart from the regular power supply, in case of power cut, the inlet Pumping Station shall have provision of stand-by power supply by means of a stand-by generator set that shall provide power supply required for the pumping station full operational capacity.

The pumping station shall have a common discharge pipe which shall be equipped with an electromagnetic flowmeter that shall record wastewater flow towards the downstream process units on continuous bases and should serve for the overall control of the influent to the WWTP. There shall be appropriate manually operated isolating valves upstream and downstream of the aforesaid flowmeter in order to enable for maintenance, repairs, dismantling, etc.

### Fine Screens

Fine Screens shall be installed in a separate structure downstream of the lifting pumping station and upstream of the grit and grease removal chambers.

The channel upstream and downstream of the screens shall be covered in order to prevent malodour to spread into environment. The screens shall be enclosed in order to reduce emission of odorous air and provide extraction of odorous air to the odour treatment facility.

The screens shall be also provided with the conveyor for collection and delivering screenings to the washing and compaction unit before disposal into containers.

Washed and dewatered screenings and grit shall be disposed off to a controlled landfill. With regard to the scope of works for this tender, the fine screen block shall be designed and constructed as follows:

- Complete design for all types of works and equipment for Phase II capacity;

- Complete civil engineering works for the final, Phase II capacity;

- Installation of a automatic fine screens in channels with all appurtenant equipment and devices as required.

Table 5-8: Design parameters for fine screen block

| Parameter | Unit | Phase I | Phase II |
| --- | --- | --- | --- |
| Population equivalent | PE | 20,000 | 27,000 |
| Peak dry weather flow, Q DW, max | m3/h | 294 | 380 |
|  | l/s | 82 | 105 |
| Peak wet weather flow to WWTP, Q WetW, max | m³/h | 615 | 820 |
|  | l/s | 171 | 228 |
| Number of units |  | 2 automatic screens | 2 automatic screens |
| Type of screens |  | Climber screen/grab-bar type, reciprocating /step screen, wedge wire drum screen, or equivalent | Climber screen/grab-bar type, reciprocating /step screen, wedge wire drum screen, or equivalent |
| Size of clear opening | mm | 6 | 6 |
| Nominal design capacity of a single screen | (l/s) | 114 | 114 |
| Flow velocity: 1) upstream of screen 2) between bars | m/s | ≥ 0.5 ≤ 1.2 | ≥ 0.5 ≤ 1.2 |
| Number of conveyors |  | 1 per screen line | 1 per screen line |
| Type of conveyor |  | Screw or belt conveyor | Screw or belt conveyor |
| Screening press |  | 1 | 1 |
| Type of press |  | Screw press with spray mechanism and feed pipe | Screw press with spray mechanism and feed pipe |
| Compaction factor | % | Minimum 30 | Minimum 30 |
| Number of containers |  | 1+1 | 1+1 |
| Size of container | m3 | 1 | 1 |

Removal of screenings shall be arranged by means of automatically operated fine screens with appurtenant screenings conveyance and dewatering installed in the screen building.

The Preliminary treatment building shall accommodate fine screens and ancillary equipment, including separate room for blower station providing compressed air for Aerated Grit Chambers (AGT). In addition, the Preliminary treatment building shall allow for solid waste compaction and storage area (screenings and grit), and the local power sub-distribution and control room.

The screen section shall comprise a receiving and distribution channel with installation channels for the screens ending into the effluent channel towards the AGT. Incoming wastewater shall be directed into the receiving and distribution channel, evenly distributed into the individual installation chambers/channels of the screens. The screens shall be for open channel installation. There shall be two screens, total capacity of the Phase II.

The channels are to be designed as open concrete channels of monolithic design with installation platforms inside the screen house. Isolating channel gates upstream and downstream of the screens as well as a complete covering with inspection manholes, access ladder and service platform with lifting devices for heavy equipment shall be provided. All channels shall be profiled in such a way that sedimentation of coarse matters is prevented. Sufficient flushing facilities (service water) shall be provided.

The Contractor shall provide design enabling system operation in emergency cases, of complete failure of any of screens or duration of power failure longer than available capacity of diesel generator.

Screenings shall be discharged into screw conveyors with spraying/washout device for conveyance into subsequent screening presses, which may feed screenings containers, alternating.

Operation control of the screens shall be realized as a water level difference control with secondary timer-control for each individual unit that shall be considered by the local PLC. Under normal operational conditions automatic operation of the screens will be controlled by continuous measurement of the upstream and downstream water level in the installation channel. Depending on preset values for the water level difference control discontinuous operation of the cleaning mechanism shall be initiated. In addition, in case of failure or under low flow conditions the secondary timer control shall initiate regular cleaning of the screens. Operation of the screenings conveying system shall be synchronized.

The solid waste treatment and storage area shall consider space requirements for arrangement of the screenings containers as well as for the grit classifier and containers. A work safe and approved transportation system for the containers, i.e. rail-system or container carriers, shall be provided.

The special environmental conditions of raw sewerage treatment require construction of the concrete works with sulphate resistant concrete; finishing of floors and walls with ceramic tiles up to 2.0 meters above finished floor level; completion of all internal steel works (ladders, platforms, a.s.o.) shall be in stainless steel grade EN 1.4571; completion of all internal pipe work shall be in stainless steel grade EN 1.4571 or polyethylene (HDPE). With regard on possible emissions of hydrogen sulphide (H2S), bad odours and classification of the operation room as Ex-zone Ex1. It shall be made sure for sufficient ventilation of the screen house.

The third operational section of the fine screen building shall comprise a blower room for arrangement of at least n+1 blowers (rotary piston blowers) for grit chamber aeration: n=2. The blower room shall have sufficient size for installation of the blowers, local switchboards and compressed air pipework. It shall have sufficient natural lighting and ventilation; access shall be separate, from outside, only.

Low-voltage power supply and operation control of the mechanical treatment facilities shall be arranged in a separate control room located in the fine screen structure. It shall have sufficient size for installation of the required number of control cabinets for the individual electric drives, feeder and measuring cabinets of the local sub-distribution as well as control boards for PLC and measuring instruments. The local PLC shall be interlocked with the main operation control of the plant. It shall have sufficient natural lighting and ventilation; access shall be separately, from outside, only.

### Aerated Grit Chamber

The Grit Chambers shall be designed and constructed for capacity of Phase II. For grit and grease removal longitudinal aerated grit chambers with lateral grease traps and travelling suction scraper bridges shall be applied.

Table 5-9: Design Criteria for Aerated Grit Chamber

| Parameter | Unit | Phase I | Phase II |
| --- | --- | --- | --- |
| Population equivalent | PE | 20,000 | 27,000 |
| Peak dry weather flow Q DW, max | m3/h | 294 | 380 |
|  | l/s | 82 | 105 |
| Peak wet weather flow to WWTP, Q WetW, max | m³/h | 615 | 820 |
|  | l/s | 171 | 228 |
| Number of units |  | 2 | 2 |
| Type |  | Aerated longitudinal |  |
| Type of sand/scum removal |  | Scraper bridge or suction scraper |  |
| Separation efficiency |  | ≥ 95 % for Ø 0.25 mm |  |
| Minimum retention time at peak flow | s | ≥ 300 or separation of particles >0.25mm with 95% efficiency |  |
| Flow velocity, horizontal | m/s | < 0.2 |  |
| Grease trap surface load, qA | m/h | ≤ 25 |  |
| Width/depth ratio |  | 0.8 |  |
| Specific air requirement | Nm3/(m3∙h) | 0.5-1.3 |  |
| Diffuser depth | m | 0.7 x water depth |  |
| No. of blowers |  | 2+1 |  |
| Type of blowers |  | Rotary piston blower |  |
| Number of sand pumps |  | 2+1 |  |
| Type of pump/impeller |  | Submersible/vortex |  |
| Capacity | m3h | As per Contractor’s design |  |
| Number of scum pumps |  | 2+1 |  |
| Capacity | m3/h | As per Contractor’s design |  |
| Type of pump/impeller |  | Submersible/vortex |  |
| No. of Grit classifier |  | 1 |  |
| No of grit containers |  | 1+1 |  |
| Volume of grit container | m3 | 1 |  |

The AGT shall be designed as parallel operated chambers. Isolating channel gates in the influent and effluent sections of the grit chambers shall be considered. Inspection manholes, access ladders and service platforms with lifting devices for heavy equipment, and coverings shall be provided accordingly. All channels shall be profiled in such a way that sedimentation of coarse matters will be prevented. Moreover sufficient flushing facilities (service water) shall be considered.

The aeration system of the grit chambers shall comprise horizontally installed tube aerators, blowers and air distribution pipework, c/w. all required fittings and armatures. The blowers are to be installed in a separate blower room. It shall have sufficient size for installation of the blowers, local switchboards and compressed air pipework with natural lighting and ventilation.

Travelling service bridge equipped with scraping blades for discontinuous sand and scum removal shall be installed.  Scrapers and scum blades are to be assembled at the travelling service bridge, one set per each chamber. Sand is removed from the bottom of the sand trap by scraping it into sand hopper from where it is extracted by pumps. Height adjustable scum blades shall be provided for the grease traps in order to remove scum layers into grease pits at the front side of the tanks.

Optionally, the sand removal system shall be designed for application of a suction scraper system comprising travelling bridges with suction pump which discharge the sand from the bottom sand trap into a lateral effluent channel, which conveys the flow into a sand pumping station at the front side of the tanks.

A grit classifier shall be provided for sand washing and dewatering, which shall be installed in the screen building, where screenings compaction unit and storage containers are placed. Classified grit shall be fed into grit containers, which shall be provided in a sufficient number.

Conveyance of the sand-water mixture from the sand hoppers or the sand pumping station at the grit chambers into the grit classifier shall be applied by air-lift pumps or submersible pumps. Submersible pumps to be applied for sand conveyance shall be in special, abrasive resistant design of pump-body and impeller.

Separated scum and grease shall be discontinuously discharged from the grease pits at the grit chambers by submersible pumps. The liquid phase shall be returned to the wastewater flow, while the solids shall be disposed in separate closed containers.

Operation control of the travelling scraper bridge shall be realized by means of a PLC unit with timer control of the operation sequences, installed in a local switchboard, which is assembled onto the bridge with power supply via a motorized cable reel. The operation of the grit and scum discharging systems, incl. grit classifier and screen, shall be synchronized accordingly.

Completion of all submerged metal parts and pipework shall be in stainless steel grade EN 1.4571; completion of all connecting pipework and shall be in polyethylene (HDPE).

### Influent Flow and Quality Measurement

The Influent Sampling and Flow Measurement facilities shall be designed and constructed for the capacity of Phase II.

Table 5-10:  Flow measurement – basic design criteria

| Parameter | Unit | Phase I | Phase II |
| --- | --- | --- | --- |
| Peak dry weather flow Q DW, max | m3/h | 294 | 380 |
|  | l/s | 82 | 105 |
| Peak wet weather flow to WWTP, Q WetW, max | m³/h | 615 | 820 |
|  | l/s | 171 | 228 |

Control of pH-value and temperature shall be located in the inlet/distribution chamber. Additionally, an automatic sampling unit shall be installed. Basic design requirements are set in the following table.

Measuring devices shall be microprocessor-controlled with temperature compensation, provided within a weatherproof housing, with local display and remote transmission to the PLC/operation control centre. Online monitoring instruments for continuous measurement of certain influent quality parameters such as pH/conductivity/temperature shall be applied.

An automatic sampler shall be provided with arrangements to take flow proportional 2-hour-composite or 24-hour-composite samples.

All signals shall be processed by the control centre (PLC-control-system) of the preliminary treatment facilities at the screen building and shall be furthermore transmitted to the main operation control centre of the plant.

### Equalization Tank

Equalization tank shall be located downstream of the grit and grease removal chambers. Main function of the equalization tank shall be to balance variations of wastewater inflow from the upstream process unit (preliminary treatment) and transfer of wastewater to the downstream units (biological treatment). Effective volume of the equalization tank shall be sufficient to accommodate the least favourable operational regime (both Phases I and II to be considered) in terms of differential inflow and outflow, including provision for accommodation of 1.5-hour inflow of the wet-weather component of the incoming flow. In any case effective volume of the equalization tank shall be ≥ 900m3. Size and detail design of the equalization tank shall be defined at the design stage.

The equalization tank shall be designed and constructed in accordance with the WWTP Phase II capacities and requirements. The aforesaid tank shall be designed as a semi-berried water-tight reinforced concrete structure.  The tank shall be hydraulically shaped (slopped slabs and walls, and similar) so as to prevent settling of suspended solids in wastewater. The tank shall be covered with a top slab with adequate access covers and adequate ventilation and odour removal devices. The tank shall be also equipped with adequate mixing devices in order to prevent settling within the tank volume as well as flushing and cleaning devices (high-pressure water jetting or similar).

Wastewater from the equalization tank shall be transferred to the biological treatment by means of a SBR feed pumping station that shall be placed next to or within the tank. The tank shall have a safety overflow provision capable of evacuating maximal differential flow in case that the SBR feed pumping station is out of operation.

Table 5-11:  Equalization Tank – basic design criteria

| Description | Unit | Phase I | Phase II |
| --- | --- | --- | --- |
| Peak dry weather flow, Q DW, max | m³/h | 294 | 380 |
|  | l/s | 82 | 105 |
| Peak wet weather flow to WWTP, Q WetW, max | m³/h | 615 | 820 |
|  | l/s | 171 | 228 |
| Effective volume | m³ | In accordance with the Contractor’s design, ≥ 900m3 |  |
| Safety overflow provision |  | Gravity discharge capacity ≥ 228 l/s to the by-pass pipeline, for Q1% flow in the recipient (Z water level=660.85masl), |  |

### SBR Feeding Pumping Station

SBR Feeding Pumping station shall be constructed for the Phase II project horizon, but equipped for the Phase I project horizon.

The SBR feeding Pumping Station shall be able to transfer the maximum design dry weather flow, including returned supernatant liquor. The following table includes basic design criteria for the lifting Pumping Station.

Table 5-12: SBR Feeding Pumping Station – basic design criteria

| Parameter | Unit | Phase I | Phase II |
| --- | --- | --- | --- |
| Peak dry weather flow Q DW, max | m3/h | 294 | 380 |
|  | l/s | 82 | 105 |
| Pump type |  | submersible | submersible |
| Drive |  | VFD (FC) | VFD (FC) |
| Number of units in operation |  | Minimum 3 | Minimum 4 |
| Number of stand-by units |  | 1 | 2 |

In addition to operating units, one stand-by unit equal characteristics shall be provided. Operation control of the pumps shall be by means of frequency converters (FC-VFD) in relation to hydraulic conditions at the inlet, and in relation to the WWTP requirements. Individual pumps shall be switched “ON/OFF”, depending on operational requirements, in case of pump failure and also in order to equalize hours of operation of individual pumps an automatic changeover “Duty/Standby” shall be provided. Water level measurement in the sump shall be established as a continuous ultrasonic measurement (or equal), with transmission to the local PLC. In addition, each pump shall have its individual dry-run protection system. The local PLC shall be interlocked with the main operation control of the plant.

Apart from the regular power supply, in case of power cut, the lifting Pumping Station shall have provision of stand-by power supply by means of a stand-by generator set that shall provide power supply required for the pumping station full operational capacity.

Appropriate lifting device shall be considered for installation and maintenance services.

### Biological Treatment Processes

The biological treatment shall be based on suspended growth activated sludge process with nutrient removal and aerobic sludge stabilisation. All facilities as required by Contractor’s design for the Phase I shall be constructed end fully equipped with provision of space for extension in the Phase II.

Tenderers are required to propose technical solution in accordance with the Employer’s requirements, with enclosed complete calculations and provided with sufficient details of the proposed technology in order to enable a full and complete evaluation to be made.

Activated sludge process shall be designed in accordance with DWVK ATV-131, with provisions for carbon and nutrient removal, as specified in required effluent quality. Therefore, advanced wastewater treatment concerning biological nitrogen and phosphorous removal shall be considered. In order to enhance phosphorous removal provision of flocculant agent (FeCl3) shall be foreseen.

Provided sludge age shall correspond to low loaded activated sludge systems, in order to provide nutrient removal.

Table 5-13:  Activated sludge process – basic design criteria

| Parameter | Unit | Phase I | Phase II |
| --- | --- | --- | --- |
| Peak dry weather flow Q DW, max | m3/h | 294 | 380 |
|  | l/s | 82 | 105 |
| Loads |  |  |  |
| Inlet BOD5 | kg/d | 1,200 | 1,620 |
| Inlet TSS | kg/d | 1,400 | 1,890 |
| Inlet TKN | kg/d | 220 | 297 |
| Inlet P | kg/d | 36 | 49 |
| Effluent requirements |  |  |  |
| Effluent BOD5 | mg/l | 25 | 25 |
| Effluent TSS | mg/l | 35 | 35 |
| Effluent N | mg/l | 15 | 15 |
| Effluent P | mg/l | 2 | 2 |
| Additional Load by supernatant |  |  |  |
| BOD5 | % | Per Contractor’s design | Per Contractor’s design |
| COD | % |  |  |
| Ammonia (Ntot) | % |  |  |
| Phosphorous (Ptot) | % |  |  |
| Total Suspended Solids, TSS | % |  |  |
| Design Criteria |  |  |  |
| Design temperature for N elimination | °C | 12 |  |
| Minimum sludge age for N elimination | d | 10 |  |
| Minimum sludge age for aerobic sludge stabilization including nitrification and deliberate denitrification | d | 25 |  |
| MLSS | kg/m3 | 4-5 |  |
| Oxygen load | kg O2/kg BOD5 | ≥ 3 |  |
| Type of mixing equipment |  | submersible |  |

With simultaneous aerobic stabilisation the settleable solids which reach the wastewater treatment plant with the raw wastewater and the waste activated sludge formed with the biological wastewater treatment are stabilised simultaneously in a reactor in a process step with the biological removal of carbon and nitrogen compounds. For an extensive stabilisation of the sludge a high sludge age is necessary, which can be realised process-technically through a long aeration time and a sufficiently high activated sludge content in the simultaneous aeration or stabilisation tank.

The Contractor is required to check winter temperature of the wastewater during preparation of Detailed design. The design shall present the optimum layout arrangement of the plant facilities with regard to space occupancy, accessibility, system flexibility and future extension of the plant, easy and cost-effective operation and maintenance, maximum oxygen transfer efficiency and energy efficiency of the proposed equipment.

Activated sludge process shall take place in Sequencing Batch Reactor (SBR), in accordance with DWA M-210. The SBR shall be fully automatic to maximise control of energy and to optimize sequencing of all activities between reactors taking into account variations in flow rates to the plant.

SBR tank shapes, aeration, as well as mixing systems for Phase II, shall be designed to:

- maximize oxygen introduction into the wastewater at minimal energy costs,

- avoid/minimize wastewater spraying/splashing/generation of aerosols prevent sludge sedimentation

- allow for removal of Nutrients

- allow aerobic stabilization of sludge

Sequencing Batch Reactor (SBR) shall incorporate scum removal devices which shall be located in the corner of each basin in such a way that the prevailing wind drives the scum and floating matter toward the removal device. The scum removal device may be manually operated or automatic.

The decanting device shall be designed to collect and discharge clarified effluent from the SBR, properly sized to prevent vortex and withdrawal of settled sludge and shall be provided with skimming device to prevent breach of scum or other floating matter into clarified effluent. In addition to these, an automatic turbidity measurement device shall be installed at the effluent outlet in order to control clarification.

SBR tanks shall be provided with service platforms (bridges) for installation and maintenance of the mixers, submersible pumps or other equipment within the tank. Platforms shall be of sufficient space, protective rail and all necessary accessories for installation of mixers for future nutrient removal requirements.

Adequate mixing of the SBR volume shall be provided by installation of submersible mixers. Operation control of the denitrification process shall be achieved by means of a combined Redox/DO control using an automatic controller. On-line measurements are required for each individual basin.

A lifting davit of sufficient capacity to lift the equipment installed in SBR, such as submersible mixers, pumps, etc. shall be provided for maintenance services per two subsequent tanks.

Table 5-14:  SBR – basic design criteria

| Parameter | Unit | Phase I | Phase II |
| --- | --- | --- | --- |
| Peak dry weather flow, Q DW, max | m3/h | 294 | 380 |
|  | l/s | 82 | 105 |
| Number of units |  | 3 | As per Contractor’s design |
| Number of cycles per day |  | 3 | 3 |
| Effective depth | m | ≤ 6 | ≤ 6 |
| Decanter capacity | m³/h | As per Contractor’s design | As per Contractor’s design |
| Decanter drive |  | Electric motor or hydraulic drive |  |

The facilities for Phosphorous removal shall be designed based on chemical precipitation of phosphorous or biological phosphorus removal, enhanced with chemical precipitation.

The chemical dosing facilities for phosphorous precipitation shall be provided and designed for the following loads and design criteria under consideration of respective pre-treatment efficiencies and internal re-load from sludge recycling.

Table 5-15:  Criteria for Phosphorous removal

| Parameter | Unit | Phase I | Phase II |
| --- | --- | --- | --- |
| Peak dry weather flow, Q DW, max | m3/h | 294 | 380 |
|  | l/s | 82 | 105 |
| Number of units |  | 3 | As per Contractor’s design |
| Influent P-load | kg/d | 36 | 72 |
| Required effluent concentration | mg/l | 2 | 2 |
| Precipitant |  | FeCl3 or equal |  |
| Storage time for FeCl3 tank | month | 1 |  |

Storage and dosing facilities shall be located indoor, close to SBR. Operation control of the dosing process shall be flow/proportional with preset dosing rates of the manually adjustable dosing pumps.

Waste sludge (excess sludge) shall be discontinuously removed from the system and shall be transferred to excess sludge balance tank, upstream the sludge treatment facilities. Each SBR shall be provided with a submersible pump, complete with accessories and guide bar, for extraction the waste activated sludge (excess sludge). Pumps shall be provided with VFD.

The pump sump shall be profiled in such a way that sedimentation of coarse matters will be prevented. The special environmental conditions require completion of all internal steel works (ladders, platforms, a.s.o.) shall be in stainless steel grade EN 1.4571; completion of all internal pipe work shall be in stainless steel grade EN 1.4571 or polyethylene (HDPE).

Table 5-16:  Excess sludge pump – basic design criteria

| Parameter | Unit | Phase I | Phase II |
| --- | --- | --- | --- |
| Type |  | submersible | submersible |
| Drive |  | VFD | VFD |
| Capacity | m3/h | As per Contractor’s design |  |
| Number of units in operation |  | one per each tank | one per each tank |
| Number of stand-by units |  | 1 in storage | 1 in storage |

Oxygen supply shall be realized by system of compressed air. An aeration system comprising non-clogging membrane aerators, compressed air supply and distribution pipework with blowers for compressed air generation are to be provided. A sufficient number of disc aerators which are to be installed on a certain number of aerator panels, shall be distributed over the bottom surface in such a way that an area-covering arrangement of the aerators can be made sure. Aerator panels shall be provided with a drain system and shall be connected to the supply pipe individually via separate shut-off devices. A blower station for compressed air generation shall be constructed close to the SBR. At least two DO-meters (dissolved oxygen content measurement) for continuous monitoring of the content of dissolved oxygen inside the SBR volume shall be provided for each tank. Operational control of the aeration systems of the individual tanks shall be achieved by control of the blower capacity in accordance to the measuring value against a pre-set standard value. Therefore the electric motors of the blowers shall be provided with frequency converters.

Special attention has to be paid in the design regarding the change of any pipework under the biological tanks for removal/maintenance.

Low-voltage power supply and operation control shall be arranged in the adjacent blower house. The local PLC shall be interlocked with the main operation control of the plant.

For situation with complete failure of the main electricity supply and where standby electricity supply has to be used the aeration system shall limit aeration to that equivalent to average dry weather flow.

Aeration of the mixed liquor in the oxidation and nitrification stage shall be achieved by diffused air aeration equipment. Fine-bubble membrane diffusers are preferable to coarse-air bubble aeration.

The aeration system should be of high efficiency and should have a capacity to cover the oxygen demand at any time and any possible situation in the biological stage by dissolved oxygen concentrations of 2.0 mg/l.

Table 5-17:  Aeration system – basic design criteria

| Parameter | Unit | Phase I |
| --- | --- | --- |
| Oxygen Supply |  |  |
| Type of aeration |  | Fine bubble |
| Type of aerator |  | Disk/membrane |
| Diffuser depth | m | ≤ 6.0 |
| Design wastewater temperature | °C | 20/12 |
| Design air temperature | °C | 30 |
| Altitude | 660 | masl |
| α-value |  | 0.5 – 0.6 |
| Oxygen yield - membrane aerators | g O2/m3N/ m | ≤ 20 |
| Type of blowers |  | Rotary Piston/Turbo Blower variable speed |
| Number of blowers |  | n+1 |
| Number of DO meters per tank |  | 2 |

When a single blower per tank is used, it should be sized to provide maximum aeration under worst-case conditions. These conditions typically occur in the summer months, when higher temperatures decrease the amount of oxygen that can be dissolved in wastewater. For facilities that utilize a single blower per tank, a variable frequency drive shall be considered.

The aerator oxygen transfer rate shall be certificated by the Contactor and the Manufacturer with respect to the aerator performance, both in terms of oxygen input and efficiency in kg oxygen per kWh into clean deoxygenated water at 30° C.

### Blower Station

The Blower Station shall be constructed adjacent to the biological tanks. The blower house shall consider two sections for the installation of the blowers with ancillary equipment and local control panels, and the local power sub-distribution and control room.

The blower room shall be designed in such a way that the requirements for noise control and working security will be fully meet. Therefore each blower shall be provided with a sound protection hood. Access to blowers and components (such as valves and local control panels) shall be secure and unhindered. The blower room shall be provided with an overhead crane for installation and service requirements. With regard on the waste heat production of the blowers, sufficient ventilation and natural lighting shall be provided.

Low-voltage power supply and operation control of the biological treatment facilities shall be arranged in a separate control room located at the blower house. It shall have sufficient size for installation of the required number of control cabinets for the individual electric drives, feeder and measuring/marshalling cabinets of the local sub-distribution as well as control boards for PLC and measuring instruments. The local PLC shall be interlocked with the main operation control of the plant. It shall have sufficient natural lighting and ventilation with access from the blower room and from outside.

### Effluent Sampling

The Effluent Automatic Sampling Station shall be designed, supplied and installed in Phase I. Monitoring of the treated effluent quality shall be applied in accordance to the National legislative requirements and Urban Wastewater Directive 91/271/EEC at the effluent channel.

For laboratory analysis & monitoring of the treated effluent an automatic sampling station in a closed cubicle for installation of 12 sample bottles with automatic probe pump, probe distribution in order to complete composite samples, incl. sufficient ventilation, shall be installed on a service platform close to the effluent manhole.  The sample will be analysed for as a minimum, COD, BOD, TSS, NH4-N.

### Effluent discharge pipeline

Effluent discharge pipeline is to be constructed from the SBR units to the final disposal point – outfall to the Lim River. The most downstream section of the effluent discharge pipeline shall be common for treated effluent and by-pass line flow discharge. Connection of these two lines shall take place in a separate chamber, where the by-pass line shall be normally separated by the isolating sluice gate valve.

Upstream of the aforesaid connection chamber on the effluent discharge pipeline there shall be an effluent flowmeter which shall be of open-channel type, Parshall flume type or similar.

The effluent flowmeter shall be a fixed hydraulic structure used in measuring volumetric flow rate in the wastewater treatment plant, and industrial discharge applications. The Parshall flume accelerates flow though a contraction of both the parallel sidewalls and a drop in the floor at the flume throat. Under free-flow conditions the depth of water at specified location upstream of the flume throat can be converted to a rate of flow. Effluent discharge flows shall be measured on a continuous basis by an ultrasonic flow meter or flume system. The minimum accuracy shall be ± 2% full scale deflection.

The effluent discharge pipe shall be design in such a manner as to ensure hydraulically favourable conditions for the aforesaid effluent flowmeter, even for the specified high water level in the Lim River of 660.85 masl.

Maximum design capacity of the effluent discharge pipeline shall be 230 l/s.

### Sludge BufferTank

The excess sludge withdrawn from the SBR tanks shall be collected in a storage tank and pre-thickened on mechanical gravity belt thickener prior to dewatering.

Excess sludge will be discontinuously discharged by the extraction pumps into sludge storage tank. Sludge buffer tank shall be used for synchronisation of the excess sludge discharge cycles of the activated sludge system and the operation time of the mechanical thickening facilities. Tank shall be provided with agitator for intermittent operation as well as height adjustable supernatant discharge device.

Supernatant shall be returned back to wastewater treatment process by gravity. The sludge volume shall be mixed and homogenized discontinuously in intervals in order to prevent compaction of sludge on the tank bottom.

The tank shall be covered and odorous air shall be extracted and treated at the odour treatment facility. Covers shall be made of glass-fibre reinforced polyester resin or similar lightweight material of sufficient hardness and resistant to corrosion and external loads.

Table 5-18:  Waste Sludge Storage Tank – basic design criteria

| Parameter | Unit | Phase I |
| --- | --- | --- |
| Type |  | Concrete tank, with light covering, equipped with agitator for intermittent mixing |
| Dry solids content of feeding sludge | % | 0.7 - 1 |
| Tank volume |  | As per Tenderers design |
| Number of tanks |  | 1 |
| Effective height of the tank | m | As per Tenderers design |
| Type of feeding pumps |  | Positive displacement |
| Number of feeding pumps |  | n+1 |

### Sludge Thickening

The Sludge shall be conditioned with polymer and fed into a feed/distribution box, where the sludge is distributed evenly across the width of the moving belt.

Table 5-19:  Sludge Thickening – basic design criteria

| Description | Unit | Value |
| --- | --- | --- |
| Type |  | Mechanical gravity belt thickener with light covering or drum thickner |
| Dry solids content of feeding sludge | % | 0.7 - 1 |
| Operation time weekly | d/w | 5 |
| Operation time daily | h/d | 8 |
| Solids content in thickened sludge | % | minimum 5 % |
| Number of units |  | 1+1 |
| Type of feeding pumps |  | Positive displacement |
| Number of feeding pumps |  | 1+1 |
| Flocculation agent |  | Organic polymer |
| Number of polymer dosing pumps for sludge thickening |  | 1+1 |
| Type of polymer dosing pumps |  | Positive displacement |

The Mechanical sludge thickening facility shall comprise sludge thickening machine with sludge feeding pumps, equipment for automatic preparation and dosing of polyelectrolyte with dosing pumps and in-line mixers, and local switchboards. Each thickening machine shall be provided n + 1 feed pumps from the positive displacement type and its own dosing station.

In order to prevent odour, each mechanical thickening device shall be covered and odorous air extracted and treated at odour treatment facility.

The waste sludge shall be fed to the mechanical thickening machines by individual suction and pressure pipework. Each suction pipe shall be equipped with an inductive flow measurement device (EFM) for continuous sludge flow measurement with registration, remote transmission, and operation control of the sludge thickening process.

Eccentric (positive displacement) dosing pumps with (FC) shall be provided for dosing of organic polymer for sludge conditioning. Polyelectrolyte dosing control shall be flow proportional against a preset standard ratio, which depends on the particular sludge characteristics and which shall be determined during trial operation.

Filtrate shall be piped by gravity into the supernatant pumping station of the WWTP.

The sludge thickening facilities shall be located in an operation building for the installation of the machinery with ancillary equipment and local control panels, and the local power sub-distribution. The operation room shall be designed in such a way that all requirements for noise/odour control and working security are fulfilled. Access to the machines, pumps and components (such as valves and local control panels) shall be secure and unhindered. The operation room shall be provided with a crane hoist for installation and service requirements. With regard on the humid environment in the operation room sufficient heating, ventilation and natural lighting shall be provided.

The area where sludge thickening facilities are installed shall be enclosed, provided with air extraction fan and ducts transporting odorous air to odour treatment facility.

Low-voltage power supply and operation control of the mechanical dewatering facilities shall be arranged in a separate control room. It shall have sufficient size for installation of the required number of control cabinets for the individual electric drives, feeder and measuring cabinets of the local sub-distribution as well as control boards for PLC and measuring instruments. The local PLC shall be interlocked with the main operation control of the plant. It shall have sufficient natural lighting and ventilation with access from outside, only.

All piping shall be executed in stainless steel grade EN 1.4571 or HDPE/Polypropylene pipes. Inspection manholes, access ladders and service platforms with lifting devices for heavy equipment, and coverings shall be provided accordingly.

Polymer dosing shall be applied for the thickening process. The Contractor shall demonstrate during commissioning and performance testing that the mixers in the storage tank achieve a uniform consistency.

### Septic Sludge Reception Station

For acceptance of septic sludge by means of sludge trucks the septic sludge shall be pumped to a storage tank. The septic sludge reception station shall provide one discharge spot for one septic tanker and shall be equipped with an automatic cleaned coarse screen (50 mm). Screenings will be disposed in a container while the remaining sludge will be stored in a tank from where it will be pumped in portions into the head of the WWTP. Due to high concentration of dry solids, pumping capacity shall not exceed 2% of average plant inflow. Monitoring system for wastewater load downstream injection point shall be provided.

The Septic Sludge Reception Station has to be able to accept a daily delivery up to 20 m³/d. The net tank volume shall be of sufficient volume to store the given maximum daily septic sludge delivery

Table 5-20: Septage Sludge Reception Station – basic design criteria

| Description | Unit | Value |
| --- | --- | --- |
| Type |  | Compact screening and pressing septic receiving station with light cover |
| Dry solids content of feeding sludge | % | 5 |
| Operation time | months/ year | 12 |
| Daily amount | m3/d | 20 |
| Solids content | % | 1.5 |
| Number of units |  | 1 |
| Type of transfer pumps |  | Submersible |
| Number of transfer pumps |  | 1+1 |
| Number of containers |  | 1 |

### Sludge Dewatering

This facility comprises all necessary structures and installations for the sludge dewatering and return of the drained water to inlet structures of the plant. The sludge dewatering facilities shall be sized to facilitate capacity of the plant within the first phase.

It shall comprise but not limited to the following process units:

Mechanical Sludge Dewatering;

Dewatered Sludge Acceptance Area;

Power supply and connection to main control centre;

Related infrastructure connections;

Interconnecting pipework & cabling

Protective covers / hoods, if applicable, preventing spreading of odorous air into environment

The Mechanical Sludge Dewatering Facility shall comprise sludge dewatering machines with sludge feeding pumps, the polymer dosing stations and in-line mixers, and local switchboards.

Sludge dewatering facilities shall be sized to treat the average weekly production when operated 8 hours per day, 5 days per week.

The sludge shall be conditioned with polymer in order to achieve the required dry substance concentration for dewatered sludge.  An in-line mixer insures the mixing of the sludge and the polymer prior to the mixture entering dewatering facility.

The polymer preparation unit is comprised of the tank equipped with agitators, dry polymer volumetric dosing screw, and control cabinet, connection for service water and safety overflow. The polymer solution is pumped into the sludge feed line by polymer dosing pumps.

Table 5-21:  Sludge Dewatering Facility – basic design criteria

| Description | Unit | Value |
| --- | --- | --- |
| Type |  | Belt filter press |
| Dry solids content of feeding sludge | % | 3-5 |
| Operation time weekly | d/w | 5 |
| Operation time daily | h/d | 8 |
| Solids content in dewatered sludge cake | % | minimum 25 |
| Number of units |  | 1+1 |
| Type of feeding pumps |  | Positive displacement |
| Number of feeding pumps |  | 1+1 |
| Flocculation agent |  | Organic polymer |
| Number of polymer preparation units |  | 1+1 |
| Number of dosing pumps for sludge dewatering |  | 1+1 |
| Type of polymer dosing pumps |  | Positive displacement |

The excess water from the sludge dewatering is returned back into the wastewater treatment process, by gravity.

The polymer preparation unit shall be supplied with service water for preparation of the polymer suspension. Final effluent may be used for further dilution and as carrier water. Dewatered sludge cake shall be withdrawn from the machine discharge device into containers for sludge cake temporary storage before final disposal.

The sludge dewatering facilities shall be located in an operation building that shall be comprised of two sections for the installation of the machinery with ancillary equipment and local control panels, and the local power sub-distribution and control room. The operation room shall be provided with a crane hoist for installation and service requirements.

Containers for dewatered sludge handling shall be placed in a separate room in order to prevent spreading of odour into environment. Odorous air shall be extracted and treated at odour treatment facility.

Low-voltage power supply and operation control of the mechanical dewatering facilities shall be arranged in a separate control room. The local PLC shall be interlocked with the main operation control of the plant. It shall have sufficient natural lighting and ventilation with access from outside, only.

### Odour Control Plant

The principal odour sources shall be covered and ducted to odour control plant via a forced air ventilation system. For those areas with normal access by plant personnel, to ensure a proper working atmosphere, an air exchange cycles of 6-12 volumes per hour shall be foreseen. For closed atmospheres without access for plant personal such as grit and grease chamber and storage tank an air exchange cycles of 4-6 volumes per hour shall be sufficient.

In order to avoid corrosion of concrete and metal parts avoid areas without normal access shall be ventilated furthermore the concrete used for such areas shall be resistant to H2S. The Contractor may propose higher air exchange rates.

The areas considered as principal odour sources that are to be provided with odour treatment are:

- Coarse screens and Lifting pumping station

- Preliminary Treatment building

- Compensation tank with SBR feeding pumping station

- Septic sludge reception tank

- Waste sludge storage tank

- Sludge thickening and dewatering building

Table 5-22:  Required Air exchange rates (ATV-M 204)

| Building | air exchange rate [volumes/ hour] |
| --- | --- |
| Non-passable area | 3-4 |
| Passable (non-working) area | 4-6 |
| Working area | 6-12 |

Odour Control equipment suitably sized for the process requirements shall include the following features:

- Odour Control plant shall be covered in order to protect the filter material from rain and sunlight. Furthermore sprinkler utilities shall be foreseen to avoid a dry-out of the filter material during summer season.

- Hoods and covers to contain odours shall be installed at the odour source along with adequately supported ducting to convey the odorous air to the treatment units.

- Access and measurement points shall be included in hoods and ducting. Quick release catches are to be fitted to the covers and hoods which shall be lift able by one person without the use of crane wherever possible.

- Ducting systems shall include provision for flow balancing on multi-extraction source systems and shall incorporate condensate traps fitted with accessible manual drain valves. Ducting shall be routed above ground level.

- Odour extraction fans shall be of the axial or centrifugal type suitable for use in zone 1 hazardous area. The fan rating shall be adequate to extract from all parts of the odour controlled space via the system ducting.

- The Contractor shall design the odour control plant to treat the foul air to a quality that will allow the permitted odour concentrations at the site boundary to be met.

A maximum surface load of 150m³/m² for biological odour control plant shall be fulfilled. The Contractor is expected to carry out an odour survey of the site and modelling of the odour emissions prior to the detailed design of the odour control plant.

### Hazardous Area Study

The Contractor shall carry out a Hazardous Area Study and include for suitably rated plant in any Hazardous Area.

### Vehicles and Miscellaneous Operational Equipment

The Contractor shall supply the following new vehicles for operation of the wastewater treatment plants.

The vehicles shall not be used by the Contractor during the execution of the construction works. All trucks, vehicles, special vehicles necessary for the sound operation of the plant, at least but not limited to:

Table 5-23:  Vehicles for operation of WWTP

| Vehicle Main Features |  |
| --- | --- |
| Type | Details |
| Pick-up | (4+1 passengers), Minimum engine size 2000 cc |
| Container loader | For disposal of screen, grit and sludge, Diesel Engine |
| Fork Lift Truck | 1.2 ton capacity, diesel engine |
| Combined mini tractor | Power take off of no less that 25 kW, closed cabin with heating and ventilation, with lawn cutter, snowbrush, snow-plough, hydraulic front-loader) |

Consumable spares (oil filters, brake pads etc.) shall be supplied for the operation of these vehicles during two years or 30 000 km whichever is the longer, after Take-over. All Vehicles Supplied by the Contractor must be clearly identified, and visibly carry the MNE licence tag. All vehicles shall be covered by a five year guarantee.

Process guarantee

### Introduction

The Contractor shall guarantee that the WWTP shall achieve at all times the requested performance criteria included in this Section. The plant shall comply with the applicable effluent discharge criteria, while staying below an operational costs limit, which shall be guaranteed by the bidder.

The corresponding guarantee schedule is included in Volume 4 – Section 2 Schedule of Guarantees and shall be completed by the Tenderer, duly signed and stamped. This schedule shall become part of the Contract.

### Definitions

Tests on Completion and Commissioning Period

Pre-commissioning and commissioning tests: All civil, mechanical, electrical and control components and related functions are finished, tested dry and wet, found in compliance with the contract conditions and accepted by the Engineer.

Trial operation: The technically completed plant starts operation and biomass is built up to design level. This period is under the responsibility of the Contractor.

At the end of the commissioning period and when stable operation is reached, the works are handed over to the Beneficiary (Taking-Over Certificate )

Defects Liability Period

The period of 12 months immediately following the date of provisional acceptance, during which Beneficiary operates the plant, while the Contractor is required to remedy defects or faults as instructed by the Engineer.  At the end of the defects liability period and under the condition that all defects have been successfully remedied Performance Certificate shall be issued.

Process and Operational Cost Guarantee Period

The process and operational cost guarantee period is 12 months starting at the upon issuing of the Taking-Over Certificate  This Guarantee Period runs in parallel with the Defects Notification Period. The Contractors pays periodical visits to the plant to monitor the compliance of guarantees and propose remedial actual if required.

### Process Guarantee Conditions

#### Wastewater Treatment

The WWTP shall be designed for the capacity as indicated in the table below.

Table 5-24: Design Flow and Load Parameters for Process Guarantees

| Parameter | Unit | Phase I |
| --- | --- | --- |
| Wastewater flow QDW | m³/d | 4,540 |
|  | l/s | 53 |
| Peak dry weather flow Q DW, max | m3/h | 294 |
|  | l/s | 82 |
| Peak wet weather flow to WWTP, Q WetW, max | m³/h | 615 |
|  | l/s | 171 |
| Population Equivalent |  | 20,000 |
| BOD5 | kg/day | 1,200 |
| COD | kg/day | 2,400 |
| TSS | kg/day | 1,400 |
| TN | kg/day | 220 |
| TP | kg/day | 36 |
| Average pollutant concentrations in wastewater |  |  |
| BOD5 | mg/l | 264 |
| COD | mg/l | 29 |
| TSS | mg/l | 308 |
| TN | mg/l | 48 |
| TP | mg/l | 8 |
| Effluent standards |  |  |
| BOD5 | mg/l | 25 |
| COD | mg/l | 125 |
| TSS | mg/l | 35 |
| TN | mg/l | 15 |
| TP | mg/l | 2 |

The Bidder hereby guarantees that the effluent from the plant after the Commissioning Period will meet the effluent standards given in Table 5-25: Effluent Standards for Process Guarantees.

The process guarantee shall cover the running of the plant under different flows and loads ranging from 100 % to 60% of the design capacity as given in Table 5-24.

Table 5-25: Effluent Standards for Process Guarantees

| Parameter | Unit | Value |
| --- | --- | --- |
| BOD5 | mg O2/l | 25 |
| COD | mg O2/l | 125 |
| Total suspended solids | mg/l | 35 |
| Total Nitrogen (total organic plus inorganic) | mg/l | 15 |
| Total Phosphorous | mg/l | 2 |

Control of the effluent meeting the standards shall be performed according to the EU Urban Wastewater Directive 91/271/EEC  (Annex I, Table 3).

The corresponding guarantee values shall be declared in Volume 4, Section 2.

In the event of incompliance with the declared water treatment guarantee values, penalties shall be applied by the Employer and /or the Final Beneficiary.

#### Sludge Treatment

The performance of the sludge treatment line shall be guaranteed on the basis of the following parameters that shall be declared by the Bidder.

Percentage of guaranteed dry solid contents in the thickened sludge

Capacity of sludge dewatering unit

Percentage of guaranteed dry solid contents in the dewatered sludge

Use of polymer for mechanical thickening and for dewatering

The corresponding guarantee values shall be declared in Volume 4, section 2.

In the event of incompliance with the declared guarantee values, penalties shall be applied by the Beneficiary.

Table 5-26: Sludge Treatment Requirements for Process Guarantees

| Parameter | Unit | Value |
| --- | --- | --- |
| Sludge stabilization |  | aerobic |
| Minimum dry content in the thickened excess sludge | % | ≥ 5 |
| Polymer type (100 % active substance) |  | as per the Tenderer’s design |
| Polymer dose for sludge thickening | kg/t dry matter | as per the Tenderer’s design |
| Polymer type (100 % active substance) |  | as per the Tenderer’s design |
| Polymer dose for sludge dewatering | kg/t dry matter | as per the Tenderer’s design |
| Dry solids content in dewatered sludge | % | ≥ 25 |

### Guaranteed Operational Costs

#### Introduction

The Bidders are required to guarantee the operational costs for the technical solution that they are proposing for the WWTP in Berane.

This is necessary for the bid evaluation with respect to the whole life costs of the plant, which consists of the investment costs and the net present value of 20 years of operational costs. At current discount rates the net present value factor equals to 14, resulting in the following formula:

Whole Life Costs = Investment Costs + 14 * Yearly Operational Costs

The winning Tender shall be one that is compliant with the administrative and technical requirements and has the lowest whole life cost.

The principal operational costs to be taken into account are those for electricity, for polymer usage for mechanical sludge thickening, for sludge dewatering as well as for sludge disposal. For the purpose of evaluation simplicity, the costs for personnel, maintenance of civil and electromechanical works, depreciation, etc, are not considered in the operational costs guarantee.

#### Energy Consumption Guarantee

The guarantee for energy consumption shall be provided in kWh as the annual consumption of the WWTP.

The energy consumption shall be determined for the design capacity of the plant.  However after plant commissioning and  taking over, the actual load of the plant during the guarantee period is expected to be lower that the design capacity.  To allow a fair comparison between the guaranteed value and the actual energy usage during the guarantee period, the consumption shall be differentiated between 3 load situations of the WWTP, being 100%, 80% and 60% of the annual BOD load.

For each load situation, the guarantee values shall show the total yearly energy consumption. The annual guaranteed values shall refer to the 12-month DNP, between the issuing of the Taking-Over and Performance Certificates.

The determination of the compliance with the energy consumption guarantee done by comparing the achieved energy consumption with the guaranteed energy consumption at the measured load condition (interpolated between the 100%, 80% and 60% load condition as required).

The Tenderer shall complete the corresponding table in the Guarantee Schedule Volume 4, Section 2.

#### Operational Cost Guarantee

The Tenderer shall formally present his estimated operational costs as completed forms in Volume 4. The Tenderer shall complete the corresponding table in Volume 4, Section 2. The Tender will be evaluated on the basis of Net Present Value as calculated in Volume 4.

Incompliance with the guaranteed operational costs shall be subject to penalties.

#### Tests

##### Pre-commission and Commissioning Tests (Test on Completion)

Pre-commissioning and Commissioning Tests (Tests on Completion) are performed when all civil, mechanical, electrical and control components and functions are finished, tested dry and wet, found in compliance with the contract conditions and accepted by the Engineer for start of the trial operation.  Remedy of defects shall be done according to the decision of the Engineer before or under the trial operation.

##### Trial Operation

During a period of at least 6 months after the tests on completion and start of operation, the biomass is built up to the design level and full excess sludge production takes place.  The efficiency of the plant is controlled by taking flow proportional 24 hours samples of influent and treated effluent, when appropriate, according to request of the Contractor and approval of the Engineer.  Routine analyses (effluent standard analysis and inhibition measured as BOD on diluted samples) are performed by the Contracting Authority/Beneficiary at their costs under supervision of the Contractor.  Special analyses requested by the Contractor are performed according to agreement between the Contractor and the Engineer.  The costs for special analysis shall be carried by the Contractor as long as the result does not show important influence of the analysed parameters on the processes of the plant. After the successful completion of the trial period, the Taking-Over certificate shall be issued.

##### Tests on Process Completion

Subsequent to the trial operation period, fourteen sets of consecutive flow proportional 24 hours influent and treated effluent samples shall be taken.  When the effluent standards are met by all parameters in all samples the plant is finalized in respect of the process functioning and can be taken over.  If any sample fails to meet the effluent standards, the tests on process completion continue until fourteen samples meet the effluent standards.

##### Tests on Process Guarantee

During the 12 month long guarantee period, the Employer/Beneficiary will carry out 24 hours flow proportional sampling and analyses of the influent and treated effluent according to the national regulations. The sampling and analyses will be performed during two (2) periods of four (4) weeks each.  The results shall be monitored by the Contractor on site, as defined in chapter 11.

The Employery/Beneficiary shall immediately inform the Contractor in case a result indicates that the effluent standards cannot be met to provide the Contractor the possibility of immediate remedy arrangements.

The Employer/Beneficiary and the Contractor shall agree on a procedure to find the reason if one or several parameters do not meet the effluent standards and the exceeded values are indicating that the process guarantee cannot be met.

Performance tests shall be carried out for two periods of four weeks each over the 12 month period: four weeks during the coldest months (January/February) and four weeks during the warmest months (July/August).  If the Works do not achieve the required performance requirements during a testing period, the period of continuous operation shall be recommenced until trouble-free continuous operation is achieved for a period of four weeks.  The objective of the performance testing will be to confirm that the works will fully meet the performance requirements with the loads at commissioning and at the Phase I design horizon.

Samples shall be taken daily, i.e. 28 samples over each 4 week period. No more than 3 non-conforming samples shall be permitted.

The test shall be carried out both with the actual loads at commissioning and with the Works configured to simulate as far as is possible the hydraulic and BOD loads that will occur at the Phase I design horizon.

The performance tests shall be deemed to have been satisfactorily completed if the following have been achieved:

The final effluent quality and emission standards for odour and noise meet the specified performance requirements

The quantity of energy consumed is within the limits stated in the Contractor's Guarantees.

The specified system of control is suitable for automatic operation of the whole works and that the operational parameters can be maintained within the specified range.

In addition to the parameters specified in the performance requirements the following data shall be recorded on a daily basis throughout the period of performance testing:

Weather conditions: temperature, barometric pressure, humidity, wind direction and precipitation.

Influent flows, final effluent flows, sludge recycle rate, and return liquors return rate.

Influent wastewater and return liquors quality (i.e. concentration of sanitary parameters).

Quantities of screenings, grit, and sludge.

Physical characteristics of influent wastewater e.g. temperature, colour, odour

Any relevant visual observations on performance of biological treatment processes, e.g. activated sludge biomass, presence of foaming, etc.

Consumption of chemicals, electrical energy, fuel and potable water.

If the tests fail due to non-compliance with the above criteria, or do not attain the specified minimum process requirements or the Engineer is not satisfied that the operational parameters can be maintained, the Contractor shall:

Identify the reason for the failure,

Put forward written proposals for rectification,

Obtain written approval from the Engineer for these proposals

Rectify the problem and re-test.

If the effluent standards meet the requirements during the Process Guarantee Period the Performance Certificate shall be issued at the end of this period.

The test for the standard aeration efficiency in kg O2/kWh shall be performed in accordance with the German Advisory Leaflet ATV – M 209 or equivalent Standards, Codes, Manuals or Regulations. Clean water tests shall be performed.  The checks are considered satisfactory if the determined SAE do not vary by more than 5% of the guarantee value. Two series of check measurements shall be performed. The average results shall be taken.

The minimum concentration of solids shall be checked by taking and analyzing 20 grab samples. 18 out of 20 samples shall achieve the guarantee values.

Tests on Consumption of Energy:

Compliance with the guarantee is controlled by calculation of the annual load and wastewater flow to the WWTP during the guarantee period:

The daily load is calculated by multiplying the concentration in the composite inlet sample with the corresponding daily wastewater volume measured at the outlet on the days when samples and analyses are performed.

The average daily load is calculated as the average of the daily load determinations.

The annual load is calculated as 365 multiplied by the average daily load.

The annual amount of wastewater volume is the measured amount at the outfall.

Based on the calculated annual load and the wastewater volume, the guaranteed maximum energy consumption is calculated. The guaranteed maximum energy consumption is compared to the measured energy consumption. If the measured annual energy consumption is equal to or lower than the guaranteed maximum energy consumption the guarantee is fulfilled.

After the first 6 months of operation after “Process Completion Period” the actual energy consumption shall be compared with the guaranteed consumption.  The energy consumption shall be corrected for any improvements executed by the Contractor according to agreement between the Contractor and the Contracting Authority/Beneficiary.

#### Remedial Actions

##### Process

In case the effluent does not meet the standards and the process guarantee comes into force the Contracting Authority/Beneficiary shall immediately raise a claim to the Contractor. Within 30 days after receipt of a claim the Contractor is obliged to submit a project proposal to improve the function of the plant so the process guarantee can be met. The same procedure shall apply with respect to the performance of the sludge treatment system.

When the Contracting Authority/Beneficiary has accepted the project proposal to improve the function of the plant, the Contractor shall perform at his own costs the accepted project proposal as fast as technical possible.  The accepted project proposal shall be finalized within a maximum of 6 months.

After a new Running-in Period of maximum 3 months from finalization of the improvement, new Tests on Completion shall take place and a new process guarantee period of 12 month starts. In the event that the Tests continue to fail, the whole procedure shall be repeated.

Where the Beneficiary incurs costs in the form of penalties from the national authorities for failure of the effluent to comply with the Standards and these failures are shown to be due to the failure of the plant to meet the guarantee, then these costs will be recovered from the Contractor, through the demand of payment from the performance guarantee.

#### Operational Costs

If the measured monthly energy consumption is higher than the guaranteed energy consumption, taking into account the plant load conditions, and no unusual events have happened as explanation for the overrun of the energy consumption, the guarantee comes into force and the Employer/Beneficiary shall immediately raise a claim to the Contractor.

Within 1 month after receipt of a claim the Contractor is obliged to submit a project proposal to reduce the energy consumption of the plant so the guarantees can be met, if the guarantee is not met in the meantime.

When the Employer/Beneficiary has accepted the project proposal to reduce the energy consumption of the plant, the Contractor shall perform, at his own cost, the accepted project proposal as quickly as technically feasible.  The accepted project proposal shall be implemented within a maximum of 2 months.

If at the end of the guarantee period for operational costs, the measured cost for electricity is still higher than the guaranteed value, the Contractor shall have to pay a penalty to the Employer/Beneficiary for the difference between the measured and guaranteed operational costs, multiplied by 14 (discount factor for 20 year operational costs), to compensate for the losses caused to the Final Beneficiary.

# ELECTRICAL, INSTRUMENTATION AND CONTROL DESIGN REQUIREMENTS

  - Scope of Works

The term "Electrical Systems" shall mean Contractor obligation under the Contract to cover complete system design all manufacturing, procurement and delivery, assembling and installation, testing and commissioning of the required power supply, power distribution and sub-distribution systems for the process units, which shall be performed by the Contractor.

Contractor shall also be responsible for Electrical power supply from the public mains network, including all coordination and technical clarification with the responsible power supply companies.

The following shall be included, but not limited to, within the limits of the Works:

- MV Power supply from the nearest MV 10kV Zaostro overhead distribution line. In accordance with Local Location Study in adjacent of future WWTP plot there is existing 10 kV; 50 Hz, overhead line. Location Study foreseen Power supply of the future WWTP Transformer Station with underground MV cable in accordance with the terms and recommendation of Division for Energy Distribution “Elektroprivrede Crne Gore” a.d. Nikšić

- WWTP Transformer station shall be located on the plot as a separate facility with the following characteristic: 10/0,4 kV, 2x630 kVA, with MV and LV switchgear, power transformers, main low voltage (LV) distribution board and associated equipment included in the contract.

- Low voltage main distributions, reactive power compensation units, battery systems, safety and protection devices, etc.;

- Standby power supply, from diesel generator set equipped with ATS automatic switch. In the event of public network malfunction, important consumers shall be supplied from the Main distribution cabinet feed by generator (MDC-G).

- Low voltage systems, c/w separate low tension distributions at all process stages with switch gear panels; control systems for manual, automatic, local and remote control; PLC units; marshalling cabinets; safety and protection devices, etc.;

- Instrumentation

- Complete SCADA, process control and instrumentation system, incl. all instruments required to supervise and control the various process stages, control systems, control centres at all major process sections, building security, building intrusion, fire fighting etc.;

- Outdoor lighting

- Lightning protection

- HVAC installation and building service described in Volume 3 Section 3

- Bi-directional telecommunication control system between control points and local control centre.

  - MV Power Supply

According to the Local Location Study for ”Donji Talum” for Construction of WWTP in Berane, and Preliminary Electrical Design, future WWTP Transformer Station shall be feed from neighbour MV overhead line by two underground cables buried directly in the ground. Where cable route crossing road cable shall goes trough HDPE 100mm protection pipes covered with concrete MB200, 20cm high above pipes. Additional one spare pipe foreseen. Two three phase single core systems are foreseen with cable type  XHE 49-A 3x(1x120mm2) or XHE 49-A 4x(1x150mm2). Contractor shall determine cables routes and other necessary details in cooperation with local power supplier.

The Employer/Beneficiary shall be responsible for liaising with the local power supplier (Elektroprivreda Crne Gore), while the Contractor shall execute all  for works (including civil and building works) associated with supply and installation of the power supply cables. These works shall be carried out in accordance with the Employer’s requirements, but shall also take into account the conditions issued by the relevant local power supply authority.

  - Transformer Station

According to the Local Location Study for ”Donji Talum” for Construction of WWTP in Berane and Preliminary Electrical Design future Transformer Station 10/0,4 kV, 2x630  kVA shall be situated on the WWTP plot.

Transformer station building shall be of prefabricated type, providing enough space for installation of equipment and safety distances, as well as proper cooling of power transformers. Within the transformer station, there are:

- High voltage switchgear 10kV.

- Low voltage switchgear 0,4 kV

- Dry Energy transformers 630kVA, 10/0,4kV (2 pcs)

### MV Switchgear

Industrial distribution substation 10/0,4kV, 2x630kVA, designed to be equipped with a middle-voltage compact switchgear block. In order to attain flexibility regarding future capacity extension of the WWTP and higher energy needs, the Transformer Station building is designed to accommodate two dry transformers, as stated in the attached layout plan of the project.

The Switchgear 10kV shall consists of modular, metal-clad, air insulated, type attested cells for indoor installation, rated voltage 12kV, rated current 630A, short-circuit withstand (1 sec) 16kA. The Switchgear shall be freestanding against the wall, with front side doors with a possibility of easy switchgear extension (installation of new cells) or configuration change.

The plant consists of the following modules (cells), respectively: two Incoming Switch Units, current and voltage measurement unit and two transformers switch-fuse combination units.

Switch Units and Switch-fuse Units with earthing switch shall be insulated by SF6 gas of the low pressure (relative overpressure 0.4 bar) in the hermetically closed housing of epoxy resin, not requiring any maintenance. The device is mounted horizontally along the cell, so the position of the main contacts and contacts for earthing is clearly visible from the front side of the cell. Position indicator is mounted directly to driving axle.

The basic technical data of the middle voltage switching block are:

- nominal voltage 12 kV

- nominal current of the busbars 400 A

- nominal frequency 50 Hz

- means for insulation and arc prevention: SF6 gas

- nominal arc pressure 0,2 bar (20˚C)

- environment temperature:

- nominal atmospheric impulse withstand 125kV

- nominal one-minute impulse withstand 50 Hz, 50 kV

- nominal short-term bearable current 12,5 kA/1s

- nominal specific bearable value of the current 31,5 kA

- breaking current (conducting fields)

- nominal .... ................................. . 630A

- unloaded cable...... ………………...50A

- grounding...... ………………............90A

- capacitive to grounding...…………..52A

- breaking current (transformer field)

- nominal……………………………..200A

- unloaded transformer.........………..20A

- short-circuit………………………...16kA

Cable feeders (leads), as well as the transformer field may be accessed only if the tree-position switch in that field in the “earthing” position, so the doors are unblocked and the access to cable and fuses is possible.

Voltage indicators, located at the front part of the field, containing ports for checking of the sequence of phases by the phase comparator, are used for control of voltage presence.

The switching block is equipped with:

- power-off coil 220 V AC,

- capacitive voltage indicator,

- short-circuit indicator,

- pressure indicator of the SF6,

- handle for turn on disconnecting devices and grounding contacts.

Transformer field switch-fuse combination unit is equipped with three-position switch-disconnection with earthing switches (on-off-earthing) with fitted fuse holders and high-performance fuses with firing pin. On MV cable there is an additional earthing, mechanically coupled to the earthing switch-disconnection, enables earthing of the cable even in cases of fuses burn out. Switch-disconnection are manually operated, with accumulated energy and parallel trigger (switch off coil). Switch-disconnection has an option of a three-pole switching off at burn out of at least one high-performance fuse (by firing pin), as well as acting of basic protection against internal failure of the transformer as well as the manual switching off by the button located on the front panel.

The transformer cell equipped with:

- a vacuum switch of 12 kV, 630 A, 21 kA

- disconnector with grounding blades and a 220 V AC disconnecting trigger,

- electronic protection relays with a current transformer of 80/1 A

- three-phase bus bars

- voltage indicator

- grounding blades on the lower side

- dry cable joint

Measuring field shall be used for connection of feeding transformer fields and placement of measuring equipment required for measuring of consumed energy. It shall be equipped with current and voltage measuring transformers with corresponding reduce factor.

The measuring cell shall be equipped with:

- 2 current measuring transformers 100/5A, 0.5 category; 7.5 VA

- 2 voltage measuring transformers 10/√3/0.1/√3/0.1/3 kV kl.0,5; 30 VA with integrated fuses

- three-phase bus bars

On the Volume 5 Drawings single line diagram of middle voltage switchgear is shown.

### Power transformer

There should be a dry-type energy transformers with self-cooling, power 630kVA and transfer ratio of 10kV2x2,5% /420V, coupling Dyn-5, frequency 50 Hz, with installed 6 PTC sensors + Z-converter (protective relay delivered with transformer and mounted in the distribution board of the low voltage), anti-vibration devices, interface for connection to armoured  rail distribution 1600A.

Transformer is placed on special mounts of extruded steel profiles and steel bent sheet metal through floor opening. Transformers are in accordance with the IEC 76-1...5, IEC137 and IEC354 standards.

The link between transformer and low voltage is achieved by prefabricated armoured rail distribution, with degree of protection IP55 and in accordance with IEC 60439-2 standard.

There should be cooling of energy transformer by natural airflow through the openings-blinds on the entrance door of the substation department.

Protection of transformers at 10kV side is done with a corresponding high voltage high-performance with firing pin that automatically turns the three-pole power disconnector, 12kV, 630A, located in the substation cell. At the low voltage side, the protection of transformer from overload and short circuit is done with automatic switch of nominal current of 1600A with micro-processing protective unit with an option to set the parameters.

Transformer characteristics are:

- 10/0, 4kV, 630 kVA, 50 Hz, Dyn5 coupling

- possibility of  voltage regulation  ±  2.5%  and  ±  5%,

- Short-circuit voltage of 6%.

Transformer shall have a visible plate with the technical data. Transformer`s housing equipped with separate connections for grounding via (M12 bolt).

### Bus bar System

The low voltage installation consists of a standard LV block for the connection of future consumers.

The  equipment  is  installed  in  a  low-voltage  distribution  block  of  0.4kV  and  has  the

following technical characteristics:

- nominal voltage 0,4 kV

- nominal current of the bus bars 2000 A

- nominal drain current depending on the consumers

- nominal short-term bearable current at 0.4 kV; 25 kA/1 s

### Main LV distribution board

High power, metal enclosed bus bar system composed of type tested, prefabricated elements shall be applied for LV distribution from power transformers to main low voltage distribution board. It is intended for use as a part of TN-C/S earthing system, and rating current in accordance with rated power of transformer. Short circuit ratings shall comply with calculated prospective values.

The inlet field of the LV block 0.42 kV contains the following equipment:

- low voltage switch type Micrologic 2000 A;

- the current measuring transformers (T1-T3) with a transmission relation 1500/5 A, class 0,5, shall be placed at the low-voltage inlet, from the transformer side;

- in the same field there shall be installed the measurement elements: the universal measuring  instrument  with  microprocessor, display,  functional keyboard and the possibility of connection via MODBUS  communication  (optional card for connection  to  a  MODBUS),  that  measures:  current,  phase  and  line  voltages, frequency, active and reactive and apparent power, active and reactive energy.

- on the front door of field +N2, together with the main low voltage switch, there shall be installed a push-button  for  the  emergency  power-off  of  the transformer  on  the primary side.

In field +N1 there shall be installed:

- serial terminals,

- voltmeter, lighting and socket fuses in a plastic case, 250 V,16A,

- installation fuses for the local protection of circuits,

- multifunctional meter for the consumption of electric energy, 5 A, 100 V

Field +N4 shall be equipped with:

- copper bus bars 3x100x10 + 50x10 mm, installed at suitable distance,

- 6 low-voltage drains with fuses, namely:

- 5 x  400A 3P,

- 1 x  630A 3P,

- 1 low voltage drain for the connection of the reactive energy compensation board, with a 630A 3P fuse.

### Reactive power compensation

In order correct power factor and to reduce the cost of the electricity centralized automatic reactive power compensation needs to be achieved by three phase capacitor banks controlled by electronic regulator. Batteries shall be equipped by integral discharge resistors, and switched via three pole contactors designed for that purpose. Expected level of current harmonic distortion shall be taken into account when designing capacitor banks. This equipment shall be installed either as a part of incoming cubicles, either as a separate cubicle connected to LV bus bars. In both cases, summary power factor of a plant, derived from account metering has to have minimum value of 0.95.

Estimated condenser batteries shall be of total power app. 225 kVAr (5x45 kVAr). Contractor shall calculate real necessary value in according to accepted solution.

  - Standby power supply

In case of network power failure, critical consumers need to be supplied from diesel generator set. Its rating needs to be chosen in a way that minimum level of process along water treatment line at phase I of construction can be maintained during eight hours of power failure. The Contractor shall specify the facilities to be supplied from diesel generator in case of power failure. The capacity of the generator shall be determined by the Contractor based on the installed capacity of the offered equipment and the required power needs during a mains power failure observing also the Employer’s Requirements.

The minimum capacity of the diesel generator set shall be calculated based on the power requirement of the equipments given below, but excluding standby units:

- Inlet pumps: 						100% of installed capacity

- Coarse and fine screens: 					100% of installed capacity

- Mixers and blowers: 					50% of installed capacity

- Excess sludge pumps: 					100% of installed capacity

- Site lighting, control room: 					100% of installed capacity

- SCADA, instrumentation: 					100% of installed capacity

- General indoor lighting                                                          30% of installed capacity

- General installation of socket outlets                                      10% of installed capacity

Step load is permitted, under condition that duration of supply pause will not jeopardize above criteria. During standby supply, output voltage of generator must satisfy specified allowable limits (RMS, frequency and distortion) for proper work of connected consumers. Besides manual, control panel of a gen-set must be able to allow a remote start as well.

  - Electrical Distribution System

The Contractor shall design and install the site LV electrical distribution system based one central distribution board, including motor control centres (MCCs) and distribution boards located as necessary around the site.

The Contractor shall be responsible for determining the rating of all  switchgear and motor control gear sufficient for the requirements of the plant as detailed elsewhere in this specification. Besides, selectivity between protection equipment from source to end consumer must be achieved, resulting in reliable operation and short downtime. Dimensions of the distribution cabinets should be based on the required space for appropriate storage and connecting of the provided equipment, including 20% of the spare space.

The power distribution boards and motor control centres shall be manufactured in accordance with the Volume 3 -1 –Section 4 General Specifications for Electrical Works and SCADA.

Devices foreseen for installation in rooms & open space that are potentially endangered by explosive atmosphere or materials and therefore assigned to an "Ex-Zone" shall be approved for use in such locations. Devices for Ex-zone 1, like the channels for wastewater, shall be dimensioned according to DIN VDE standard 0170 part Ex d IIB T3 respectively part EEx i IIB T3, if not otherwise required. International and Montenegro applicable standards are: EN 50014 and EN 60079.

In order to place the cables smoothly, through the facility buildings, they shall be laid down in cable trays installed on suitable manner and in compliance with relevant standards, roles and technical recommendations.

Requirements for power cables described in detail in the Employer’s Requirements (Volume 3-1, Section 4)

  - Motor Control Centres

Motor control centres (MCCs) shall be provided and installed for the supply, monitoring and control of all electric drives. The MCCs shall be designed and manufactured in accordance with the Volume 3-1, Section 4 .

Disposition of MCCs and power distribution shall follow process logic and consist of the following blocks:

- Inlet structure with Raw Water Pumping Station, screens equipments, grit and grease removal equipments

- Equalization tank with feeding pumps

- Biological treatment equipment with air compressors

- Sludge treatment & Dewatering equipments

- Administrative and Computer monitoring and control centre with SCADA facilities

Special caution needs to be taken in regard of MCCs room ambient conditions in order to prevent MCCs equipments damages caused by aggressive gases, temperature, presence of moisture or water.

For the smooth operation of the plant all major engines shall be managed by frequency converters.

Programmable logic controller (PLC) shall operate and control MCCs field. PLC shall also transmit necessary information and measured values into the control Centre or another PLC in the WWTP.

UPS (uninterruptible power supply) shall be used for the power supply of all control, measuring and regulating devices.

  - Outdoor lighting

Internal road has to be illuminated with proper level of illumination derived from long lasting, high efficient light bulbs (high pressure sodium for example), mounted in luminaries for outdoor installation, on steel pole. If a supervision and/or access to some facilities needed, it must be properly illuminated additionally if necessary.

  - Earthing System

The Contractor shall provide an earthing system for the plant, equipment and buildings being installed under the Contract.

TN-C/S earthing system will be applied for protection of indirect touch, with circuit breakers and residual current devices (if necessary) as protection devices. Specially, for protection of semiconductors and measuring equipment, using of fuses is permitted.

Besides properly sized protective conductors, earthing conductors and equal potential bonding shall be installed. During civil construction phase, earthing conductors shall be embedded in concrete foundations wherever is possible, providing long lasting, low resistance earthing. Equipotent bonding needs to be done in a way which provides reliable mechanical connection, and with materials avoiding detrimental electrochemical effects. All earth bars shall be suitably interconnected and shall be connected to the main LV earth point so as to create an equal potential zone covering the entire site.

  - Lightning Protection

The Contractor shall provide lightning protection for the plant, equipment and buildings fully in accordance with the Volume 3-1, Section 4. Additional attention has to be given to areas and rooms classified during design phase as potentially explosive (Ex zones), if any. For indoor lightning protection of electrical equipment, surge arresters shall be installed.

  - Package Plant

Where the Contractor proposes package or skid mounted plant to perform a process or service function, the package plant shall comply with the  Volume 3-1, Section 4  and the following:

- Where package plant is installed within a hazardous area the associated electrical control gear and control panels shall wherever practical be installed in a safe area. Where installation within a hazardous area is necessary the Contractor shall ensure that electrical equipment installed is appropriately rated. Equipment shall be installed strictly in accordance with the conditions stated on the classification certificate.

- Electrical power and control equipment forming part of a package plant shall be located such that it is accessible for maintenance with the minimum of disturbance to process operations.

- Signals connected to the SCADA system shall be provided to monitor the operation and status of the package under normal and fault conditions. Conditions that cause the package plant to shut down either in part or in full shall, prior to the shutdown occurring initiate a pre-alarm signal. A fault alarm shall be initiated when a shutdown occurs. Pre-alarms and faults shall be indicated on the local panel as well as on the SCADA system.

- Process interlocks (inhibits) or protection interlocks from instrumentation, plant or equipment external to the package plant, shall be indicated on the package plant control panel or on the adjacent MCC common control section MMI.

- Package plant located in areas where the ambient or operational conditions are such that the operation or maintenance of the associated switchgear and control panels cannot be carried out safely and without inconvenience shall have the switchgear and control panels located in the plant MCC. The package plant equipment so located shall comply with the design and construction requirements of the MCC. In such cases local control stations shall be provided adjacent to the plant and incorporate the necessary control pushbuttons and selectors to operate the plant during maintenance or commissioning. Where individual drives forming part of the package may require operating during maintenance of the package plant then additional local controls for such drives shall also be provided.

The Contractor shall provide for each item of package plant a functional design specification, which shall be submitted, to the Engineer for approval prior to manufacture and purchasing commences. The Contractor shall include the following material as a minimum:

- Contents list.

- Reference to supporting standards, manuals and specification.

- Description of the design and design criteria.

- Relevant details of associated mechanical, electrical and instrumentation equipment.

- Functional description (control philosophy)

- Complete set of supporting drawings

- Design documentation which shall include as a minimum:

- An English and Montenegrin language description of each major element of the control scheme.

- A flow chart or ‘pseudo-code’ description of each sequential element of the control scheme.

- An analysis of the modes of failure and shutdowns procedures.

- Where a PLC or configurable device is to be provided the Contractor shall provide hard copy documentation of all configurable data, all user accessible source code i.e. control program code etc, and database contents including listings. All programmed listings shall be clearly constructed and provided complete with comments so as to convey to the reader a full understanding of the function of the program. So-called ‘self documenting’ code without additional supplementary comments shall not be acceptable.

- Calculations.

- Description of quality control methods and approvals.

- Outline of test procedures.

- Literature for each item of equipment supplied.

The above document shall be updated as necessary during the Contract and form part of the final take-over documentation.

  - Building Services

### General

The Contractor shall design and install building services (lighting, heating socket outlets, HVAC systems etc.) within all new structures, buildings, rooms etc. to be provided by the Contractor under the Contract.

Power supply of the Building Services consumers shall be done from separate distribution cabinets, one field of which shall be used for placement of controllers for automatic regulation and control.

Distribution cabinets for Building Services consumers shall be free standing or wall mounting (depending on the quantity of built-in equipment) made of sheet, composed of required number of fields, with front doors. Inside of the distribution cabinets there shall be energy protective and switchgear equipment for each individual source. At the supply cables of the distribution cabinet there shall be a switch with a trigger for switching off, and signalization of the voltage presence  (phases L1, L2 and L3). Engine terminals are equipped by a combination engine circuit breaker – contactor, and other terminals by circuit breakers or circuit breakers and contactors.

A certain number of general lighting devices, 30% shall be connected to diesel-generator, especially in communications space (stairs and corridors).

In the event of a complete power outage in the administrative building and facilities for pre-treatment, there shall be installation of panic lighting with operating autonomy of 3h.

In mechanic spaces, power substation, administrative building and diesel premises there shall be installation of service outlets alternative energized by diesel generator.

The building services shall comply with the requirements of the Volume 3-1, Section 4.

### Internal Lighting

The Contractor shall design and install lighting throughout the site in accordance with the requirements of the general specification (high efficient light bulbs). The installations shall be designed to provide suitable lighting for safe access, maintenance, operations and functioning of the plant and equipment as appropriate for each area. Detail Design requirements described in Volume 3-1, Section 4.

### Heating Ventilation and Air conditioning (HVAC)

The Contractor shall design and install HVAC systems as required in accordance with the requirements of the general specification. The installation shall be designed to provide suitable HVAC systems for personnel to operate the plant and equipment as required.

The Contractors design shall make due allowance for the seasonal variation in temperature on the site.

### Small Power

The Contractor shall provide mains and safety electrical low voltage socket outlets throughout the works. These shall be environmentally rated to be suitable for the area in which they are installed.

### Computer home network

The Contractor shall design and install WWTP Computer home network systems. The installation shall be designed to provide suitable home Computer WWTP network systems to enable personnel staff comfortable operation of the plant. Contractor will design and install equipment for communication nod TN-0. Following equipments shall be installed:

- Switch 8 port RJ45 cat6, with 2 SFP Mini GBIC slots

- Copper SFP MINIGBIC module TX/RX (for TN-27)

- Optic module TX/RX for MM fibres

- Finishing optical box, for reserve optic cable, 12 SC adapters, splice box, etc.

LAN network shall include administrative building and workshop, performed by structural shape cabling with UTP 4x2x0.5 mm2 cable cat6.

### Telephone installation

The Contractor shall design and install WWTP home telephone systems. The installation shall be designed to provide suitable home telephone systems to enable personnel staff comfortable operation of the plant. Contractor will design and install following equipment:

- Home digital automatic telephone central unit console type for installation in 19'' rack with 4 public lines up to 16 extensions.

- Power supply via UPS - 6 hours autonomy.

- UTP cable cat6, 4x2x0.5 mm2 – structural cabling

- Digital telephone devices

Telephone network shall include administrative building and workshop.

### Fire Detection and Alarms

Analogue addressable fire detection and alarm systems shall be provided in all occupied buildings to be provided under the contract including but not limited to the following:

- All rooms in Administration and Control Building

- Screen building

- Workshop / store

- Thickening and Dewatering Building

- Blower building

The system shall comprise call points, smoke detectors and rate of rise temperature detectors as appropriate, with local audible and visual alarms, local control panels and repeat alarms to SCADA,

The fire alarm systems shall be interlocked with the appropriate ventilation systems within each area to shut the systems down on detection of fire or smoke, and where applicable shut down plant.

### Intruder Alarms

Analogue addressable Intruder alarm systems shall be provided in all occupied buildings to be provided under the contract including the following:

- All rooms in Administration and Control Building

- All process, control and mechanical rooms

The system shall comprise proximity readers, door controllers, lock mechanisms, cameras, communication interface and auxiliary equipment.

  - Instrumentation

This section and the general specification describe the minimum requirements for and the general location of instrumentation.

All instruments shall display their values in SI system engineering units e.g. flow in litres/sec depth in metres etc. This will apply to local/remote indication on site on the MMI graphic displays.

The controllers for instruments shall be located in IP56 weatherproof enclosures adjacent to the instrument sensors.

All instruments, which require a power supply (with exception of safety low voltage) and do not form part of an MCC, shall be provided with an insulating housing, or other measures for prevention of electric shock shall be taken.

The signals from all instrumentation shall be relayed to the local MCC for display. If communication protocol is used for signal transmission, it shall be compatible with protocol used in the rest of control loop.

Instrumentation for package plant shall be provided fully in accordance with the equipment supplier’s recommendations and fit for its intended use.

The Instrumentation equipment and systems shall comply with Section 4 of these Employer’s requirements.

  - Control Philosophy

### General

The general specification and control philosophy is intended as a guide only and outlines the general control philosophies of each proposed treatment area. The detailed design of the operating philosophy in order to achieve the control required to operate the plant safely, efficiently and effectively shall be the responsibility of the Contractor but shall be subject to the approval of the Engineer.

It shall be incumbent upon the Contractor to ensure that the design takes into consideration aspects such as communications, contingency, and back-up systems. This applies to all aspects of the schedule including, but not limited to, power systems, control systems and instrumentation.

All plant areas shall be automatically controlled (unless otherwise stated) with facilities for manual control.

The Contractor shall provide all instrumentation necessary for the safe, reliable and efficient operation requirements.

Essentially, all instrumentation analogue signals, under all operating conditions, shall be measured, located in PLC registers, displayed on the MMI and independently (i.e. not through the PLC), displayed on the MCC by means of an analogue display. All presets shall be adjustable to allow optimum configuration of the automatic control. Critical presets, such as levels, flow interlocks etc. shall only be accessible via password or similar security interlock.

It shall be the Contractors responsibility to provide a fully functional and reliable method of control including all control and standby sensors, monitoring devices and systems necessary to operate the plant and achieve the process requirements.

The Contractor shall submit a detailed, written control philosophy of the plant for approval by the Engineer, prior to submission of detailed design drawings.

The control system shall be designed to fail-safe in order to prevent flooding, spillage and prevent hazardous occurrences. On rectification of plant failure due to power loss, the system shall resume automatic operation without manual intervention, in a systematic manner.

In addition to the primary control device the Contractor shall provide backup control on critical plant, as defined within his Risk Assessment.

### Automatic Operation

Automatic control shall be carried out by means of a PLC dedicated to control of MCC. The MCC section or separate automation cubicle shall have a window to allow viewing of the PLC hardware and I/O cards.

The Contractor shall provide a UPS for the PLC and any safety critical instrumentation to maintain operation of the instrumentation for at least 60 minutes. Line interactive topology, assuming automatic voltage regulation, is required for UPS as minimum.

### Manual Operation

All plant shall be individually operable in manual mode. Manual control shall only be available when manual mode is selected and be via the push button controls on the MCC starter door.

In manual mode all protection systems shall remain operable, automatic control inhibits shall be inoperable unless specified and automatic duty changeover shall be inhibited.

### Duty and Standby Control

Where standby drives are provided, the general mode of operation unless otherwise specified, shall be that on failure of the duty drive the standby shall operate as the new duty drive. Manual facilities for alternating the duty drive shall be provided. The standby drive shall be complete, fully installed available for immediate changeover to the duty drive.

  - SCADA System

### System Overview

The Contractor shall supply, install, interface to instrumentation and programme all necessary PLC and communications equipment, including Lightning Protection Units (LPU) as detailed in the Volume 3 – 1 Section 4 , to monitor and control the treatment areas and pumping stations according to the detailed control philosophies.

The local control programmes shall select the appropriate standby equipment on detection of duty equipment failure.

The system implemented should be able to operate within the control strategy described within the Volume 3-1, Section 4  for SCADA but shall be flexible enough to be easily changed should the control philosophy change.

The proposed system shall provide a centralised Dispatcher processing function, complete with standby facilities and local workstations.

The Dispatcher equipment and operator workstations shall be accommodated within the Administration Building.

### Signals

The following signals shall be provided for display on the SCADA system. The Contractor shall note that the signals detailed below are provided for guidance only and as such does not imply to cover all signals required:

Supply and control:

- Power supply failure (incoming supplies)

- MV circuit breaker open/closed.

- LV circuit breaker open/closed

- Power consumption.

- Power supply failure (all MCCs).

- Intruder Alarm (if fitted).

- Fire alarm.

- PLC status.

- UPS loss of power.

- Typically for drives:

- VFD fault

- Motor running.

- Motor protection activated.

- etc.

Typically for instrumentation:

- Analogue signal (level, flow, pressure, dissolved oxygen etc.)

- Instrument failed.

- High, low, high high, low low etc. alarm/control signals.

- etc.

The Contractor shall submit, as part of the detailed design information, a detailed SCADA signal list for the approval of the Engineer.

### SCADA System Requirements

The SCADA system shall be implemented as an operational management tool i.e. shall be provided with facilities to undertake the day to day monitoring and control of the waste water treatment plant and associated sewage pumping stations and the production of general management information.

### Scope of Work

The scope of work includes the following:

- Production of a Functional Design Specification, to be approved by the Engineer.

- Supply, installation and commissioning of a master and standby dispatcher equipment sized to monitor and control each treatment process with a total of 4000 database points, complete with:

- Operating system

- Hardware

- All necessary data storage devices

- Printing Devices

- Furniture

- Communications equipment and cabling for communicating with the PLC equipment located within the wastewater treatment plant and administration building.

- Supply, installation and commissioning of 2 (no) operator workstations

- Supply installation and commissioning of the SCADA system software.

- Supply installation and commissioning of the communications network, including Lightning Protection Units, via a cable communications network for the on-site PLCs.

- Supply, installation into Motor Control Centres or separate automation cubicles, interface to instrumentation signals and commissioning of PLC equipment.

- Supply, installation and commissioning of all necessary PLC programming equipment, software and licences.

- Supply, installation, and commissioning of instrumentation equipment.

- Configuration of the SCADA system database, including:

- all PLCs

- all mimic displays

- all trend displays

- all reports

- Programming of all PLC equipment to perform local control.

- Performance Factory Acceptance Tests (FAT) witnessed by the Engineer or his representative.

- Performance Site Acceptance Tests (SAT) witnessed by the Engineer or his representative.

- SCADA system commissioning.

- Training of the following personnel to a standard recommended by the supplier as appropriate:

- Operators

- System developers/maintenance

- System Manager

- Documentation – English and Montenegrin language.

  - Plant Maintenance Software

In addition to General Technical Requirements stated in Volume 3-1, Section 4 the Contractor shall supply and implement a proprietary Plant maintenance software system. The high-level functional requirements of this system are as follows:

- Asset database

- Planned maintenance scheduling and recording / work order processing (unplanned / emergency repairs) including recording information on:

- location of work / plant reference

- details (description) of work

- materials needed

- personnel involved

- programmed date for work

- Reporting completion of the work and any changes from the planned work;

- Updating of asset register to show any changes that have taken place to the asset stock.

- Facility for analysis of data to determine any patterns which might indicate potential for cost savings or improved efficiency, as well as identifying best practices, components and materials.

- The contractor shall supply necessary documentation and training of the personnel to a standard recommended by the supplier as appropriate, including:

- Plant management

- Administrative users of the system located on the site and in the headquarters of the local PUC (assumed 10 in total).

- System developers/maintenance

- System Manager

  - Telecommunication

### Telecommunication Connection

Contractor shall Design and construct new telecommunication line connecting public Telecommunication network with WWTP telecommunication infrastructure in accordance with terms and conditions presented in the Local Location Study  for ”Donji Talum” for Construction of WWTP in Berane. Location Study foreseen usage of existing underground telecommunication cable line situated along regional road Berane-Bijelo Polje. Local Study plan described construction of new access road crossing with existing regional road. During new road construction, a new section of telecommunication infrastructure shall be performed. New telecommunication infrastructure consider following objects:

- Two telecommunication manholes (T1 and T2)

- Telecommunication piping consisting of two PVC pipes 110 mm and two 40 mm diametar

- Access piping from manhole T1 to WWTP facilities

The Drawing „Plan of Telecommunication infrastructure“ in Volume 5 present principal of telecommunication connection. Type of TK cable shall be determined by PUC conditions and recommendations.

### WWTP Telecommunication infrastructure

Within WWTP construction plot, Contractor shall construct Telecommunication infrastructure in accordance with Section 4 of these Employer’s requirements.

# CIVIL ENGINEERING DESIGN REQUIREMENTS

  - General

The civil engineering works comprise the following:

- Preparatory Works including flood protection:

  - Site clearance,

  - Regulation of River Makva,

  - Removal of top soil,

  - Backfilling until 662.50 masl,

  - Construction of embankment on the left bank of the River Lim along the WWTP site, until 661.85 masl

- Earthworks and foundations;

- Construction of water-retaining and other structures/buildings associated with the wastewater and sludge treatment processes;

- Connection of pipes to the plant;

- Process pipelines and cable ducts;

- Site drainage system;

- By-pass pipeline construction

- Flood protection measures

- All other miscellaneous works required for the construction of the Works

All civil engineering structures are to be designed and constructed for at least the minimum design life with a minimum amount of maintenance. The design and materials of construction shall take account of the climatic conditions and different operational environments.

  - Flood protection

### General description

The WWTP site is potentially endangered by flooding of both nearby water courses including the Lim River and the Makva River/Creek which intersects the site.

It is therefore necessary to elevate the WWTP plateau at the elevation that provides required level of flood protection as well as to carry out other works and banks stabilization works on the abovementioned water courses within the zone of WWTP site.

The WWTP shall be protected from the floods of 100-year recurrence interval, which is, in accordance with the Detailed Design of the Lim River regulation (2011) for this section 835 m3/s.

The Lim River section next to the WWTP – so-called section D shall be of longitudinal grade of 3‰ (0.003), which is equivalent to the regulated grade adopted for the upstream section (defined in the Detailed design, 2011).

Regulated cross-section of the river is to be of trapezoidal form of 60m width and with slope of 20‰. For the embankments the slope of 1:2 is designed. The embankments are to be constructed along both river banks to the elevations defined in the Preliminary Design, providing required level of flood protection.

At the WWTP profile designed elevation of the embankment is 661.85masl, whereas the plateau of the WWTP itself is to be elevated to the elevation of 662.50 masl.

Further details regarding the river regulation and flood protection works are presented in Volume 5 of this tender.

At the moment the Makva River intersects the WWTP site and should be therefore relocated and regulated in order to ensure flood protection of the WWTP from this water course. The regulated water course is to be constructed just upstream of the WWTP plot with cross-sectional width of 8m, longitudinal slope of 5‰, while the slope of embankments is 1:2. Similarly to the Lim River regulation, the elevation of the embankments is to be at 661.85 masl.

In addition to the abovementioned flood protection works it is also necessary to protect the WWTP from waters that can be generated on the hilly terrains to the west of the WWTP. For that purpose, the canal encircling the WWTP site and discharging into the Lim River is to be constructed. Longitudinal slope of the canal is to be 6‰, the width of the cross section is 4m, while the designed side slope is 1:2. Similarly to the flood protection works described before, the design elevation of the embankment is set at 661.85 masl.

### Geotechnical requirements for WWTP Plateau Construction

General characteristics of the site

The proposed location is situated on the bank of the Lim River near the confluence with Makva creek. The site has served as a borrow pit for construction material. Therefore it is expected that the terrain of the location is heterogenic, morphologically and geologically.

These characteristics indicate the need to prepare consistent conditions for alignment and foundation of the WWTP units, buildings and equipment.

Geotechnical investigation works

The Contractor shall check the terrain composition, especially in low areas, in addition to the previously conducted investigations. The ground conditions along the river can change drastically after floods.

The main objective is to determine potential existence of unsuitable, compressible materials. In this case, the low quality materials should be replaced with the good quality materials.

Preparation of the plateau base

In order to make consistent conditions, i.e. quality of the base, the following phases of works need to be done:

- Phase 1 - removal and transport of organic and low quality materials in a layer of no less than 0.3m. It is expected that the layer of low quality materials is thicker in the lower areas, so the additional checking should be done in these areas.

- Phase 2 - levelling and filling of the low areas using the material that is taken from higher areas. This means that the lower areas will not be filled using only the material from borrow pits.

- Phase 3 - levelling of the whole plateau base to a uniform ground level

- Phase 4 - compaction of the base using vibro-rollers

- Phase 5 - installation and compaction of the plateau material in layers

- Phase 6 - thickness of the finishing layer of the plateau has to be at least 0.5m and should be made using stone material, in case the plateau is built using soil material.

Construction of the plateau has to be of highest quality and major settlement of the structures must not occur. Maximal allowed settlement is 2 cm. In addition, bank slopes should be resistant to erosion caused by the river Lim and Makva creek.

The structures should have a safety factor of min F=1.3 against uplift during high water levels. The evidence of the resistance to hydraulic lift and erosion should be provided. The bank slopes should be analysed for stability under the conditions of rapid drop of river water level.

Terms of construction of the WWTP plateau

Materials for the construction of the plateau, borrow pit: in order to construct the proposed plateau it is necessary to bring approximately 100,000 m3 of material.

Plateau may be constructed using gravel material, crushed stone from quarry or soil based materials.

The following conditions apply to these types of materials:

Gravel

Gravel is suitable material for construction of the plateau. The basic requirement is that clay and sludge content does not exceed 30%.

The Contractor shall determine a proper borrow pit and to prove that it contains sufficient quantity of material, as well as that the grain size fractions of the material are suitable.

The Contractor must obtain necessary approvals for usage of gravel material and to prepare a statement on the method that will be used to arrange the borrow pit after the excavation, and in line with the requirements set by the relevant local authorities.

Crashed stone quarry materials

These materials need to fulfil the following requirements:

- Maximum diameter should be less than 0.5 m.

- Clay content should be less than 5%.

Soil material

The contractor should prove that the level of moisture of the material is approximately equal to the optimal moisture for the chosen borrow pit. This means that minimum 5 Proctor tests should be done for each borrow pit.

For the purpose of determining methodology for installation of soil into plateau the following should be confirmed:

- the height of the layer that needs to be compacted

- number of the roller crossovers

In order to determine these two key elements, pilot sections must be constructed. These pilot sections may become an integral part of the plateau.

The height of the layer can be determined on the basis of comparative experience, and in case of soil based materials suggested height of 0.25m might be adopted so this element does not need to be determined separately.

Number of crossovers (1 crossover tour-retour)

Cylindrical samples should be collected on pilot sections after each crossover and bulk density and moisture of samples should be determined.

The results should be recorded in the diagram number of crossovers-bulk density. The final number of crossovers should be adopted on the basis of this diagram.

Tests should be conducted after 5, 10 and 15 crossovers on the pilot sections. When it comes to the soil based materials, the expected number of crossovers is between 4 and 8. However, construction methodology is contractor’s responsibility.

Geotechnical conditions for river bank revetment

It is envisaged that the bank slopes will be secured using stone blocks. The quality of these works needs to be demonstrated and stability of the slopes in relation to the river bank materials, proven. This analysis should confirm whether the bank structures are sufficiently anchored in the Lim riverbed and creek Makva and whether the inclinations of the slopes are appropriate.

In addition to this, the Contractor has to demonstrate that the slopes supported by stone blocks are resistant to erosion. If the blocks are laid onto fine-grained sand material or soil material, the slopes should be secured against interior erosion, i.e. washing the small particles out from the plateau. This problem could be easily solved by covering the slopes with geo-textile or with drainage layers.

Stone blocks used for bank fortification must be attested for frost resistance.

Quality control of the plateau construction works

Stone materials

Quality control should be done using the tests with 30cm diameter test slab. The tests should result in compressibility module of minimum 50.0 MPa, which should not be a problem when it comes to plateaus built using stone materials.

Soil material

The quality control of the materials that were incorporated into the plateau consists of the following basic geotechnical tests:

Bulk density is determined using cylindrical samples taken from the individual layers after compaction. On average, one sample should be taken for every 1000 m2 from each layer.

Measuring of moisture of incorporated material should be done on the same samples that were used for bulk density measurements. On average, one sample should be taken for every 1000 m2 from each layer.

NOTE: control investigations should prove that the following two basic requirements are met:

Bulk density should be approximately equal to the results of the Proctor tests and at least of 90% of the bulk density from these Proctor tests.

Moisture of layer should be approximately equal to the optimal one from the Proctor tests and allowed tolerance is max. 2%

Preparatory works

The contractor must prepare work methodology which includes time schedule, access roads, site laboratory, construction equipment, preliminary tests of materials to be incorporated, potential borrow materials and setting out plan for the buildings and the plateau.

Geotechnical investigation works

When it comes to the preparation of the site, the contractor needs to resolve the following:

- Find the appropriate borrow pit for materials

- Demonstrate the quantities of materials needed for construction of the plateau

- Obtain relevant environmental approval for borrow pit

- Test the material from the borrow pit and assess its suitability

- Carry out additional investigation excavations in lower areas

- If soil material will be used for plateaus, the contractor shall prepare a methodology on how to ensure optimal moisture. When it comes to this sort of material, the tolerance is max. 2% from the optimal level of moisture.

- The Contractor should fulfil all geotechnical requirements that are given in this report

- The Contractor needs to ensure continuous presence of geotechnical supervisor, as a part of contractor’s on-site team.

  - WWTP

The Contractor shall design and construct all buildings necessary for the correct operation of the Plant. The minimum required facilities are as follows, but not limited to:

Wastewater and Sludge Treatment Facilities

- Inlet chamber with emergency overflow towards the by-pass pipeline

- Coarse screens structure

- Inlet pumping station

- Fine Screens building

- Grit removal facility, with classifier/ washer for clearing grit

- Equalization tank

- SBR feeding pumping station

- SBR

- Effluent flow measurement

- Drainage system to facilitate tank emptying and general site drainage needs

- Associated pipe work and ancillary equipment connecting the various process units.

- Odour control facilities for wastewater and sludge line. (All preliminary treatment facilities as well as septic reception station and sludge thickening and dewatering facilities are enclosed, enabling suction of odorous gas to odour treatment facility).

- Sludge buffer tank

Buildings*

- Screen building

- Blower house for biological treatment stage

- Sludge treatment building

- Transformer Station

- Administration & Control building

- Laboratory

- Workshop and stores building

- Parking place and vehicle washing area

- Guard house

* Some of these buildings may be designed to be combined into single units

### Administration and Control Building

The Contractor shall provide an Administration and Control Building to house the management, operational, technical and administration staff.

The minimum requirements for the Administration Building are shown in the tables below. Floor areas shown are indicative and the facilities shall be sized to accommodate the number of management, operational, technical and administration staff required to operate the plant.

Table 7-1: Requirements for the Administration and Control Building

| Facility | Area min. (m²) | Floor finish | Wall finish | Telephone / data exchange sockets |
| --- | --- | --- | --- | --- |
| Central Control Room | 26 | Carpet tiles with under floor ducts for cables | satin latex paint | 2 (see note 1) |
| Laboratory | 32 | Acid resistant floor tiles | tiled from floor to ceiling | 2 |
| Offices | 15 x 2No. | Wood-parquet | satin latex paint | 3 |
| Kitchen | 18 | Floor tiles | gloss paint | 1 |
| Toilets (M & F) |  | Floor tiles | tiled from floor to ceiling |  |
| Shower and washing room (M & F; 8 no.) |  | Floor tiles | tiled from floor to ceiling |  |
| Lockers (18 no.) and changing rooms |  | Floor tiles | tiled from floor to ceiling |  |
| Corridors |  | Floor tiles | gloss paint |  |

Note: 1. In addition to those for SCADA system.

Table 7-2: Furniture and Fittings for the Administration and Control Building

| Room | Furniture / Fittings |
| --- | --- |
| Central Control Room | 3 No. Lockable steel cupboards for diskettes, paper, ribbons, documentation, spare parts 2 No. Desks incorporating side drawers, to carry a Supervisory Unit, a telephone set or a printer 1 No. Cupboard 25 m of fixed shelving 2 No. Swivel office chairs, adjustable height 2 No. Visitor’s chairs. |
| Laboratory | Tiled (acid resistant) workbench with sink 2 No. Lockable steel cupboards 2 No. Desks each incorporating side drawers 2 No. Swivel office chairs, adjustable height 1 No. PC’s reasonable price, latest generation, for office purpose, incl. basic software (Win, MS Office, antivirus, ACAD preview, etc.), internet available 1 Laser A3 printer |
| Offices | 3 No. Desk with drawer units at each side, hardwood top 3 No. Leather armchair, five castors, adjustable height 3 No. Telephone table 3 No. Filing Cabinets 2 No. Cupboard 4 No. Visitor’s chairs. |
| Office equipment | 3 No. PC’s reasonable price, latest generation, for office purpose, incl. basic software (Win, MS Office, antivirus, ACAD preview, etc.), internet available 1 No. Combined Copy/Print/Scanner device A3 colour 8 No. Of Telephone units 1 No. Of Telephone exchange (8 lines) 1 No. Telefax |
| Kitchen | 1 No. Tall standing Refrigerator 1 No. Cooker (ceramic hob and oven) 1 No. Double sink with drainer Fitted worktop / cupboard units Crockery and cutlery for minimum of 12 persons Table / chairs for 6 persons |

The Contractor shall design and install a laboratory suitable for analyses of wastewater and sludge.

The Contractor shall supply a complete set of general laboratory equipment and facilities for normal operation including, but not limited to, glassware, scales, refrigerator, drying oven, ignition oven, fume cupboard, demineralised water unit, furniture, desktop computer and printer for data management, and safety equipment.

Table 7-3: List of Laboratory Equipment to be provided

| Item | Volume |
| --- | --- |
| General Laboratory Basic Equipment |  |
| Beakers (glass) | 250, 500, 1000 ml |
| Funnels (glass), D = 10 cm, stem = 10 cm. |  |
| Reagent bottles (Amber glass) | 500, 1000 ml |
| Plastic bottles for washing | 500 ml |
| Measuring pipettes glass | 1,5, 10, 25 and 50 ml |
| Suction flask pipettes | 2, 5, 10, 25 ml |
| Full pipettes glass | 1, 5, 10, 25, 50, 100 ml |
| Pipettes bulb (ball) |  |
| Test glasses (Tubes) 16 x 160 mm - pkg. 100 piece |  |
| Test glasses stand for 12 tubes |  |
| Feeder machine, complete | 0 - 30 ml |
| Feeder machine, complete | 0 - 50 ml |
| Bottles NS narrow neck - clear glass | 50 ml |
| Bottles NS narrow neck - clear glass | 100 ml |
| Bottles NS narrow neck - clear glass | 250 ml |
| Spatula 18 / 8 , 210 mm long |  |
| Double Spatula 18 / 8 , 210 mm long |  |
| Tweezers 18 / 8 , blunt , 115 mm long |  |
| Hot plate - 180 mm diameter |  |
| Drip stand - metal (wire) |  |
| Glass dishes, low form | 100, 1000 ml |
| Erlenmeyer flask, narrow neck | 300, 500 ml |
| Erlenmeyer flask, large neck | 300, 500 ml |
| Set of Brushes for laboratory glassware and vessels |  |
| Balloon with plastic tap | 10 l |
| Narrow neck bottles PE | 250, 1000 ml |
| Large neck bottles PE | 250, 1000 ml |
| Measuring (graduated) cylinder, high form | 10, 50 ml |
| Distillation apparatus 4 l with reserve vessels |  |
| Water Bath (0-100°C) |  |
| Suction Pump |  |
| Buchner Funnel | 300 ml |
| Manual Sampling |  |
| Sampling stick 3.5 m long |  |
| Sampling ladle, one piece | 1000 ml |
| Basket, metal wire |  |
| Transport vessels, plastic | 2000 ml |
| Measuring dish | 1000 ml |
| Sedimentation vessels | 1000 ml |
| Intake stand, PVC |  |
| Stop watch 120 min. |  |
| Oil test paper 320 |  |
| Indicators set |  |
| Test sticks |  |
| Temperature Measurement (set of thermometers for measurement of temperature of ambient air and wastewater) |  |
| pH Measurement |  |
| Portable (Pocket) pH -meter, (pH 96A / Set) |  |
| BOD5 – Measuring Instruments |  |
| BOD5-Instruments and equipment for Dilution Method. |  |
| BOD5 - Measuring instrument manometric, 6 places |  |
| BOD5 - Thermostat cupboard 370 l (air incubator) |  |
| Allyl urea (ATH) |  |
| Feeder – machine for ATH |  |
| Oxygen Measuring Instruments (DO-Measurement) |  |
| Oxygen/Temperature Measuring Instrument (e.g. OXI* 92/Set) |  |
| Microprocessor-O2-Measuring Instrument (e.g. OXI* 196) |  |
| Oxygen – Electrode (e.g. EO 196-1.5) |  |
| Electrical Conductivity (EC) Measuring Instruments |  |
| Pocket Portable EC - Measuring Instrument (e.g. LF 92/SET) |  |
| Sludge Sampling |  |
| Sludge Siphon up to 12 m depth |  |
| Dry Solids Content |  |
| Hygrometer, for solid and moisture content ORI* - mat |  |
| Sludge – Volatile Solids |  |
| ORI* - high speed - incinerator |  |
| Crucible | 75 ml |
| Microscope |  |
| Primus monocular, Stage 10 x, 40, 100 objectives |  |
| Total Nitrogen |  |
| Nitrogen - Sample preparation with Microwave |  |
| Instruments |  |
| Dissolved Oxygen (DO) Meter |  |
| - Portable (battery), digital temperature measurements required - Oxygen measurement range 0-19, 99 mg/l - Accuracy ± 5% of measured value at constant temp. - Quick calibration, free of zero current. - Automatic temperature compensation. - Automatic atmospheric pressure correction by integrated pressure sensor - Temp, measurement range - 5 to + 45° C, accuracy ± 0.2°C |  |
| Analytical balance |  |
| - Digital, 220 V, suspended pan. - Range 0-200g, readability 0.1 mg. - Precision 0.05 mg. - Built in weights. - Pan Dia x Box H 9 x 18 cm. |  |
| Drying Oven |  |
| - 200V, 1200 Watts, max. temp. 250°C. - Mechanical conversion. - Sensitivity +0.25 °C - chamber dimension W = 33 cm, L=36 cm, H=33 cm |  |
| Electric hot plate |  |
| - 220 V, 600 Watts. - Surface area 225 cm² - Max. temp. 510 °C - On/Off switch. |  |
| COD reactor HACH* or equivalent |  |
| - 220 V, micro samples, for 16 samples. |  |
| Reagent Vials for COD Tests to fit a.m. reactor |  |
| - Disposable (box with 25 vials) |  |
| Forceps for crucibles (Length 50 cm) |  |
| BOD Bottles with caps, with sealing water tip. | 300 ml |
| Dessicator with porcelain plates |  |
| Burettes + Container (500 ml) |  |
| Volume 25 ml, Subdivision 0.1 | 25 ml |
| Filter paper Watman 40/42, (100 filter/packet), Packets |  |
| Filter paper Watman, diameter 15 cm, (100 filter/packet), Packets |  |

The laboratory should be located within the administration building. The following list of analyses to be carried out is indicative and a list of equipment, chemicals, liquids and materials shall be submitted by the Contractor, to the Engineer for approval, prior to procurement, before Taking-Over. Testing methods shall be in accordance with international best practice, making use of the appropriate instruments where applicable.

### Workshop and Stores Building

The Contractor shall provide a Workshop and Store area. The building shall be of sufficient size to carry out all maintenance and repairs required to efficiently operate the Plant, and include a store room.

The minimum requirements for the Workshop and Stores Building are shown in the tables below. Floor areas shown are indicative and the facilities shall be sized according to the plant maintenance and spare parts storage requirements, taking into account the equipment and fittings required as listed below.

Table 7-4: Requirements for the Workshop and Stores Building

| Facility | Minimum Area (m²) | Telephone and sockets | Data exchange sockets |
| --- | --- | --- | --- |
| Workshop – Mechanical Electrical Storeroom | 80 | 1 | 1 |

The workshop and storage area shall have vehicle entry for the delivery of parts and machinery and be equipped with a motorised overhead travelling crane of sufficient capacity to handle the heaviest single item of operational plant when broken down for maintenance work.

The workshop shall be sub-divided into Mechanical, Electrical and Storeroom. The storeroom shall be fitted with necessary storage system to allow for an organised system of storage and inventory.

The workshop shall include washroom and rest facilities for the staff.

Floors to the workshops and the storeroom shall have a power floated, surface hardened concrete floor finish. This shall be painted then with a non slip industrial grade floor paint (grey)

The Contractor shall provide all equipment, tools and consumables required to efficiently operate and maintain the Plant and Spare parts as described in Section 1 of these Employer’s Requirements.

Any process chemical storage facilities shall be provided separately to the Workshop Building.

Table 7-5: Indicative Equipment and Fittings for the Workshop and Stores Building

| Location | Equipment / Fittings |
| --- | --- |
| Mechanical Workshop | - Workbenches with vices and lockable drawers - Motorised overhead travelling crane - Disc Saw - Bench Grinder - Pillar and Magnetic Base Drills - Welding Plants - Gas Bottle Stands - Weld test equipment - Milling Machine - Hand Pallet Truck - Hand Drills and Grinders - Trolleys - Pipe Rack - Toolboxes filled with required tools for maintenance of the plant - Mobile Scaffold Tower - Electrical Testing Equipment - Benches - Toolboxes |
| Storage Room | Storage shelves |
|  | - 1 No. PC’s reasonable price, latest generation, for office purpose, incl. basic software (Win, MS Office, antivirus, ACAD preview, etc.), internet available - 1 Laser A3 printer |

### Waste Materials Storage

In accordance with standards and requirements in Montenegro, with particular consideration being given to the Health and Safety and Environmental regulations, the Contractor shall provide all necessary storage facilities for operational waste materials which shall include as a minimum the following:

- Waste oil/lubricants (including those arising from oil/grease removal equipment) – 1 months capacity

- Waste chemicals and contaminated materials (packaging/containers etc) – 1 months capacity

- Household waste - area required for containers provided by Municipal Solid Waste Collection Company.

The Contractor shall give due consideration in his design of the access requirements and facilities required for safe and easy collection.

### Wash water System

A wash water supply system shall be provided that is compatible with the process equipment being provided. Duty/standby or duty/assist/standby pumping shall be provided. Service water shall be taken from the potable water connection. The minimum wash water pressure shall be maintained under all operating conditions.

Sufficient hydrants shall be provided at the following operational areas such that maximum hose lengths are limited to 20 m:

- Screening and grit removal areas

- Each biological treatment basin

- Sludge treatment areas

Connections shall be provided to the screening and grit removal equipment to suit the equipment being provided.

The use of the Wash Water system must not interfere or jeopardize in any way the Fire Fighting System.

# ROADS DESIGN AND LANDSCAPING REQUIREMENTS

  - Main Access Road

The main access road to the WWTP site is to be by means of the connection to the main road Bijelo Polje – Berane, M2 which is near the site. The main characteristics of the planned access road are described in these Employer’s Requirements, Volume 3-1, Section 2, Chapter 1.

  - Internal Site Roads and Car Parking

The Contractor shall provide all-weather paved site internal roads to give easy access to all facilities and operational areas.

The entry to the WWTP site is arranged as a two-way road 6m wide. It must have minimal radius of bend suitable for heavy and fire-fighting vehicles. Internal roads and road surfaces must be designed in accordance with the Regulations on technical requirements for access roads, turntables and paved plateaus for fire-fighting vehicles for structures with increased fire risk.

Minimal cross sectional slope of the internal roads and plateaus shall be 2% in order to enable storm water drainage while the longitudinal slope of the internal roads should be minimum 0.3%.

Road surface for traffic and plateaus shall be asphalted with concrete curbs 18/24cm.

Road structure should be minimum 0.47 m thick and shall include the following base layers:

  - Surface course – asphalt concrete AB11s-BIT60, d = 0,04 m;

  - Base course – bituminized stone material BNS32B-BIT60, d = 0,08 m;

  - Sub-grade of granular material, d = 0,35 m.

The minimum width of the site roads shall be 3.5 m designed for 30 tonne trucks for heavy goods transportation and for medium design load. Main site roads with two way routes shall be 6 m wide and bends shall be widened to prevent running off the edge of the road way.

Hard-standings shall be provided at all key operational areas, to facilitate personnel and vehicle access for operational and maintenance purposes. All access roads and hard-standings shall be designed to prevent standing water and all necessary drainage shall be provided (gullies and piped system).

The roadway and free distances provided between and into the buildings shall allow for clear and safe approach and manoeuvring of all types and size of operational vehicle required for the operation and maintenance of the Works. Provisions for vehicle access shall be made at all locations where necessary to facilitate personnel and vehicle access for operational and maintenance purposes. Where appropriate, ramps at equipment access doors shall be provided to enable a vehicle to be driven into the building.

Turning areas shall permit a vehicle to manoeuvre into the final discharge or pick-up position. Surface markings shall be provided to identify areas allocated as turning areas and parking/unloading bays.

A minimum of 6 car parking spaces shall be provided.

Hard paved, lighted pedestrian walkways 1 metre wide shall be provided to all access points to tanks, chambers and building entrances unless these are beside road ways. The paved routes shall follow logical lines likely to be used by the maintenance workers.

  - Perimeter Fencing and Entrance Gates

The Site shall be maintained as a secure site. The Contractor shall provide suitable 2.4 m high metal security fencing to all working areas and compounds. Fencing shall be steel bars or mesh and shall have apertures or spaces that prevent debris or waste material being blown out of the site. The main access gate shall be capable of automatic opening and closing from the Administration Building. Warning signs in Montenegrin and English shall be fixed at suitable intervals along the fence lines and on gates to warn the public of the dangers of entering the wastewater treatment plant site. These requirements shall be regarded as the minimum standard for security purposes. This shall not relieve the Contractor of his responsibility for site security.

  - Flood Protection to WWTP Site

The WWTP area shall be graded in such a way as to avoid the occurrence of any flooding from surface water. If required, drainage shall be provided at any areas susceptible to flooding (an example is indicated in the Preliminary design). Discharge of surface water may only be to agreed discharge points.

  - Exterior Lighting

Outdoor lighting shall be provided around treatment structures and buildings and along roads on the Site. Lighting intensities and other technical details shall be in accordance with the Employer’s Requirements (Volume 3-1, Section 4). The use of low energy lighting is compulsory.

Key operational areas shall be provided with emergency lighting.

  - Landscaping and Green Belt Setting

The Contractor shall produce a Landscape plans as part of the Detailed Design. The Contractor shall plant trees and shrubs around the WWTP to break up the outline of the buildings; ensure the WWTP is less intrusive to the surrounding landscape and to act as a wind break against the spread of odours from the site.

The tree and shrub species should be those found in the local and be of a type that will minimise interference with the operation of the works.

Landscaped mounds (bunds) could be constructed around the perimeter of the Site using surplus soils available from the construction of the WWTP. These bunds should be planted with trees and shrubs.

Areas designated for landscape screen planting shall be planted in the first planting season at the beginning of the contract. During the contract any trees or shrubs that fail to grow or die shall be replaced.  Open areas within the site are to be grassed. No trees shall be felled or removed from the Site without the Engineer’s consent. Where it would be impractical to maintain the grass due to shape, slope etc, gravel beds shall be provided. Gravel shall comprise uniform, clean, rounded pebbles (diameter 6 - 32 mm).

  - Signs

Appropriate signs shall be erected at the entrance to the treatment works, around the treatment works site and inside buildings (directions, indicators, safety alerts, alarm plan etc).

In particular a large sign board announcing the title of the project, financing arrangements, employer-, PEA-, consultant-, contractor data etc. shall be erected at the entrance to the site.

Prior to manufacture all signs shall be submitted for approval to the Engineer. All signs shall be large enough to be easily seen and read by those for whom they are intended. Generally signs shall be in both Montenegrin and English unless otherwise agreed on site with the Engineer and/or Employer.

# COMMISSIONING AND TESTING

  - General

The Contractor shall perform all necessary tests to demonstrate compliance of the Works with the Specifications, the Plant performance requirements and the Process Performance Guarantees. All tests specified herein and/or found necessary for the Works shall be carried out under responsibility and at the cost of the Contractor.

The Contractor shall be responsible for establishing and maintaining procedures for quality control, which will ensure that all aspects of the Works comply with the requirements of the Contract. The Contractor shall prepare in accordance with the requirements set in this document and submit to the Engineer as per sub-section 3.7.3 of this document, a detailed, proposed Quality Control Plan. The Plan shall include the quality control of all aspects of the Contract implementation.

The Contractor’s Quality Control Plan shall be subject to approval of the Engineer. The approved Quality Control Plan shall be followed throughout the performance of the Contract, unless otherwise instructed by the Engineer. Any approval by or on behalf of the Engineer of the Contractor’s Plan shall not relieve the Contractor of his obligation to ensure that the Works comply with the requirements of the Contract.

The Contractor shall appoint a suitably qualified member of his staff to be responsible for all aspects of quality control (QC Executive) and to maintain close and effective liaison with the Engineer on site at all times.

Testing procedures and processes for the recording of test results shall be set out in the Contractor’s Quality Plan. Nevertheless, the Contractor shall submit in due time a programme of specific tests for the Engineer’s consent. When special test device/instrument needs to be supplied for testing, the Contractor shall provide the associated calibration sheets, which shall be submitted to the Engineer for review prior to tests being carried out.

Testing shall be witnessed by the Engineer. In case of disagreement between the Contractor and the Engineer on performed test results, an independent testing institution shall be called for providing expertise. The Contractor should allow access to sites at any time to any external institutes or experts carrying out independent testing. The costs of expertise testing shall be borne by the party proven to be wrong.

In any case dully certified reports on the successfully completed tests shall be submitted to and signed by the Engineer/Employer. The results and approval of any testing shall not prejudice the Engineer’s rights to reject the Work if it fails to comply with the Specification when installed, or to give complete satisfaction in operation.

Also a report presenting all tests performed during certain testing period shall be prepared and submitted to the Engineer. Furthermore all testing, sampling and records keeping shall be undertaken as required by Montenegrin legislation to enable the Employer obtaining from the authorities technical permission for putting the Plant into operation.

During the testing the Contractor shall demonstrate to the satisfaction of the Engineer that:

- The Works are capable of producing the required standard of final effluent and that the sludge products meet the specified performance requirements;

- The Works complies fully with the Specification.

The Contractor shall demonstrate that the Plant operates satisfactorily when operated in both manual and automatic control.

The testing shall include, but not be limited to:

- Inspection and testing at the manufacturers' premises.

- Quality Control and testing during construction.

- Tests on Completion.

- Tests after Completion (Performance Tests)

  - Inspection and Testing during Manufacturing

The mechanical and electrical equipment shall be tested either at Manufacturer’s premises (Factory Acceptance Test - FAT) or at site (Site Acceptance Test - SAT). The Contractor shall list all the mechanical and electrical equipment and propose for each component an inspection and testing procedure, arranged to represent the plant working conditions as closely as possible for approval by the Engineer.

The Contractor shall allow in the Schedule of prices for all travel and accommodation expenses for 1 representative of the Employer and 1 of the Engineer to attend all necessary factory inspections and factory acceptance tests performed out of Montenegro.

The Engineer shall be given four weeks notice in writing to attend FAT testing. The Engineer will give at least two weeks written notice of his intention to attend the tests. The Engineer may, at his discretion, forego the witnessing of any tests. In such instances, the Contractor shall have the required tests carried out, and shall supply test certificates to the Engineer. The Engineer’s approval is required before shipment to the site. Formal test certificates are required in triplicate in all cases.

All major items of plant, including but not limited to pumps, the equipment with electric motors greater than 50kW, standby generator, control panels, SCADA hardware and software, aeration equipment, decanter units, Odour control units and sludge thickening/dewatering plant, shall be subject to testing by the Contractor and inspection by the Engineer before shipment from manufacturers' premises.

The tests on the SCADA System hardware and software shall demonstrate all aspects of the functionality of the SCADA / PLC System. Test of Control Panel shall simulate the function of the panel, shall simulate fault and alarm situations as well as all other functions that will be experienced while in operation.

Copies of test certificates of all major items shall be included in the operating and maintenance instructions as detailed elsewhere.

  - Quality Control and Testing during Construction

### Responsibilities and Procedures

The Contractor shall be responsible for establishing and maintaining procedures for quality control during construction/installation works, which will ensure that all aspects of the Works comply with the requirements of the Contract.

All materials and equipment shall be visually inspected before installation to ensure that no damage has occurred during transportation or storage. Labelling, warranty certificates, statements of conformity, etc. shall also be checked.

At the beginning of the equipment installation, the Engineer will visually inspect all materials and equipment to check/ensure:

- Their compliance with the requirements of the Specification;

- That installation procedures are acceptable and in compliance with the Manufacturer’s requirements.

- Warranty certificate;

- Statement of conformity.

In addition to complying with any specific requirements for sampling and testing the Contractor shall be responsible for routine inspection, sampling and destructive and non-destructive testing of all materials and workmanship during construction. The Contractor shall have available at site and ready for operation necessary non-destructive test devices not limited to the following:

- Ultrasonic welded joint gauge

- Ultrasonic wall thickness gauge

- Coating layer thickness gauge

- All devices needed for plate load tests

### Quality Control Plan

The Quality Control Plan during construction shall contain without limitation the following parts and shall be supplemented with additional information as required by the Engineer:

- Organisation chart for quality control;

- List of the Contractor’s staff to be engaged in quality control and testing, together with details of their relevant experience;

- Location and layout of any site testing laboratory or any external laboratory employed;

- List of major testing equipment and a description and certificate of the testing capability relevant to the Works of any site testing laboratory or any external laboratory;

- List of materials intended for the Works which require inspection at the supplier’s premises and the proposed testing procedures for ensuring quality control;

- List of materials and operations to be inspected and/or tested by the Contractor at the various stages of the construction work on site, together with inspection procedures, specified tests and their frequencies;

- List of proposed ”hold points”, defined as points when specified inspection and/or testing shall be performed by the Contractor and relevant documentation submitted for the Engineer’s review prior to proceeding with the work: (for example concrete placement, back-filling, start-up of equipment, testing pipelines and so on).

### Material Samples and Testing

The Contractor shall provide all material samples at his cost, together with the necessary storage, packing and transportation. Samples shall be subject for testing and approval by the Engineer. Material samples shall be submitted not less than 28 calendar days prior to the time such materials are needed for incorporation into any work. Also, the Contractor shall give the Engineer adequate notice of intended testing at supplier’s premises or external laboratories to enable the Engineer to arrange for such inspections. Material represented by such samples shall not be manufactured, delivered to the site nor incorporated into any work without prior approval of the Engineer.

The Contractor shall not be entitled to any compensation or claim for delays, inconveniences, damage, standing time or any other cause whatsoever, arising from the late submission of material samples.

Where samples, including samples of materials and/or works constructed on the Site, are taken as a reference for the quality of materials and workmanship provided as part of the Permanent Works they shall, after approval by the Engineer, be carefully preserved for this purpose by the Contractor until permission is given by the Engineer for their disposal.

Manufactured items and materials delivered to the site shall be inspected by the Contractor on arrival. Any defects shall be notified to the Engineer. Minor defects to surface finishes and the like in manufactured items shall be made good in an approved manner to the satisfaction of the Engineer. Items with more serious defects shall be returned to the suppliers for correction or replacement, as appropriate.

### Site Records and Test Certificates

Quality Control records, test certificates, reports and daily records of on-site testing and inspection shall be kept in forms approved by the Engineer. All test certificates and inspection records shall be accurately marked referring to the relevant part of the Works and shall include information required by the Employer’s Requirements and relevant referenced Standard.

The timing for submission of test certificates shall be as follows:

  - Manufacturer’s and/or supplier’s test certificates shall be submitted as soon as the tests have been completed, in any case not less than two weeks prior to the time such materials are needed for incorporation into the Permanent Works.

  - Certificates of tests carried out during the construction or on completion of parts of the Permanent Works shall be submitted within 7 days of the test completion.

### Reports on Tests & Inspections

Weekly, or at such intervals as the Engineer instructs, the Contractor shall submit in an approved form a report in triplicate including information on all quality control inspections and tests performed at the site and/or elsewhere during that period. The Report shall comprise all the works performed and relevant tests performed by the Contractor and shall include inspection and dully certified test reports with applicable sample numbers.

All test data shall be summarised in tabular and/or graphical form in a manner, which best illustrates the trends, specific results and compliance with the requirements. Where tests results do not meet specified requirements, full explanations shall be provided together with actions proposed to be taken (e.g. correction of the work, retesting, etc.).

Each report shall also contain envisaged quality control of works likely to be carried out during the succeeding period. The works “Hold points” shall be identified.

The Contractor shall keep, in an approved form, detailed up-to-date inventory of goods and materials that are subject to quality control (ordered, delivered, found faulty, lost during the work or found to be surplus to the contract requirements). The Engineer shall have access to these records at all times. Summary inventory records shall be submitted to the Engineer once a month.

  - Tests on Completion

### General

The Contractor shall prepare a comprehensive testing program and details of the inspection and testing procedures he proposes to employ in performing the Tests on Completion (ref. Clause 9 of the Contract Conditions) including for the start-up of the Plant. The Program shall be submitted to the Engineer for approval at least 60 days prior to the commencement of the Tests on Completion. Subject to the approval of the Employer the Works may be subdivided into sections (water/sludge line) which may be tested separately.

The pre-commissioning tests will be carried out when all civil, mechanical, and electrical and control components and functions are finished, tested dry, found in compliance with the contract conditions.

The Contractor shall carry out pre-commissioning tests including functional (“dry”) tests of all installed equipment, in order to demonstrate that each item of the Plant is ready for operation. The Contractor shall give the Engineer 21 days' notice of his intention for carrying out functional tests and submit a program for testing the function of each part of the Works. Within 7 days of completion of any functional test, the Contractor shall submit to the Engineer, a test reports giving detailed records of all inspections and tests carried out on the equipment or for any part of the Works. When the functional tests and inspections have been successfully completed the Engineer shall confirm their acceptance.

Upon all mechanical and electrical equipment having been inspected and tested “dry” on site to the satisfaction of the Engineer, a particular item of Plant and/or the Plant’ sub-systems (functional units) can be tested “wet”. The particular equipment or the main functional units (complete working unit e.g. inlet works, lifting pumping station, aeration tanks with blowers, etc.) shall be put (to extent possible) in operation required for “wet” operational testing after having approval of the Engineer. The equipment operational tests shall be executed aiming to demonstrate that functional units and the Works can be operated safely and as specified under all available operating conditions, as agreed with the Engineer. All ‘wet’ tests shall be carried out using potable water.

When all civil, mechanical, electrical and control components and functions are completed, tested “dry” and “wet” (to extent possible), found in compliance with the contract conditions and accepted by the Engineer for commencement of the Start-up and the trial operation, the WWTP should be fed with influent wastewater. The biomass in the system should gradually reach the design level(s).

The start-up of the Plant shall be made in two steps: commence with operation of wastewater treatment, and upon established stable operating conditions (developed biological process an adjusted process parameters) and produced sludge extends on sludge treatment facilities.

The Plant performance testing during trial operation period is foreseen. All equipment not fully tested during previous phases shall be tested now. During this period the Contractor shall also optimize the wastewater treatment process. The period of testing shall terminate after the Plant has been satisfactorily and successfully run by the Contractor (as certified by the Engineer) for 28 consecutive calendar days (in conjunction with the 14 days period foreseen for the Plant final performance testing).

At this point in time, upon the approval of the Engineer the plant can be formally handed over to the Employer.

The Plant final performance testing shall be carried out for a period of 14 days which shall commence after the specified effluent quality has been achieved. The tests shall be carried out both with the actual influent loading and with the Works configured to simulate as far as possible the hydraulic and BOD loads that will occur at the end of design horizon. During 14 days of the final testing samples shall be taken daily (a total of 14 composite samples) according to Montenegrin “By-law on the wastewater quality and the sanitary-technical conditions for the discharge into a recipient and public sewerage system (Official gazette No. 45/08, 09/10, 26/12 and 52/12) and according to the EU Urban Wastewater Directive 91/271/EEC.

The Tests on Completion shall be deemed to have been satisfactorily completed if the following have been achieved:

      - The final effluent quality, final product standards for screenings/grit and sludge, and emission standards for odour and noise meet the specified performance requirements with “zero failure”.

      - The quantities of the consumables are compliant to quantities stated in the Contractor's Tender.

      - The system of control is suitable for automatic operation of the WWTP and that the operational parameters can be maintained within the specified range.

If the Tests on Completion fail due to non-compliance with the aforementioned criteria, or do not attain the specified minimum process requirements or the Engineer is not satisfied that the operational parameters can be maintained, the Contractor shall:

- identify the reason for the failure,

- submit written proposals for rectification to the Engineer,

- obtain written approval from the Engineer for these proposals

- rectify the problem and re-test.

- All testing, sampling and records keeping shall be undertaken as required by Montenegrin legislation to enable the Employer obtaining from the authorities official permit. The Contractor will provide all needed documentation and assistance to the Employer in this regard.

- The “Use Permit” for the WWTP operation will be issued upon obtaining the positive Technical Inspection Report on the completed Works by the authorities. The Technical Inspection will be undertaken within the period of the Plant testing. The Plant passing the Test on Completion is pre-condition for issuing the positive Technical Inspection Report.

- Upon passing the Tests on Completion, the Contractor may apply by the notice to the Engineer for the Taking-Over Certificate.

Copies of test certificates of all major items obtained during the Tests on Completion shall be included in the operating and maintenance instructions as detailed elsewhere.

### Instruments, Materials and Consumables for Testing

1.	The Contractor shall provide and install ready for use any apparatus, machinery, instruments, tools, materials, consumables, water, etc. necessary for execution of the tests at his own costs.

2.	For tests with water it is required to use freshwater such as potable water, ground water or surface water.

3.	Any equipment used in the testing of the plant shall comply with the appropriate safety regulations and requirements in all respects. The Contractor shall ensure that all subcontractors are acquainted with the contents of the Employer’s Requirements.

4.	The Contractor shall ensure the accuracy of all instruments used for tests and, if required, shall produce recent calibration test certificates, or otherwise have the instruments calibrated at his own expense by an independent authority.

5.	 Meters for Electrical power consumption (kWh) shall be checked for correct rotation and creep tests shall be carried out to ensure that the meter is inoperative with voltage alone if the secondary of the current transformer is left connected with the primary current interrupted.

### Functional “Dry” Tests of Equipment

The Contractor shall carry out pre-commissioning tests including functional (“dry”) tests of all installed equipment, in order to demonstrate that each item of Plant is ready for operation.

The Contractor shall give the Engineer 21 days' notice of his intention for carrying out functional tests and submit a program for testing the function of each item of Plant. Within 7 days of completion of any functional test, the Contractor shall submit to the Engineer, a test reports giving detailed records of all inspections and tests carried out on the equipment or for any part of the Works. When the functional tests and inspections have been successfully completed the Engineer shall confirm their acceptance.

Functional tests of each item of Plant shall be carried out by the Contractor in accordance with the approved program, under supervision and to the satisfaction of the Engineer, comprising without limitation the items listed in sub-section 9.4.6.

### Hydraulic Tests

a)	Pumps, pipes, valves and Pressure vessels shall be hydraulically tested to the pressure as specified or to at least 2.0 times the maximum working pressure or 1.5 times the normal pressure, whichever is the greater.

b)	Testing of Pipelines

The testing of pipelines will be carried out according to Volume 3-1 Section 5. The Contractor shall provide complete pipeline, including blank flanges, caps, plugs, pressure gauges, pipe connection cocks, struts and thrust blocks, etc., and anything necessary for effectively testing of the pipelines at the required pressure.

c)	Testing of Tanks

The testing of tanks on water tightness shall be carried out similar to DVGW W 311 (or internationally acceptable standards). The following is an overview for testing with DVGW W 311. Distribution chambers and manholes of gravity pipelines shall be tested accordingly:

- External walls of the tank shall be left uncovered, easily accessed, while inside or outside faces shall not be coated or plastered before the water tightness tests have been successfully completed Excavation for tanks shall not be filled, tank wall outside and inside faces shall not be coated nor plastered, shall no plain concrete (for making of internal benching etc.) be placed before the water tightness tests have been successfully passed.

- Testing shall not commence before the concrete has hardened for 28 days.

- Filling with water shall take place at an uniform rate of not greater than 2 m in 24 hours.

- A period of 1 week shall be allowed for stabilization (intake of water into the concrete).

- Water levels shall be measured by approved means at 24 hours intervals during test period of 7 days.

- During the test period the total acceptable drop of water level, after allowing for evaporation and rainfall, shall not exceed 1/500 of the average water depth of the full tank or 1 cm, whichever is the more.

Notwithstanding the satisfactory completion of the above test, any leakage or soaking visible on the outside face of the tank walls shall be stopped, after allowing for self-sealing. Any caulking or making good of cracks in the concerned wall section shall, where practicable, be carried out from the inside face.

Adjacent internal chambers within a structure shall be tested sequentially in case the treatment process allows for emptying of the respective chamber independently of the whole structure. Then chambers adjacent to the chamber under test shall be empty during the test.

### Start-up and WWTP Performance Testing

When all civil, mechanical, electrical and control components and functions are finished, tested dry and wet (to extent possible), found in compliance with the contract conditions and accepted by the Engineer for commencement of the Start-up, the WWTP should be fed with wastewater, in coordination with “ViK” company operating the sewerage system. The Contractor will secure for by-pass of the wastewater flow in case of unforeseeable problems at the WWTP. The Contractor is fully responsible for the Start-up and running of the Plant during trial operation and shall supervise operation of the mechanical and electrical plant to effect any adjustment and remedial works that may be necessary.

The Plant testing shall not be commenced until the required quantity of wastewater flow is available and the Engineer has approved the Contractor’s proposal and program for performance testing of the Works. Subject to the approval of the Employer, testing of the Works may be subdivided into the wastewater treatment section and the sludge treatment section, which may be tested successively.

During testing the Contractor shall fully test all items of equipment and the whole plant and shall include provision and arrangement of:

i.	All skilled and qualified staff and labour for operating and testing equipment.

ii.	Provision and disposal of all consumables such as lubricants, fuel, electricity, water, etc.

iii.	All measuring and testing instruments necessary to demonstrate that the equipment 	operates complying with the Specifications and the Plant performance requirements.

The Plant performance testing period is foreseen. In this period all equipment not fully tested and all performance tests not executed during previous phases shall be executed. During this period the Contractor shall optimize the wastewater treatment process. The services to be provided during the Plant trial operation and performance testing period shall include but not be limited to the following:

- Operating of the WWTP under a series of selected routine and non-routine process modes and conditions to determine the performance of individual Plant items providing a base record of the capabilities of the WWTP for future reference.

- Operating and maintenance of the WWTP using various operating and maintenance procedures to test different and determine optimum methods of operation. The operating trials shall include but not be limited to the following:

- in coordination with “ViK” company operating the existing sewerage system, establish required wastewater inflow to the WWTP;

- cleaning intervals of the screens;

- grit and grease separation operating periods;

- oxygen supply for aeration tanks;

- excess sludge withdrawal rates, optimization of MLSS in biological tank;

- sludge pumping system characteristics at different sludge densities and 	compositions;

- sludge thickening and dewatering system characteristics at different sludge flows dry solid contents;

- Optimization of power consumption;

- Performance testing of the entire Plant to demonstrate that it’s operation complies with the Employer’s requirements and the Process Performance Guarantees. The Plant final performance testing shall be carried out for a period of 14 days which shall commence after the specified effluent quality has been achieved. The tests shall be carried out both with the actual loads at the commissioning and with the Works configured to simulate as far as possible the hydraulic and BOD loads that will occur at the design horizon. During 14 days of the final performance testing samples shall be taken daily (a total of 14 composite samples) according to Montenegrin “By-law on the wastewater quality and the sanitary-technical conditions for the discharge into a recipient (Official gazette no. 45/08, 9/10, 26/12 and 52/12) and according to the EU Urban Wastewater Directive 91/271/EEC.

The Plant final performance testing shall be deemed satisfactorily completed if the following have been achieved:

- The final effluent quality, final product standards for screenings/grit and sludge, and oxygen transfer efficiency are in accordance with the Process Performance Guarantee, with “zero test failure” and emission standards for odour and noise meet the specified performance requirements.

- The quantities of the consumables are generally within the limits stated in the Contractor's Tender.

- The system of control is suitable for automatic operation of the WWTP and that the operational parameters can be maintained within the specified range.

In addition to the parameters specified in the performance requirements, the Contractor shall record the following data on a daily basis throughout the period of performance testing:

- Weather conditions: temperature, barometric pressure, humidity, wind direction and precipitation.

- Influent flows, final effluent flows, sludge recycle rate, and return liquors return rate.

- Influent wastewater quality.

- Quantities and percentage of dry solids content of screenings, grit, and sludge.

- Physical characteristics of influent wastewater e.g. temperature, colour, odour

- Any relevant visual observations on performance of biological treatment processes e.g. activated sludge biomass, presence of foaming, etc.

- Consumption of chemicals, electrical power, fuel and potable water.

The period of testing shall terminate after the Plant has been satisfactorily and successfully run by the Contractor (as certified by the Engineer) for 28 consecutive calendar days (in conjunction with the 14 days commissioning period of the Plant final performance testing).

- Monitoring and reporting to the Engineer. If the Plant testing fail due to non-compliance with the aforementioned criteria, or do not attain the specified minimum process requirements or the Engineer is not satisfied that the operational parameters can be maintained, the Contractor shall:

- identify the reason for the failure,

- submit written proposals for rectification to the Engineer,

- obtain written approval from the Engineer for these proposals

- rectify the problem and re-test.

- All testing, sampling and records keeping shall be undertaken as required by Montenegrin legislation to enable the Employer obtaining from the authorities official permission (the “Usage Permit”) for operating the Plant within the sewerage system of Berane.

- Upon successful completion of the tests specified for the Tests on Completion, the Contractor may apply by the notice to the Engineer for a Taking Over Certificate in accordance with the Clause 10 of the Contract Conditions (“Employer’s Taking Over”).

### Performance Testing of Particular Equipment

All installed equipment shall be tested on performance by the Contractor under the supervision of and to the satisfaction of the Engineer, comprising without the following as a minimum:

a)	Each pump set shall be tested for capacity, delivery head, power consumption and mechanical reliability.

b)	Each blower shall be tested for capacity, head, power consumption and mechanical reliability.

c)	Each mixer of the wastewater or sludge mixing system shall be tested for its purpose, power consumption and mechanical reliability.

d)	Each screen shall be tested for its purpose, stability, capacity, power consumption and for full reliability in all aspects.

e)	Each screening press shall be tested for its purpose, stability, capacity, power consumption and for full reliability in all aspects.

f)	Each grit classifier shall be tested for its purpose, stability, capacity, power consumption and for full reliability in all aspects.

g)	Each aeration unit shall be tested for vibration-free running, power consumption, complete mix of liquid, sufficiently strong suspension, and freedom from mass rotation of liquid. All aeration devices specified by the Contractor shall be subject to clean water tests to establish compliance with the following parameters that shall be specified in the Contractor’s Tender:

- aeration capacity (kgO2/h);

- air flow rates (m3/h);

- blower maximum operating differential pressure (kPa); and

- aeration efficiency (kgO2/kWh)

h)	Each excess sludge mechanical thickening and sludge dewatering machine shall be tested for its purpose, stability, capacity, power consumption and for full reliability in all aspects.

I)	Each motor for the emergency power plant shall be tested for fuel input, power and thermal output and effectiveness and for full reliability in all aspects

The Contractor shall demonstrate that the above parameters are achieved during three successive tests under the same conditions.

### Performance Testing of Sub-Systems

The following sub-systems, shall be tested on performance (capacities, flows, pressures, separation effectiveness, fuel input, output of electrical and thermal energy, electrical and thermal efficiency, etc.) as a whole, including the dedicated power supply, instrumentation and local control and automation systems:

- Water supply and site process water system

- Screens and screening press

- Grit removal and classification

- Primary sludge separation, pumping and thickening

- Aerators oxygenation capacity and oxygen transfer efficiency under wastewater conditions as specified in the latest edition of the German Association for Water, Wastewater and Waste Standard under consideration of DIN EN 12255-15 for Measurement of Oxygen Transfer into Clean Water.

- Excess sludge extraction

- Excess sludge thickening

- Thickened sludge pumping, sludge mixing system

- Sludge dewatering including side systems

- All mobile and fixed lifting systems

- Emergency power plant including fuelling systems

- Electrical power supply including power switching, transforming, distribution

- Building and outdoor installations, telephone systems, security and safety systems, earthing, lightning protection systems, site lighting.

  - Tests after Completion

### General

Upon issuing the Taking-Over Certificate of the Works, the Defects Notification Period shall commence. The Tests after Completion will be carried out by the Employer in order to test the compliance of the plant operation during the DNP with the specified design parameters and to prove the specified performance and guaranteed OPEX costs. The Tests after Completion shall be performed during two (2) periods of four (4) weeks each, over the 12 months of the DNP: four weeks during the coldest months (January/February) and four weeks during the warmest months (July/August). The test shall be carried out with the actual loads.

The effluent samples shall be taken daily, i.e. 28 composite samples over each 4 week period. No more than 3 nonconforming samples shall be permitted.

In addition to the parameters specified in the performance requirements, the Contractor shall record the following data on a daily basis throughout the period of performance testing:

- Weather conditions: temperature, barometric pressure, humidity, wind direction and precipitation.

- Influent flows, final effluent flows, sludge recycle rate, and return liquors return rate.

- Influent wastewater and return liquors quality (i.e. concentration of sanitary parameters).

- Quantities and percentage of dry solids content of screenings, grit, and sludge.

- Physical characteristics of influent wastewater e.g. temperature, colour, odour

- Any relevant visual observations on performance of biological treatment processes e.g. activated sludge biomass, presence of foaming, etc.

- Consumption of chemicals, electrical power, fuel and potable water.

If the Plant testing fail due to non-compliance with the aforementioned criteria, or do not attain the specified minimum process requirements or the Engineer is not satisfied that the operational parameters can be maintained, the Contractor shall:

- identify the reason for the failure,

- submit written proposals for rectification to the Engineer,

- obtain written approval from the Engineer for these proposals

- rectify the problem and re-test until trouble-free continuous operation is achieved for a period of four weeks

The Tests after Completion shall be deemed to have been satisfactorily completed if the following have been achieved:

  - The final effluent quality, final product standards for screenings/grit and sludge, and emission standards for odour and noise meet the specified performance requirements.

  - The quantities of the consumables are generally within the limits stated in the Contractor's Tender.

# PLANT OPERATION AND TRAINING

  - Plant operation

Prior to the issue of the Taking-over Certificate the Contractor shall be responsible for Trial operation of the wastewater treatment plant (starting with its testing phase), including all associated costs of personnel, electricity, chemicals, water, other consumables, etc. During this period the Contractor shall:

- Provide operating, maintenance and training personnel according to the staff list presented by the Contractor in his tender, subject to the Engineer/Employer consent.

- Prepare, submit for approval and execute a comprehensive training programme for future operating and maintenance personnel of minimum duration 6 months, starting before commencement of the Tests on Completion and ending at the issuing of the Taking-Over Certificate. The training program shall cover overall works management, operation and maintenance, and administration functions including for procurement of goods (i.e. placing of orders, and payment of invoices etc).

- The training programme shall include assessment and examination of trainees, aiming for issuing to trainees a certificate of training and competence in performing the work activities studied. The Contractor shall submit details of his proposed training program for approval by the Engineer.

- Establish the required operating regime of the Plant. Establish the Maintenance Plan for mechanical and electrical equipment and vehicles, including implementation of appropriate maintenance software package for the Plant.

- Disposal of any “out-of-spec” screenings, grit or sludge.

During the 12 months Defects Notification Period coinciding with the Process Guarantee Period and the Guarantee Period for Operational Costs, the Contractor shall provide all technical support needed to ensure continuing compliance with the contract requirements. Contractor shall provide a prompt and effective trouble-shooting service and will take urgent corrective action whenever the continuous particulate emission monitors indicate that the WWTP is failing to meet the guaranteed performance.

  - Plant Attendance/Manning Requirements

The wastewater treatment Plant shall be designed to be manned during one 8 hour shift per day, seven days per week. At all other periods, senior management and maintenance staff should be on call for emergency needs only, triggered by the SCADA system.

  - Training

The Contractor shall prepare, submit for approval and execute training programme for the Beneficiary's assigned personnel. The training should cover all aspects of operation and maintenance of the wastewater treatment plant facilities providing full understanding of the plant operation in regular and emergency situations including practice at the existing WWTPs of similar complexity and size. The Contractor shall provide practical instructions to the Beneficiary’s staff to ensure that by the end of this period the staff will be considered by the Beneficiary to be capable of managing, operating and maintaining the Works to the highest internationally accepted standards without additional supervision. The training shall commence during Tests on Completion and end with the issuing of Taking Over Certificate

The total allowance to cover the Contractor’s expenses in connection with training shall be included in the Price Schedules

The Contractor shall identify any off-site training requirements, such as training at the premises of the equipment manufactures and include for all costs of such training.

The Contractor shall carry out the training on the basis of a structured programme, which shall be submitted not less than two (2) months before the start of the training period for review and approval to a Representative appointed by the Contracting Authority.

The training shall in general consist of familiarisation with operational aspects of the system as a whole, followed by familiarisation with the specific items of equipment on the WWTP.

The training shall be based on the actual Plant and the implementation of operation and maintenance schedules outlined in the operation and maintenance manuals provided by the Contractor.

The training for each piece of equipment shall be for a duration of not less than one week, to the satisfaction of the Employer.

The training is to be provided in advance of commissioning is aimed at enabling the Employer’s staff to participate in the full process commissioning of the system.

The Contractor shall allow for training the following numbers of personnel:

up to 5 plant operatives and maintenance personnel

up to 5 engineers

up to 2 laboratory technicians

The trainee shall be allowed the unhindered access at any time to any part of the Works/Plant.

The liability for the entire Works during training remains with the Contractor, irrespective of who may be responsible for any fault or damage.

### Training Programme

As a minimum the training programme shall include, but need not to be limited to the following:

- General training: covering the principle of the WWTP regarding its mechanical, electrical equipment and  biological treatment processes

- Operational training: Practice in operation of all mechanical and electrical equipment and its affect on the treatment processes and results. Plant optimisation and “Troubleshooting”.

- LV training: Operation of power distribution system and standby generator

- SCADA system and operational control

- Instrumentation / Automation training: Covering programming, application design, and debugging principles and practise.

- Preventive maintenance, covering all mechanical and electrical equipment.

- Health and safety procedures and training

The General Training course should be designed to cover as a minimum the following topics:

Plant hydraulics, monitoring and interpretation

Physical and biological treatment processes principles

Operating parameters, monitoring and interpretation thereof

Effluent characteristics targets

Impact of operational changes to treatment efficiency

Operational support during defects liability period

The Operations Training course shall be designed to provide the operatives with sufficient knowledge to operate the plant safely and efficiently. The course shall cover as a minimum the following topics:

Principles of motors and pumps including safe and efficient operation and practical on site demonstration

Principles and importance of the different machines and components

Monitoring requirements and trouble shooting of all main components

Energy efficiency

Practical hands on operation and maintenance on equipment provided

Operational support during defects liability period

The LV Training course shall be designed to provide operatives with knowledge of the installed electrical system in order to safely operate the system. The course shall cover as a minimum the following topics:

Operation of low voltage systems

Operation of emergency power systems

Troubleshooting electrical faults

Maintenance and repairs of distribution panels and switchgear

Operational support during defects liability period

This SCADA course shall be designed to familiarize the assigned Beneficiary staff with the general running of the standard operating system including but not limited to:

- Loading and starting up the Plant

- System Operators interface

- Operator control of programme/task execution

- Operator control of disc files

- Operator response to system failure, online/offline diagnostics, transfer of control between the computers synchronization of the system database

- PLC system interrogation facilities – alarm lists, log printouts select mimic and trend display etc.

- Alarm acknowledge accept/delete

- Control actions e.g. start pump, close valve etc

- All functions associated with each access level of the PLC system

Operational support during defects liability period

The Instrumentation and automation training course is intended for operatives who will be responsible for maintaining and repairing instrumentation hardware and control software installed in various areas of the WWTP. The course shall cover as a minimum the following topics:

Methods and principles of instrumentation

Practical hands on maintenance of the different instrumentation equipment on the WWTP

Operation and fault detection for all instrumentation and PLCs

Programming of PLCs with practical training

Debugging of control programmes

Programming of EEPROMS and flashcards

Operational support during defects liability period

The Preventive Maintenance Course shall be designed around all the equipment that has been provided for the WWTP. The course shall cover as a minimum the following topics:

Planned maintenance programming

Practical hands-on maintenance on actual or practice equipments

Operational support during defects liability period

The Health and Safety Course shall provide operatives with the knowledge of potentially dangerous situations which can arise at a WWTP. The course shall cover as a minimum the following topics:

Legal requirements

Dangerous materials at WWTP

Dangerous situations and environment at WWTP

Avoidance strategies

Safety equipment

Safety procedures

### Execution of Training

For each course the Contractor shall indicate the operatives which must obligatorily attend the course as well as those for which the training is recommended. Courses can be held in parallel for efficient use of the time of the operatives and therefore the training programme must be designed to ensure that the operatives can satisfactorily operate the plant on completion.

To ensure that adequate training is given, the training personnel from the Contractor shall carry out each and every Operation and Maintenance activity identified in the Operation, Maintenance and Safety Manuals and shall train the Employer’s personnel to carry out these activities even if they are not required during the actual operation of the Works.

The Contractor shall pay particular attention to safety training for all assigned personnel. Safety training shall not be limited to personal safety, but shall include detailed actions to be taken by all staff in emergency situations and the use of all safety equipment. The Contractor shall be responsible for establishing procedural links with the appropriate emergency services.

The Contractor shall make available during the training period, all necessary facilities for training including didactic equipment, simulators video, slide and overhead projection equipment.

Training shall be carried out in the English language. The Contractor shall provide a sufficient number of interpreters to overcome any difficulties arising due the assigned local personnel not being sufficiently fluent in the English language.

### Contractor's Training Personnel

The Contractor shall provide training personnel for each of the positions required for management, Operation and Maintenance as identified in the training programme. The duties of each of the training personnel shall be to manage, operate and maintain that element or those elements of the Works appropriate to his position, and to train the Beneficiary’s assigned staff members for that particular position. The emphasis shall be on "hands-on" training.

In addition to his normal training personnel, the Contractor shall also provide specialist trainers who shall be responsible for formal classroom, laboratory or workshop training.

  - Operation and Maintenance Manual

It is the Contractors responsibility to prepare a comprehensive O&M manual for all components of the project. The manual presents procedures to facilitate operation and maintenance of the plant under all conditions, technical guidance for troubleshooting, and requirements for compliance with the permits and approvals issued. The manual must address the needs of the system being employed and must be directed toward the level of training required of the operating staff.

The manual must also include a plan of operation which must be submitted sufficiently early to allow the Beneficiary to prepare for the taking over of the plant and its operation. The plan of operation must provide a concise, sequential description of and implementation schedule for the following activities:

The qualification and number of operators;

Training requirements for operators;

Start-up schedules and services;

Safety programs, plans and procedures;

Emergency operations procedures and plan;

Process monitoring program with all process parameters;

Laboratory and testing requirements;

Maintenance of water quality and public health

Health & Safety plan

A draft plan of operation must be prepared at the mid-point of construction for review and approval. The final plan of operation shall be provided to the Beneficiary no later than 30 days before Taking Over.

On approval the plan of operation shall be included in the operation and maintenance manual.

The O&M manual shall have the following contents:

Explanatory plant description

Operation and maintenance guidance manual

The complete list of addresses and phone numbers of all manufacturers and suppliers

A complete file or written operation and maintenance instructions obtained from the manufacturers and suppliers

Explanatory drawings and details of any operation likely to be carried out during the life of the plant (testing, operation, maintenance, dismantling and repair

Orderly compilation of the maintenance handbooks submitted by the respective plant suppliers

Recommended maintenance and test activities / procedures and detailed for daily, weekly, monthly and other intervals

Spare part management

Works procedure sheets

Comprehensive Control Philosophy of the plant

General and preventive maintenance

Trouble shooting

  - Process Monitoring

The Contractor shall set up procedures for recording of the parameters presented in the table below. These procedures are to be implemented by the Beneficiary, supported by the Contractor in periodic assistance missions.

Table 10-1: List of process monitoring parameters

| Parameters | Measuring Frequency |  |  |  |
| --- | --- | --- | --- | --- |
|  | Daily | Bi-daily | Weekly | Monthly |
| - Climatic conditions | X |  |  |  |
| - Wastewater flows at inlet and outlet of the WWTP | X a) |  |  |  |
| - Special conditions | X b) |  |  |  |
| - Wastewater characteristics (pH, temperature, conductivity) at inflow and effluent of the WWTP | X c) |  |  |  |
| - Wastewater concentrations (SS, COD, BOD5) at inflow and effluent of the WWTP | X d) |  |  |  |
| - Wastewater concentrations (organic SS, NH4-N, PO4-P) at inflow of the WWTP |  |  | X d) |  |
| - Wastewater concentrations (organic N, NO3-N, P tot) at inflow of the WWTP |  |  |  | X d) |
| - Wastewater concentrations (heavy metals) at inflow of the WWTP |  |  |  | X d) |
| - Wastewater concentrations (SS, organic SS, COD, BOD5) before aeration tanks |  |  | X e) |  |
| - Wastewater concentrations (NH4-N, PO4-P) before aeration tanks |  |  |  | X e) |
| - Wastewater pollution loads at inflow | f), frequency like concentrations |  |  |  |
| - Wastewater pollution loads before aeration tanks | f), frequency like concentrations |  |  |  |
| - Treatment efficiency for the different wastewater parameters | f), frequency like concentrations |  |  |  |
| - Volume and weight of screenings and grit disposed off to landfill | g) |  |  |  |
| - MLSS, sludge volume and sludge volume index in the aeration tanks | X e) |  |  |  |
| - Sludge loading, volume loading, sludge age | X f) |  |  |  |
| - Sludge flows (excess sludge before thickening) | X a) |  |  |  |
| - Dry substances concentrations and ignition loss of all above listed | X e) |  |  |  |
| - Sludge quantities of all above listed sludge | f), frequency like concentrations |  |  |  |
| - Sludge quantities (dewatered sludge, sludge leaving the WWTP) | g) |  |  |  |
| - continuous online measurement, daily quantity readout - if necessary - calculated daily average of continuous online measurements - 24-hour flow proportional composite sample from automatic sampler - qualified grab sample (5 aliquots every 5 minutes taken) with statement of time - calculated - quantity leaving the Plant with statement of date |  |  |  |  |

Any deviation from the expected values should be investigated and reported upon at the end of every month.

Assessment of flood endangered areas of Municipality Berane (August, 2011.)

Theoretical value in clear water