## Foglio di lavoro in Preventivo
NOTE: UNIT PRICES SHALL BE ENTERED WITHOUT V.A.T.
C | POWER BLOCK
NOTES:
If, within the scope of particular items, the manufacturer of the equipment or material is listed, the Tenderer may install the equipment and material of the other manufacturer provided that such equipment and material have the same or equivalent or better characteristics corresponding to the project documentation. All the materials and elements that will be used during the performance of works shall be approved by the Employer.
All preparatory works, final cleaning of the facility, chase cutting, punching, drilling, repairing of damaged surfaces, etc. necessary for the performance of particular items of work, as well as testing of installed materials, installations and equipment, obtaining the required certificates, shall not be calculated or paid separately. The Tenderer shall be obliged to allocate and cover the costs for these works within the scope of the unit prices of the items referred to in the bill of quantities. The performance of the listed items of works shall understand all necessary construction materials, equipment, formwork, scaffolding, external and internal transport, construction site organisation, construction site connections, labour force, insurance, etc. with elements and costs required for completion of particular works in acordance with the prescribed conditions, the total finalisation with the appropriate guarantee - everything set for the technical acceptance.
CODE | DESCRIPTION | UOM. | NO. | PRICE PER UNIT | TOTAL AMOUNT
01 | ELECTRICAL INSTALLATIONS - SUBSTATION SS 10/0,4 kV, UNINTERRUPTIBLE POWER SUPPLY, DIESEL ELECTRICAL GENERATING UNIT
01 -CONDUCTORS, CABLES AND ACCESSORIES
A120.A10.A4 |  | n
MEDIUM VOLTAGE CABLE TERMINALS In accordance with standards: CEI 20-24 and subsequent amendments. Manufacturing characteristics: - compression connector; - insertion insulators (for types made of
elastomer); - connection for earthing; -bracket (optionally). Reaction to fire: - It does not spread fire.
25-240 mm2 8,7/15kV rubber terminal for interior
| MV/LV SUBSTATION - MV/LV CABLES |  | 12
| Total amount |  | 12
A210.A20.A2 |  | m
H07Z1-K 450 / 750V CABLE H07Z1-K type 2 450 / 750V In accordance with standards: CEI 20-22 / 3, 20-38 / 1 and subsequent amendments. Rated voltage: 450/750 V. Insulation: thermoplastic mass. Conductor: flexible red copper rope
Reaction to fire: - It does not spread fire ; - reduced smoke emission, toxic and corrosive gases
H07Z1-K 450/750V cable 1x2,5 mm2
| LV SUBSTATION - MV/LV CABLES |  | 30
| Total amount |  | 30
A210.A20.A6 |  | m
H07Z1-K 450 / 750V CABLE H07Z1-K type 2 450 / 750V In accordance with standards: CEI 20-22 / 3, 20-38 / 1 and subsequent amendments. Rated voltage: 450/750 V. Insulation: thermoplastic mass. Conductor: flexible red copper rope
Reaction to fire: - It does not spread fire ; - reduced smoke emission, toxic and corrosive gases
H07Z1-K 450/750V cable 1x16 mm2
| LV SUBSTATION - MV/LV CABLES |  | 15
| Total amount |  | 15
A220.A20.A10 |  | m
FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV CABLE FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV In accordance with standards: CEI 20-13, 20-22 / 3 and subsequent amendments. In accordance with the tables: CEI-UNEL 35382, 35384. Rated: 600/1000 V. Insulation:
ethylene-propylene rubber type G7. Cover: made of special thermoplastic polymer of M1 quality. Filling: unvulcanized rubber. Conductor: flexible hardened copper rope. Protection (optionally): copper braid. Reaction to
fire: - it does not spread fire; - reduced smoke emission, toxic and corrosive gases
FG7M1 0,6/1kV cable 1x70 mm2
| LV SUBSTATION - MV/LV CABLES |  | 55
| Total amount |  | 55
A220.A20.A12 |  | m
FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV CABLE FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV In accordance with standards: CEI 20-13, 20-22 / 3 and subsequent amendments. In accordance with the tables: CEI-UNEL 35382, 35384. Rated voltage: 600/1000 V. Insulation:
ethylene-propylene rubber type G7. Cover: made of special thermoplastic polymer of M1 quality. Filling: unvulcanized rubber. Conductor: flexible hardened copper rope. Protection (optionally): copper braid. Reaction to
fire: - it does not spread fire; - reduced smoke emission, toxic and corrosive gases
FG7M1 0,6/1kV cable 1x120 mm2
| LV SUBSTATION - MV/LV CABLES |  | 220
| Total amount |  | 220
A220.A20.A15 |  | m
FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV CABLE FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV In accordance with standards: CEI 20-13, 20-22 / 3 and subsequent amendments. In accordance with the tables: CEI-UNEL 35382, 35384. Rated voltage: 600/1000 V. Insulation:
ethylene-propylene rubber type G7. Cover: made of special thermoplastic polymer of M1 quality. Filling: unvulcanized rubber. Conductor: flexible hardened copper rope. Protection (optionally): copper braid. Reaction to
fire: - it does not spread fire; - reduced smoke emission, toxic and corrosive gases
FG7M1 0,6/1kV cable 1x240 mm2
| LV SUBSTATION - MV/LV CABLES |  | 345
| Total amount |  | 345
A220.A20.A31 |  | m
FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV CABLE FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV In accordance with standards: CEI 20-13, 20-22 / 3 and subsequent amendments. In accordance with the tables: CEI-UNEL 35382, 35384. Rated voltage: 600/1000 V. Insulation:
ethylene-propylene rubber type G7. Cover: made of special thermoplastic polymer of M1 quality. Filling: unvulcanized rubber. Conductor: flexible hardened copper rope. Protection (optionally): copper braid. Reaction to
fire: - it does not spread fire; - reduced smoke emission, toxic and corrosive gases
FG7OM1 0,6/1kV cable 3x2,5 mm2
| LV SUBSTATION - MV/LV CABLES |  | 1495
| Total amount |  | 1495
A220.A20.A32 |  | m
FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV CABLE FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV In accordance with standards: CEI 20-13, 20-22 / 3 and subsequent amendments. In accordance with the tables: CEI-UNEL 35382, 35384. Rated voltage: 600/1000 V. Insulation:
ethylene-propylene rubber type G7. Cover: made of special thermoplastic polymer of M1 quality. Filling: unvulcanized rubber. Conductor: flexible hardened copper rope. Protection (optionally): copper braid. Reaction to
fire: - it does not spread fire; - reduced smoke emission, toxic and corrosive gases
FG7OM1 0,6/1kV cable 3x4 mm2
| LV SUBSTATION - MV/LV CABLES |  | 1545
| Total amount |  | 1545
A220.A20.A33 |  | m
FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV CABLE FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV In accordance with standards: CEI 20-13, 20-22 / 3 and subsequent amendments. In accordance with the tables: CEI-UNEL 35382, 35384. Rated voltage: 600/1000 V. Insulation:
ethylene-propylene rubber type G7. Cover: made of special thermoplastic polymer of M1 quality. Filling: unvulcanized rubber. Conductor: flexible hardened copper rope. Protection (optionally): copper braid. Reaction to
fire: - it does not spread fire; - reduced smoke emission, toxic and corrosive gases
FG7OM1 0,6/1kV cable 3x6 mm2
| LV SUBSTATION - MV/LV CABLES |  | 300
| Total amount |  | 300
A220.A20.A49 |  | m
FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV CABLE FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV In accordance with standards: CEI 20-13, 20-22 / 3 and subsequent amendments. In accordance with the tables: CEI-UNEL 35382, 35384. Rated voltage: 600/1000 V. Insulation:
ethylene-propylene rubber type G7. Cover: made of special thermoplastic polymer of M1 quality. Filling: unvulcanized rubber. Conductor: flexible hardened copper rope. Protection (optionally): copper braid. Reaction to
fire: - it does not spread fire; - reduced smoke emission, toxic and corrosive gases
FG7OM1 0,6/1kV cable 4x10 mm2
| LV SUBSTATION - MV/LV CABLES |  | 380
| Total amount |  | 380
A220.A20.A50 |  | m
FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV CABLE FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV In accordance with standards: CEI 20-13, 20-22 / 3 and subsequent amendments. In accordance with the tables: CEI-UNEL 35382, 35384. Rated voltage: 600/1000 V. Insulation:
ethylene-propylene rubber type G7. Cover: made of special thermoplastic polymer of M1 quality. Filling: unvulcanized rubber. Conductor: flexible hardened copper rope. Protection (optionally): copper braid. Reaction to
fire: - it does not spread fire; - reduced smoke emission, toxic and corrosive gases
FG7OM1 0,6/1kV cable 4x16 mm2
| LV SUBSTATION - MV/LV CABLES |  | 85
| Total amount |  | 85
A220.A20.A62 |  | m
FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV CABLE FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV In accordance with standards: CEI 20-13, 20-22 / 3 and subsequent amendments. In accordance with the tables: CEI-UNEL 35382, 35384. Rated voltage: 600/1000 V. Insulation:
ethylene-propylene rubber type G7. Cover: made of special thermoplastic polymer of M1 quality. Filling: unvulcanized rubber. Conductor: flexible hardened copper rope. Protection (optionally): copper braid. Reaction to
fire: - it does not spread fire; - reduced smoke emission, toxic and corrosive gases
FG7OM1 0,6/1kV cable 5x4 mm2
| LV SUBSTATION - MV/LV CABLES |  | 420
| Total amount |  | 420
A220.A20.A64 |  | m
FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV CABLE FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV In accordance with standards: CEI 20-13, 20-22 / 3 and subsequent amendments. In accordance with the tables: CEI-UNEL 35382, 35384. Rated voltage: 600/1000 V. Insulation:
ethylene-propylene rubber type G7. Cover: made of special thermoplastic polymer of M1 quality. Filling: unvulcanized rubber. Conductor: flexible hardened copper rope. Protection (optionally): copper braid. Reaction to
fire: - it does not spread fire; - reduced smoke emission, toxic and corrosive gases
FG7OM1 0,6/1kV cable 5x10 mm2
| LV SUBSTATION - MV/LV CABLES |  | 65
| Total amount |  | 65
A220.A20.A65 |  | m
FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV CABLE FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV In accordance with standards: CEI 20-13, 20-22 / 3 and subsequent amendments. In accordance with the tables: CEI-UNEL 35382, 35384. Rated voltage: 600/1000 V. Insulation:
ethylene-propylene rubber type G7. Cover: made of special thermoplastic polymer of M1 quality. Filling: unvulcanized rubber. Conductor: flexible hardened copper rope. Protection (optionally): copper braid. Reaction to
fire: - it does not spread fire; - reduced smoke emission, toxic and corrosive gases
FG7OM1 0,6/1kV cable 5x16 mm2
| LV SUBSTATION - MV/LV CABLES |  | 80
| Total amount |  | 80
A220.A20.A7 |  | m
FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV CABLE FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV In accordance with standards: CEI 20-13, 20-22 / 3 and subsequent amendments. In accordance with the tables: CEI-UNEL 35382, 35384. Rated voltage: 600/1000 V. Insulation:
ethylene-propylene rubber type G7. Cover: made of special thermoplastic polymer of M1 quality. Filling: unvulcanized rubber. Conductor: flexible hardened copper rope. Protection (optionally): copper braid. Reaction to
fire: - it does not spread fire; - reduced smoke emission, toxic and corrosive gases
FG7M1 0,6/1kV cable 1x25 mm2
| LV SUBSTATION - MV/LV CABLES |  | 610
| Total amount |  | 610
A220.A20.A8 |  | m
FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV CABLE FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV In accordance with standards: CEI 20-13, 20-22 / 3 and subsequent amendments. In accordance with the tables: CEI-UNEL 35382, 35384. Rated voltage: 600/1000 V. Insulation:
ethylene-propylene rubber type G7. Cover: made of special thermoplastic polymer of M1 quality. Filling: unvulcanized rubber. Conductor: flexible hardened copper rope. Protection (optionally): copper braid. Reaction to
fire: - it does not spread fire; - reduced smoke emission, toxic and corrosive gases
FG7M1 0,6/1kV cable 1x35 mm2
| LV SUBSTATION - MV/LV CABLES |  | 20
| Total amount |  | 20
A220.A20.A9 |  | m
FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV CABLE FG7M1 0.6 / 1kV, FG7OM1 0.6 / 1kV In accordance with standards: CEI 20-13, 20-22 / 3 and subsequent amendments. In accordance with the tables: CEI-UNEL 35382, 35384. Rated voltage: 600/1000 V. Insulation:
ethylene-propylene rubber type G7. Cover: made of special thermoplastic polymer of M1 quality. Filling: unvulcanized rubber. Conductor: flexible hardened copper rope. Protection (optionally): copper braid. Reaction to
fire: - it does not spread fire; - reduced smoke emission, toxic and corrosive gases
FG7M1 0,6/1kV cable 1x50 mm2
| LV SUBSTATION - MV/LV CABLES |  | 20
| Total amount |  | 20
A230.A10.A23 |  | m
FTG10M1 0.6 / 1kV CEI 20-45 FIRE RESISTANT CABLE FTG10M1 0.6 / 1kV CEI 20-45, FTG10OM1 0.6 / 1kV CEI 20-45 In accordance with standards: CEI 20-22 / 3, 20-38, 20 -45 and subsequent amendments; EN50200. Rated voltage: 600/1000 V. Insulation:
mass of ethylene-propylene rubber quality G10. Cover: made of special thermoplastic polymer of M1 quality. Filling: atoxic rubber. Conductor: flexible tinned copper rope coated with insulating tape. Reaction to
fire: - it does not spread fire; - reduced smoke emission, toxic and corrosive gases ; - operation run-on of at least 180 min. at 750 ° C with mechanical shock every 5 minutes
FTG10M1 0,6/1kV CEI 20-45 fire resistant cable 2x4 mm2
| LV SUBSTATION - MV/LV CABLES |  | 65
| Total amount |  | 65
A230.A10.A25 |  | m
FTG10M1 0.6 / 1kV CEI 20-45 FIRE RESISTANT CABLE FTG10M1 0.6 / 1kV CEI 20-45, FTG10OM1 0.6 / 1kV CEI 20-45 In accordance with standards: CEI 20-22 / 3, 20-38, 20 -45 and subsequent amendments; EN50200. Rated voltage: 600/1000 V. Insulation:
mass of ethylene-propylene rubber quality G10. Cover: made of special thermoplastic polymer of M1 quality. Filling: atoxic rubber. Conductor: flexible tinned copper rope coated with insulating tape. Reaction to
fire: - it does not spread fire; - reduced smoke emission, toxic and corrosive gases ; - operation run-on of at least 180 min. at 750 ° C with mechanical shock every 5 minutes
FTG10OM1 0,6/1kV CEI 20-45 fire resistant cable 2x10 mm2
| LV SUBSTATION - MV/LV CABLES |  | 280
| Total amount |  | 280
A230.A10.A32 |  | m
FTG10M1 0.6 / 1kV CEI 20-45 FIRE RESISTANT CABLE FTG10M1 0.6 / 1kV CEI 20-45, FTG10OM1 0.6 / 1kV CEI 20-45 In accordance with standards: CEI 20-22 / 3, 20-38, 20 -45 and subsequent amendments; EN50200. Rated voltage: 600/1000 V. Insulation:
mass of ethylene-propylene rubber quality G10. Cover: made of special thermoplastic polymer of M1 quality. Filling: atoxic rubber. Conductor: flexible tinned copper rope coated with insulating tape. Reaction to
fire: - it does not spread fire; - reduced smoke emission, toxic and corrosive gases ; - operation run-on of at least 180 min. at 750 ° C with mechanical shock every 5 minutes
FTG10OM1 0,6/1kV CEI 20-45 fire resistant cable 3x2,5 mm2
| LV SUBSTATION - MV/LV CABLES |  | 315
| Total amount |  | 315
A230.A10.A45 |  | m
FTG10M1 0.6 / 1kV CEI 20-45 FIRE RESISTANT CABLE FTG10M1 0.6 / 1kV CEI 20-45, FTG10OM1 0.6 / 1kV CEI 20-45 In accordance with standards: CEI 20-22 / 3, 20-38, 20 -45 and subsequent amendments; EN50200. Rated voltage: 600/1000 V. Insulation:
mass of ethylene-propylene rubber quality G10. Cover: made of special thermoplastic polymer of M1 quality. Filling: atoxic rubber. Conductor: flexible tinned copper rope coated with insulating tape. Reaction to
fire: - it does not spread fire; - reduced smoke emission, toxic and corrosive gases ; - operation run-on of at least 180 min. at 750 ° C with mechanical shock every 5 minutes
FTG10M1 0,6/1kV CEI 20-45 fire resistant cable 4x10 mm2
| LV SUBSTATION - MV/LV CABLES |  | 160
| Total amount |  | 160
A230.A10.A46 |  | m
FTG10M1 0.6 / 1kV CEI 20-45 FIRE RESISTANT CABLE FTG10M1 0.6 / 1kV CEI 20-45, FTG10OM1 0.6 / 1kV CEI 20-45 In accordance with standards: CEI 20-22 / 3, 20-38, 20 -45 and subsequent amendments; EN50200. Rated voltage: 600/1000 V. Insulation:
mass of ethylene-propylene rubber quality G10. Cover: made of special thermoplastic polymer of M1 quality. Filling: atoxic rubber. Conductor: flexible tinned copper rope coated with insulating tape. Reaction to
fire: - it does not spread fire; - reduced smoke emission, toxic and corrosive gases ; - operation run-on of at least 180 min. at 750 ° C with mechanical shock every 5 minutes
FTG10M1 0,6/1kV CEI 20-45 fire resistant cable 4x16 mm2
| LV SUBSTATION - MV/LV CABLES |  | 40
| Total amount |  | 40
A230.A10.A56 |  | m
FTG10M1 0.6 / 1kV CEI 20-45 FIRE RESISTANT CABLE FTG10M1 0.6 / 1kV CEI 20-45, FTG10OM1 0.6 / 1kV CEI 20-45 In accordance with standards: CEI 20-22 / 3, 20-38, 20 -45 and subsequent amendments; EN50200. Rated voltage: 600/1000 V. Insulation:
mass of ethylene-propylene rubber quality G10. Cover: made of special thermoplastic polymer of M1 quality. Filling: atoxic rubber. Conductor: flexible tinned copper rope coated with insulating tape. Reaction to
fire: - it does not spread fire; - reduced smoke emission, toxic and corrosive gases ; - operation run-on of at least 180 min. at 750 ° C with mechanical shock every 5 minutes
FTG10M1 0,6/1kV CEI 20-45 fire resistant cable 5x16 mm2
| LV SUBSTATION - MV/LV CABLES |  | 80
| Total amount |  | 80
A230.A10.A7 |  | m
FTG10M1 0.6 / 1kV CEI 20-45 FIRE RESISTANT CABLE FTG10M1 0.6 / 1kV CEI 20-45, FTG10OM1 0.6 / 1kV CEI 20-45 In accordance with standards: CEI 20-22 / 3, 20-38, 20 -45 and subsequent amendments; EN50200. Rated voltage: 600/1000 V. Insulation:
mass of ethylene-propylene rubber quality G10. Cover: made of special thermoplastic polymer of M1 quality. Filling: atoxic rubber. Conductor: flexible tinned copper rope coated with insulating tape. Reaction to
fire: - it does not spread fire; - reduced smoke emission, toxic and corrosive gases ; - operation run-on of at least 180 min. at 750 ° C with mechanical shock every 5 minutes
FTG10M1 0,6/1kV CEI 20-45 fire resistant cable 1x25 mm2
| LV SUBSTATION - MV/LV CABLES |  | 40
| Total amount |  | 40
A230.A10.A9 |  | m
FTG10M1 0.6 / 1kV CEI 20-45 FIRE RESISTANT CABLE FTG10M1 0.6 / 1kV CEI 20-45, FTG10OM1 0.6 / 1kV CEI 20-45 In accordance with standards: CEI 20-22 / 3, 20-38, 20 -45 and subsequent amendments; EN50200. Rated voltage: 600/1000 V. Insulation:
mass of ethylene-propylene rubber quality G10. Cover: made of special thermoplastic polymer of M1 quality. Filling: atoxic rubber. Conductor: flexible tinned copper rope coated with insulating tape. Reaction to
fire: - it does not spread fire; - reduced smoke emission, toxic and corrosive gases ; - operation run-on of at least 180 min. at 750 ° C with mechanical shock every 5 minutes
FTG10M1 0,6/1kV CEI 20-45 fire resistant cable 1x50 mm2
| LV SUBSTATION - MV/LV CABLES |  | 140
| Total amount |  | 140
A290.A10.A6 |  | m
COMPACT COPPER BUSBARS - LINEAR UNITS In accordance with standards: CEI 17-13 / 1, 17-13 / 2 and subsequent options. Electrical properties: - Rated operating voltage (Ue): 400V; - Rated insulation
voltage (Ui): 1000V; - rated frequency: 50 Hz; - rated current (In): as indicated on the type; - place of installation: interior. Manufacturing characteristics: - system of copper or aluminum busbars, compact "sandwich" constructions,
in which the busbars themselves are appropriately insulated and then mounted next to each other; completely closed cover, without ventilation holes and with a guarantee of complete safety from direct contact and internal collection of
dust, consisting of a sheet steel profile with a thickness of min. 1.5 mm, hot-dip galvanized, interconnected by hemming; wide area of thermal exchange obtained by rationalisation of
the ratio between profile height and thickness; - single or double partitioning (as a function of the allowed amount of electricity) for each phase; - neutral and protective conductors with a share of 100% of the phase share; conductors
consisting of solid busbars or profiled tubes of electrolytic copper (UNI 5649/71 EPT 99.9) tinned over the entire surface before galvanizing and nickel plating of about 15 microns, thus guaranteeing a salt mist resistance of at least 30 hours and a resistance to
double thermal shock cycle at a temperature of 200 ° C; -insulation between busbars by bandaging a double cover of insulating polyester with a temperature class of F (155 ° C) or higher then packed
like a sandwich; - system of connecting units achieved by monoblocks with terminal boards made of silver-plated copper, with screws tightened with a torque wrench (foot nut or with unblocking after electromechanical tightening) and anti-released coil
devices; - hanging elements bandaged around the structure of the busbar to avoid slipping or rotation of the linear units, creating a place of attachment of the brackets to the wall. Degree of protection min .: IP55.
Materials for work completion: participation of additional equipment for fixing and installation (holders, brackets, etc.); - participation of additional equipment and materials for connection between different units; - obligations to connect to appliances and lines
covered by the lease agreement. Materials not covered by the work are described separately: - power supply device; - device for operating; - device for connection to the transformer / switchboard; - flame protection device.
Compact copper busbar, IP55 3P+N+E 2000A
| MV/LV SUBSTATION- MV/LV CABLES |  | 8
| Total amount |  | 8
A291.A30.A5 |  | n
COMPACT COPPER BUSBARS - POWER UNITS In accordance with standards: CEI 17-13 / 1, 17-13 / 2 and subsequent amendments. Electrical properties: - Rated operating voltage (Ue):
400V; - rated insulation voltage (Ui): 1000V; - rated frequency: 50 Hz; - rated current (In): as indicated on the type; - place of installation: interior. Manufacturing characteristics: - sheet metal section, box-shaped, coated with
epoxy resin or polyamide resin reinforced with self-extinguishing glass fibers, with adequately profiled terminals of dimensions that provide the connection of power cables to a rectilinear element;
- traces previously prepared for the use of tensioners; - hinged cover; - possibility of installation at the ends of safety latches or at any point of connection of rectilinear elements by connecting to
switch; - seals and other necessary equipment with standard material that guarantees the required degree of protection
Compact copper busbar - transformer power supply unit, 3P + N + E, I = 2000A, IP55
| MV/LV SUBSTATION- MV/LV CABLES |  | 1
| Total amount |  | 1
A291.A30.A55 |  | n
COMPACT COPPER BUSBARS - POWER UNITS In accordance with standards: CEI 17-13 / 1, 17-13 / 2 and subsequent amendments. Electrical properties: - Rated operating voltage (Ue):
400V; - rated insulation voltage (Ui): 1000V; - rated frequency: 50 Hz; - rated current (In): as indicated on the type; - place of installation: interior. Manufacturing characteristics: - sheet metal section, box-shaped, coated with
epoxy resin or polyamide resin reinforced with self-extinguishing glass fibers, with adequately profiled terminals of dimensions that provide the connection of power cables to a rectilinear element;
- traces previously prepared for the use of tensioners;; - hinged cover; - possibility of installation at the ends of safety latches or at any point of connection of rectilinear elements by connecting to
switch; - seals and other necessary equipment with standard material that guarantees the required degree of protection
Compact copper busbar - transformer power supply unit, 3P + N + E, I = 2000A, IP55
| MV/LV SUBSTATION- MV/LV CABLES |  | 1
| Total amount |  | 1
TOTAL CONDUCTORS, CABLES AND ACCESSORIES
02 - INSTALLATION HOSES
B10.A40.A12 |  | m
WIRE MESH CABLE TRAY MADE OF HOT DIP GALVANIZED STEEL In accordance with standards: CEI 23-76, CEI 7-6 and subsequent amendments. Impact resistance:> 1J at ambient temperature of (20 ° C ± 5)
Mechanical resistance: minimum permissible load (measured values for the maximum deformation of the curve of 1/200 of the mean load capacity, connection at 1/5 of the space between the cable trays) measured in accordance with the relevant product standards: - cable trays 50 mm high, support
span 1,5 m; * 18 kg / m for trunkings 50-100 mm wide; * 27 kg / m for 150 mm wide trunkings; * 33 kg / m for 200 mm wide trunkings; * 63 kg / m for trunkings with a width of 300 mm; * 104 kg / m for 400 mm wide trunkings; * 120 kg / m
for trunkings 500-600 mm wide; - support span 100 mm high, support span 1.5 m: * 37 kg / m for trunkings 100 mm wide; * 53 kg / m for 150 mm wide trunkings; * 73 kg / m for 200 mm wide trunkings; * 104 kg / m for trunkings
300-400 mm wide; * 125 kg / m for trunkings 500-600 mm wide. Electrical properties: - electrical continuity guaranteed by electrical resistance (at 12V AC max 50Hz, 25A): 0.005 ohms per meter and <= 0.05 ohms
in accordance with connection. Manufacturing characteristics: - cable tray made of welded steel wires, hot-dip galvanized after processing, previously degreased and cleaned, and finally coated (certain types if necessary)
with epoxy and polyester resin; - safety edge without parts with sharp corners; - minimum mass of zinc layer: 330 g / m2 +/- 10%; - average density of zinc layer: 50 micron +/- 10%. - cover
(if necessary) made of steel with the same treatment and design characteristics of the base, with closing by a latch or by means of hooks that cannot be lost. Reaction to fire: self-extinguishing coating (if necessary)
Wire mesh cable tray made of galvanized steel, size 100x105mm
| LV SUBSTATION - MV / LV CABLE TRAYS |  | 5
| Total amount |  | 5
B10.A40.A14 |  | m
WIRE MESH CABLE TRAY MADE OF HOT DIP GALVANIZED STEEL In accordance with standards: CEI 23-76, CEI 7-6 and subsequent changes. Impact resistance:> 1J at ambient temperature of (20 ° C ± 5)
Mechanical resistance: minimum permissible load (measured values for the maximum deformation of the curve of 1/200 of the mean load capacity, connection at 1/5 of the space between the cable trays) measured in accordance with the relevant product standards: - cable trays 50 mm high, support
span 1,5 m; * 18 kg / m for trunkings 50-100 mm wide; * 27 kg / m for 150 mm wide trunkings; * 33 kg / m for 200 mm wide trunkings; * 63 kg / m for trunkings with a width of 300 mm; * 104 kg / m for 400 mm wide trunkings; * 120 kg / m
for trunkings 500-600 mm wide; - support span 100 mm high, support span 1.5 m: * 37 kg / m for trunkings 100 mm wide; * 53 kg / m for 150 mm wide trunkings; * 73 kg / m for 200 mm wide trunkings; * 104 kg / m for trunkings
300-400 mm wide; * 125 kg / m for trunkings 500-600 mm wide. Electrical properties: - electrical continuity guaranteed by electrical resistance (at 12V AC max 50Hz, 25A): 0.005 ohms per meter and <= 0.05 ohms
in accordance with connection. Manufacturing characteristics: - cable tray made of welded steel wires, hot-dip galvanized after processing, previously degreased and cleaned, and finally coated (certain types if necessary)
with epoxy and polyester resin; - safety edge without parts with sharp corners; - minimum mass of zinc layer: 330 g / m2 +/- 10%; - average density of zinc layer: 50 micron +/- 10%. - cover
(if necessary) made of steel with the same treatment and design characteristics of the base, with closing by a latch or by means of hooks that cannot be lost. Reaction to fire: self-extinguishing coating (if necessary)
Wire mesh cable tray made of galvanized steel, size 200x105mm
| LV SUBSTATION - MV / LV CABLE TRAYS |  | 15
| Total amount |  | 15
B10.A40.A16 |  | m
WIRE MESH CABLE TRAY MADE OF HOT DIP GALVANIZED STEEL In accordance with standards: CEI 23-76, CEI 7-6 and subsequent changes. Impact resistance:> 1J at ambient temperature of (20 ° C ± 5)
Mechanical resistance: minimum permissible load (measured values for the maximum deformation of the curve of 1/200 of the mean load capacity, connection at 1/5 of the space between the cable trays) measured in accordance with the relevant product standards: - cable trays 50 mm high, support
span 1,5 m; * 18 kg / m for trunkings 50-100 mm wide; * 27 kg / m for 150 mm wide trunkings; * 33 kg / m for 200 mm wide trunkings; * 63 kg / m for trunkings with a width of 300 mm; * 104 kg / m for 400 mm wide trunkings; * 120 kg / m
for trunkings 500-600 mm wide; - support span 100 mm high, support span 1.5 m: * 37 kg / m for trunkings 100 mm wide; * 53 kg / m for 150 mm wide trunkings; * 73 kg / m for 200 mm wide trunkings; * 104 kg / m for trunkings
300-400 mm wide; * 125 kg / m for trunkings 500-600 mm wide. Electrical properties: - electrical continuity guaranteed by electrical resistance (at 12V AC max 50Hz, 25A): 0.005 ohms per meter and <= 0.05 ohms
in accordance with connection. Manufacturing characteristics: - cable tray made of welded steel wires, hot-dip galvanized after processing, previously degreased and cleaned, and finally coated (certain types if necessary)
with epoxy and polyester resin; - safety edge without parts having sharp corners; - minimum mass of zinc layer: 330 g / m2 +/- 10%; - average density of zinc layer: 50 micron +/- 10%. - cover
(if necessary) made of steel with the same treatment and design characteristics of the base, with closing by a latch or by means of hooks that cannot be lost. Reaction to fire: self-extinguishing coating (if necessary)
Wire mesh cable tray made of galvanized steel, size 400x105mm
| LV SUBSTATION - MV / LV CABLE TRAYS |  | 90
| Total amount |  | 90
B50.A20.A8 |  | m
FLEXIBLE HOSE MADE OF HIGH DENSITY POLYETHYLENE FOR UNDERGROUND INSTALLATION In accordance with standards: CEI 23-39, 23-46 and subsequent amendments. Classification: not less than 3441. Crush resistance:> =
450N. Impact resistance: >= 6J.Electrical insulation resistance:> = 100MΩ. Electrical firmness:> = 20kV / mm. Resistance to chemical agents and the action of microorganisms. Manufacturing characteristics: - high density polyethylene hose
(PEHD), with double wall, smooth inside and ribbed outside; - coupling for connecting several elements. Degree of system protection: min.IP4X
PEHD flexible hose Thk=160mm
| LV SUBSTATION - MV/LV TRUNKINGS |  | 80
| Total amount |  | 80
TOTAL INSTALLATION HOSES
03 -SWITCHBOARDS
D10.A22.A1 |  | n
MEDIUM VOLTAGE SWITCHBOARD In accordance with standards: CEI 17-6 and subsequent amendments. Manufacturing characteristics: - modular structure consisting of plates of pressed steel sheet to a thickness of not less than 20/10,
coated in the furnace with epoxy powder before the process of cleaning, degreasing and phosphating; joints between different elements by means of nickel-plated screws and not by welding; - floor fixing frame and / or for leveling of
profiled welded steel panels, twice coated with base coat and one black paint, with adjustable lugs and cut stone base and with holes to allow fixing to the floor by means of wedges and glue (if required)
- upper plate for closing the foldable busbar unit on the outside and fastened with nickel-plated screws; - the front door of the unit with the apparatus are flanged and coated, can be closed with a special standardised key, and opened
only in the absence of voltage by means of circuit breakers; - rear and side doors flanged and fastened with nickel-plated screws,foldable only from the inside; - the upper unit (busbar) must be
separated from the apparatus unit by means of a disconnector and circuit braeaker insulated in SF6 so as to guarantee a minimum degree of protection IP20 of the open door and live busbar, and safe access to the unit with
apparatus; - unit with auxiliary instruments in the position above the busbar unit, accessible from the front switchboard via hinged doors, which are closed with a special standardised key; - upper and lower closure of the switchboard with appropriate
ventilation hole, gas discharge and cable entry; - mechanical obstacles and blockages aimed at guaranteeing at least that: *circuit breaker's or disconnector's contacts closing is possible only with
earthing disconnector open and access door closed; *earthing circuit breaker's contacts closing is only possible with circuit breaker or disconnector's contacts open; *the unit entrance door open is only possible with earthing disconnector closed;
* circuit breaker and disconnector are blocked in the open position of the open door; - welded and coated steel conductors, for installation at auxiliary cables between the front and rear units of the
switchboard; pipes and clamps for power cables and their terminations; - earthing busbar, made of copper, part of at least 250 mm2, installed along the entire length of the switchboard;
disconnector earthing obtained by means of a sliding clamp on a suitable copper conductor, in a part of at least 250 mm2; flexible joints coated with tinned copper (16 mm2 at least), with crimp-on terminals, elastic washers and earthing screws
hinged door; - power busbars, rectangular in section with rounded edges or tubular type, completely insulated in the air or in the air and epoxy resin (thickness at least 2,5 mm) so as to provide increased dielectric and mechanical
characteristics, mounted on appropriate insulators, with the required cable termination and other accessories; - auxiliary cable terminations for voltmeter and ammeter circuits, respectively disconnecting and short-circuiting, connected in appropriate
complexes protected by transparent resin; auxiliary heat-fixing resin cable terminations, mounted within hoses and with upper jumpers; all cable terminations must be accessible to the switchboards in operation, and terminals
must be individually designated with numbers and no more than one conductor may be connected to them; possible auxiliary cable terminations, useful in case of central installation control, detachable individually and with crimp-on terminal for portable instrument
the following "clear" contacts must be provided to the cable termination (1NA + 1NC for each of the listed statuses): * circuit breaker status (closed-open-disconnected); coil mechanism status (full-empty)
* status of earthing circuit breaker (open-closed); * remote repeater (hole-closing); - cabling of auxiliary circuits with cables that do not spread fire; -anti-condensation resistors, with thermostat,
which are supplied by an alternating current circuit from the switchboard of auxiliary services and with the partition at the input of the switchboard; - synoptic diagram on the front part of the switchboard with: graphic symbols of busbars, cable terminations, ammeter transformers (AT),
TV and capacitive connections; - light signaling devices relating to the status of the circuit-breaker,earthing circuit breaker's contacts closing, presence of phase voltage; - devices with power circuit breaker control
and mechanical control of the earthing cicuit beaker; light signaling devices for regulating non-compliance with predetermined or prohibited; all signal lamps will be of the multi led type, with characteristics
described in a separate chapter of this elaborate; - nameplates on the internal and external parts of the switchboard (including cable termination, fuses, etc.); plates with data on the ratios of AT, TV, auxiliary voltages present in
each unit with their function. All nameplates must still be approved by the company. Degree of protection against accidental contacts: - IP3X on external plates; - IP2X on internal plates. Wiring diagram with one wire,
characteristics and calibration of equipment, auxiliary equipment, instruments, etc. as well as the typologies of the construction are indicated in the graphic tables, given in the appendix.
MV BLOCK
| MV/LV SUBSTATION - DISTRIBUTION CABINETS AND SWITCHBOARDS |  | 1
| Total amount |  | 1
D20.A20.A1 |  | lump sum
LOW VOLTAGE SWITCHBOARD In accordance with standards: CEI 17-13 / 1 and subsequent amendments. Rated operating voltage: up to 690V ac. Rated insulation voltage: up to 1000V ac. Rated impulse withstand voltage of at least 8 kV.
Manufacturing characteristics: - supporting modular structure consisting of a metal frame made of profiled steel or pressed sheet metal parts of at least 20/10, with slots to enable fixing the plates,
folds, pipes, profiled brackets for fixing the equipment; - fixing frame for floor and / or leveling of welded profiled steel plates, coated twice with base coat and finally
with black paint, with adjustable lugs and a cut stone base, with holes that allow fixing to the floor with wedges and glue (if necessary); - coating the entire structure in the furnace with epoxy powder that solidifies in the heat before
the process of degreasing, cleaning, phosphating, drying sheet metal; flanged sheet metal cover plates, with hinged hole at the front and rear (front with the key, rear with tool), coated
and with flexible earthing; structure with previously separated cells at the front and rear for circuit breakers and separate units for auxiliary equipment, for the busbar zone and for
power cables (pursuant to paragraph 4 of CEI 17-13 / 1 Art.7.7); - base plates, planks and the door drilled for the installation of the equipment without additional making of holes and adaptations; natural system
of ventilation of the switchboard with appropriate holes at the front and routes along the units; - copper busbars with rounded edges installed on insulating busbar brackets, which can withstand electrodynamic
stimuli caused by a short circuit; - lighting of auxiliary units with fluorescent lamps; - no. 1 terminal 2x10 / 16A + T, 230V in each auxiliary unit; auxiliary heat-resistant resin cable termination, mounted on
hoses and with upper jumpers; - auxiliary cable termination for voltmeter and ammeter circuits, respectively, disconnecting and short-circuiting, connected in adequate complexes protected by transparent resin; - eventual
auxiliary cable termination, usable in the case of central control of installations, detachable individually and with a crimp-on terminal for a portable instrument; multi led signal lamps, circuit breakers and
control equipment of auxiliary circuits with the characteristics described in a special chapter of this elaborate; - degree of external protection: as indicated in the graphic tables, including the base; - degree of internal protection of
open front and rear doors (including auxiliary equipment units) IP20; the degree of protection IP20 must also be maintained on the fixed contacts of removable and disconnecting circuit breakers
with the removed circuit breaker. Wiring diagram with one wire, characteristics and calibration of the equipment, auxiliary devices, instruments, etc. are marked in graphic tables.
"The switchboard consists of the following structures and equipment: - metal structure with 4 cabinets and 4 units for cables of overall dimensions (HxBxP): 2100x4900x1000, degree of protection IP40;; - No.2 main manual circuit breaker in box 4x630A with auxiliary contact and dialogue unit; - No.1 main manual circuit breaker in box 4x400A with auxiliary contact; - No.1 adjustable differential relay with toroid d = 0.3-10A; - No.1 surge arrester type 1 + 2 with auxiliary contact; - No.1 measuring instrument multimeter; - No.2 three-phase contactor; - No.1 voltmeter measuring group 500V, class 1.5; - No.1 modular base of 4x400A fuse brackets with fuses and auxiliary contact; - No.2 modular base of 4x32A fuse brackets filled with fuses;
"- n ° 3 automatic thermomagnetic circuit breaker in box 4x250A, with auxiliary contacts and LED status indicators; - n ° 23 automatic thermomagnetic circuit breaker in box 4x160A, with auxiliary contacts and LED status indicators; - n ° 5 motorisation for automatic thermomagnetic circuit breaker in box 4x160A; - n ° 5 circuit breaker for automatic thermomagnetic circuit breaker in box 4x160A; - signal lamps; - manual circuit breaker in box 4x630A; - motorisation for manual circuit breaker in box 4x630A; - busbar for earthing inside the switchboard "
M_LV_SB - The main LV switchboard
| LV - SUBSTATION - DISTRIBUTION CABINETS AND SWITCHBOARDS |  | 1
| Total amount |  | 1
D20.A20.A10 |  | lump sum
LOW VOLTAGE SWITCHBOARD In accordance with standards: CEI 17-13 / 1 and subsequent amendments. Rated operating voltage: up to 690V ac. Rated insulation voltage: up to 1000V ac. Rated impulse withstand voltage of at least 8 kV.
Manufacturing characteristics: - supporting modular structure consisting of a metal frame made of profiled steel or pressed sheet metal parts of at least 20/10, with slots to enable fixing the plates,
folds, pipes, profiled brackets for fixing the equipment; - fixing frame for floor and / or leveling of welded profiled steel plates, coated twice with base coat and finally
with black paint, with adjustable lugs and a cut stone base, with holes that allow fixing to the floor with wedges and glue (if necessary); - coating the entire structure in the furnace with epoxy powder that solidifies in the heat before
the process of degreasing, cleaning, phosphating, drying sheet metal; flanged sheet metal cover plates, with hinged hole at the front and rear (front with the key, rear with tool), coated
and with flexible earthing; structure with previously separated cells at the front and rear for circuit breakers and separate units for auxiliary equipment, for the busbar zone and for
power cables (pursuant to paragraph 4 of CEI 17-13 / 1 Art.7.7); - base plates, planks and the door drilled for the installation of the equipment without additional making of holes and adaptations; natural system
of ventilation of the switchboard with appropriate holes at the front and routes along the units; - copper busbars with rounded edges installed on insulating busbar brackets, which can withstand electrodynamic
stimuli caused by a short circuit; - lighting of auxiliary units with fluorescent lamps; - no. 1 terminal 2x10 / 16A + T, 230V in each auxiliary unit; auxiliary heat-resistant resin cable termination, mounted on
hoses and with upper jumpers; - auxiliary cable termination for voltmeter and ammeter circuits, respectively, disconnecting and short-circuiting, connected in adequate complexes protected by transparent resin; - eventual
auxiliary cable termination, usable in the case of central control of installations, detachable individually and with a crimp-on terminal for a portable instrument; multi led signal lamps, circuit breakers and
control equipment of auxiliary circuits with the characteristics described in a special chapter of this elaborate; - degree of external protection: as indicated in the graphic tables, including the base; - degree of internal protection of
open front and rear doors (including auxiliary equipment units) IP20; the degree of protection IP20 must also be maintained on the fixed contacts of removable and disconnecting circuit breakers
with the removed circuit breaker. Wiring diagram with one wire, characteristics and calibration of the equipment, auxiliary devices, instruments, etc. are marked in graphic tables.
The switchboard consists of the following structures and equipment: - metal structure with one cabinet and central unit for cables of overall dimensions (HxBxP): 2100x1100x1000, degree of protection IP40; - n ° 1 open-type thermomagnetic circuit breaker 4x1600A with auxiliary contacts and signal lamps;
- n ° 1 automatic thermomagnetic circuit breaker in box 4x630A, with auxiliary contacts and signal lamps; - n ° 2 automatic thermomagnetic circuit breaker in box 4x250A, with auxiliary contacts and signal lamps; - busbar for earthing inside the switchboard. "
LV_SB
| MV/LV SUBSTATION - DISTRIBUTION CABINETS AND SWITCHBOARDS |  | 1
| Total amount |  | 1
D20.A20.A20 |  | paušal
LOW VOLTAGE SWITCHBOARD In accordance with standards: CEI 17-13 / 1 and subsequent amendments. Rated operating voltage: up to 690V ac. Rated insulation voltage: up to 1000V ac. Rated impulse withstand voltage of at least 8 kV.
Manufacturing characteristics: - supporting modular structure consisting of a metal frame made of profiled steel or pressed sheet metal parts of at least 20/10, with slots to enable fixing the plates,
folds, pipes, profiled brackets for fixing the equipment; - fixing frame for floor and / or leveling of welded profiled steel plates, coated twice with base coat and finally
with black paint, with adjustable lugs and a cut stone base, with holes that allow fixing to the floor with wedges and glue (if necessary); - coating the entire structure in the furnace with epoxy powder that solidifies in the heat before
the process of degreasing, cleaning, phosphating, drying sheet metal; flanged sheet metal cover plates, with hinged hole at the front and rear (front with the key, rear with tool), coated
and with flexible earthing; structure with previously separated cells at the front and rear for circuit breakers and separate units for auxiliary equipment, for the busbar zone and for
power cables (pursuant to paragraph 4 of CEI 17-13 / 1 Art.7.7); - base plates, planks and the door drilled for the installation of the equipment without additional making of holes and adaptations; natural system
of ventilation of the switchboard with appropriate holes at the front and routes along the units; - copper busbars with rounded edges installed on insulating busbar brackets, which can withstand electrodynamic
stimuli caused by a short circuit; - lighting of auxiliary units with fluorescent lamps; - no. 1 terminal 2x10 / 16A + T, 230V in each auxiliary unit; auxiliary heat-resistant resin cable termination, mounted on
hoses and with upper jumpers; - auxiliary cable terminations for voltmeter and ammeter circuits, respectively, disconnecting and short-circuiting, connected in adequate complexes protected by transparent resin; - eventual
auxiliary cable terminations, usable in the case of central control of installations, detachable individually and with a crimp-on terminal for a portable instrument; multi led signal lamps, circuit breakers and
control equipment of auxiliary circuits with the characteristics described in a special chapter of this elaborate; - degree of external protection: as indicated in the graphic tables, including the base; - degree of internal protection of
open front and rear doors (including auxiliary equipment units) IP20; the degree of protection IP20 must also be maintained on the fixed contacts of removable and disconnecting circuit breakers
with the removed circuit breaker. Wiring diagram with one wire, characteristics and calibration of the equipment, auxiliary devices, instruments, etc. are marked in graphic tables.
The switchboard consists of the following structures and equipment: - metal structure with one cabinet of overall dimensions (HxBxP): 1700x750x600, degree of protection IP40; - n ° 1 automatic thermomagnetic circuit breaker in a box with adjustable differential relay 4x630A with circuit breaker, auxiliary contacts and signal lamps;
- n ° 3 automatic self-magnetic circuit breaker in box 4x160A, with auxiliary contacts and LED status indicators; - busbar for earthing inside the switchboard.
M_CB
| LV SUBSTATION - DISTRIBUTION CABINETS AND SWITCHBOARDS |  | 1
| Total amount |  | 1
D20.A20.A3 |  | lump sum
LOW VOLTAGE SWITCHBOARD In accordance with standards: CEI 17-13 / 1 and subsequent amendments. Rated operating voltage: up to 690V ac. Rated insulation voltage: up to 1000V ac. Rated impulse withstand voltage of at least 8 kV.
Manufacturing characteristics: - supporting modular structure consisting of a metal frame made of profiled steel or pressed sheet metal parts of at least 20/10, with slots to enable fixing the plates,
folds, pipes, profiled brackets for fixing the equipment; - fixing frame for floor and / or leveling of welded profiled steel plates, coated twice with base coat and finally
with black paint, with adjustable lugs and a cut stone base, with holes that allow fixing to the floor with wedges and glue (if necessary); - coating the entire structure in the furnace with epoxy powder that solidifies in the heat before
the process of degreasing, cleaning, phosphating, drying sheet metal; flanged sheet metal cover plates, with hinged hole at the front and rear (front with the key, rear with tool), coated
and with flexible earthing; structure with previously separated cells at the front and rear for circuit breakers and separate units for auxiliary equipment, for the busbar zone and for
power cables (pursuant to paragraph 4 of CEI 17-13 / 1 Art.7.7); - base plates, planks and the door drilled for the installation of the equipment without additional making of holes and adaptations; natural system
of ventilation of the switchboard with appropriate holes at the front and routes along the units; - copper busbars with rounded edges installed on insulating busbar brackets, which can withstand electrodynamic
stimuli caused by a short circuit; - lighting of auxiliary units with fluorescent lamps; - no. 1 terminal 2x10 / 16A + T, 230V in each auxiliary unit; auxiliary heat-resistant resin cable termination, mounted on
hoses and with upper jumpers; - auxiliary cable terminations for voltmeter and ammeter circuits, respectively, disconnecting and short-circuiting, connected in adequate complexes protected by transparent resin; - eventual
auxiliary cable terminations, usable in the case of central control of installations, detachable individually and with a crimp-on terminal for a portable instrument; multi led signal lamps, circuit breakers and
control equipment of auxiliary circuits with the characteristics described in a special chapter of this elaborate; - degree of external protection: as indicated in the graphic tables, including the base; - degree of internal protection of
open front and rear doors (including auxiliary equipment units) IP20; the degree of protection IP20 must also be maintained on the fixed contacts of removable and disconnecting circuit breakers
with the removed circuit breaker. Wiring diagram with one wire, characteristics and calibration of the equipment, auxiliary devices, instruments, etc. are marked in graphic tables.
The switchboard consists of the following structures and equipment: - metal structure with 2 cabinets and 2 units for cables of overall dimensions (HxBxP): 2200x2200x350, degree of protection IP40; - n ° 1 manual main circuit breaker in box 4x250A with auxiliary contacts and signal lamps; - n ° 2 measuring instrument multimeter; - n ° 1 voltmeter measuring group 500V, class 1.5; - n ° 2 modular base of 4x32A fuse bracketr with fuses; - n ° 1 modular fuse bracket base 2x20A with fuses and auxiliary contact;
n ° 2 automatic thermomagnetic circuit breaker in box 4x250A, with circuit breaker, auxiliary contacts and signal lamps; - n ° 10 automatic thermomagnetic circuit breaker in box4x160A, with auxiliary contacts and LED status indicators; - busbar for earthing inside the switchboard
M_UPS_SB - Main UPS switchboard
| LV SUBSTATION - DISTRIBUTION CABINETS AND SWITCHBOARDS |  | 1
| Total amount |  | 1
D20.A20.A30 |  | lump sum
LOW VOLTAGE SWITCHBOARD In accordance with standards: CEI 17-13 / 1 and subsequent amendments. Rated operating voltage: up to 690V ac. Rated insulation voltage: up to 1000V ac. Rated impulse withstand voltage of at least 8 kV.
Manufacturing characteristics: - supporting modular structure consisting of a metal frame made of profiled steel or pressed sheet metal parts of at least 20/10, with slots to enable fixing the plates,
folds, pipes, profiled brackets for fixing the equipment; - fixing frame for floor and / or leveling of welded profiled steel plates, coated twice with base coat and finally
with black paint, with adjustable lugs and a cut stone base, with holes that allow fixing to the floor with wedges and glue (if necessary); - coating the entire structure in the furnace with epoxy powder that solidifies in the heat before
the process of degreasing, cleaning, phosphating, drying sheet metal; flanged sheet metal cover plates, with hinged hole at the front and rear (front with the key, rear with tool), coated
and with flexible earthing; structure with previously separated cells at the front and rear for circuit breakers and separate units for auxiliary equipment, for the busbar zone and for
power cables (pursuant to paragraph 4 of CEI 17-13 / 1 Art.7.7); - base plates, planks and the door drilled for the installation of the equipment without additional making of holes and adaptations; natural system
of ventilation of the switchboard with appropriate holes at the front and routes along the units; - copper busbars with rounded edges installed on insulating busbar brackets, which can withstand electrodynamic
stimuli caused by a short circuit; - lighting of auxiliary units with fluorescent lamps; - no. 1 terminal 2x10 / 16A + T, 230V in each auxiliary unit; auxiliary heat-resistant resin cable termination, mounted on
hoses and with upper jumpers; - auxiliary cable terminations for voltmeter and ammeter circuits, respectively, disconnecting and short-circuiting, connected in adequate complexes protected by transparent resin; - eventual
auxiliary cable terminations, usable in the case of central control of installations, detachable individually and with a crimp-on terminal for a portable instrument; multi led signal lamps, circuit breakers and
control equipment of auxiliary circuits with the characteristicsdescribed in a special chapter of this elaborate; - degree of external protection: as indicated in the graphic tables, including the base; - degree of internal protection of
open front and rear doors (including auxiliary equipment units) IP20; the degree of protection IP20 must also be maintained on the fixed contacts of removable and disconnecting circuit breakers
with the removed circuit breaker. Wiring diagram with one wire, characteristics and calibration of the equipment, auxiliary devices, instruments, etc. are marked in graphic tables.
The switchboard consists of the following structures and equipment: - wall metal structure of overall dimensions (HxBxP): 900x750x200, degree of protection IP40; - n ° 1 automatic thermomagnetic circuit breaker with adjustable differential relay in box 4x160A with circuit breaker, auxiliary contacts and signal lamps;
- n°1 modular base of fuse bracket 2x20A with fuses; - busbar for earthing inside the switchboard.
U_CB
| LV SUBSTATION - DISTRIBUTION CABINETS AND SWITCHBOARDS |  | 1
| Total amount |  | 1
D20.A20.A4 |  | lump sum
LOW VOLTAGE SWITCHBOARD In accordance with standards: CEI 17-13 / 1 and subsequent amendments. Rated operating voltage: up to 690V ac. Rated insulation voltage: up to 1000V ac. Rated impulse withstand voltage of at least 8 kV.
Manufacturing characteristics: - supporting modular structure consisting of a metal frame made of profiled steel or pressed sheet metal parts of at least 20/10, with slots to enable fixing the plates,
folds, pipes, profiled brackets for fixing the equipment; - fixing frame for floor and / or leveling of welded profiled steel plates, coated twice with base coat and finally
with black paint, with adjustable lugs and a cut stone base, with holes that allow fixing to the floor with wedges and glue (if necessary); - coating the entire structure in the furnace with epoxy powder that solidifies in the heat before
the process of degreasing, cleaning, phosphating, drying sheet metal; flanged sheet metal cover plates, with hinged hole at the front and rear (front with the key, rear with tool), coated
and with flexible earthing; structure with previously separated cells at the front and rear for circuit breakers and separate units for auxiliary equipment, for the busbar zone and for
power cables (pursuant to paragraph 4 of CEI 17-13 / 1 Art.7.7); - base plates, planks and the door drilled for the installation of the equipment without additional making of holes and adaptations; natural system
of ventilation of the switchboard with appropriate holes at the front and routes along the units; - copper busbars with rounded edges installed on insulating busbar brackets, which can withstand electrodynamic
stimuli caused by a short circuit; - lighting of auxiliary units with fluorescent lamps; - no. 1 terminal 2x10 / 16A + T, 230V in each auxiliary unit; auxiliary heat-resistant resin cable termination, mounted on
hoses and with upper jumpers; - auxiliary cable terminations for voltmeter and ammeter circuits, respectively, disconnecting and short-circuiting, connected in adequate complexes protected by transparent resin; - eventual
auxiliary cable terminations, usable in the case of central control of installations, detachable individually and with a crimp-on terminal for a portable instrument; multi led signal lamps, circuit breakers and
control equipment of auxiliary circuits with the characteristicsdescribed in a special chapter of this elaborate; - degree of external protection: as indicated in the graphic tables, including the base; - degree of internal protection of
open front and rear doors (including auxiliary equipment units) IP20; the degree of protection IP20 must also be maintained on the fixed contacts of removable and disconnecting circuit breakers
with the removed circuit breaker. Wiring diagram with one wire, characteristics and calibration of the equipment, auxiliary devices, instruments, etc. are marked in graphic tables.
The switchboard consists of the following structures and equipment: - metal structure with 2 cabinets and 1 central unit for cables of overall dimensions (HxBxP): 2000x1850x650, degree of protection IP40; - n ° 1 automatic thermomagnetic circuit breaker in box 4x630A with circuit breaker, auxiliary contacts and signal lamps; - n ° 1 measuring group of power, current, voltage, time, frequency and relay; - n ° 4 modular base of 4x32A fuse bracket with fuses; - n ° 1 modular fuse bracket base 2x20A with fuses and auxiliary contact
- n°1 automatic thermomagnetic circuit breaker in box 4x400A, con bobina di sgancio; - n ° 1 automatic thermomagnetic circuit breaker in box 4x160A; - n ° 1 main manual modular circuit breaker 4x63A, with auxiliary contact e spie di segnalazione; - n ° 3 automatic thermomagnetic differential modular circuit breaker 2x16A, Id = 30mA with auxiliary contact; - n ° 1 automatic thermomagnetic differential modular circuit breaker 2x10A, Id = 30mA with auxiliary contact; - n ° 1 automatic modular circuit breaker with thermal 3x9A with auxiliary contact; - n ° 1 automatic differential modular circuit breaker 4x25A, Id = 300mA with auxiliary contact; - n ° 1 modular power contactor 3x20A AC3 with auxiliary contact and lamps; - n ° 1 transformer 230 / 24V power 400VA; - n ° 1 modular selector with 3 positions; - busbar for earthing inside the switchboard
EG_SB - Switchboard with emergency generator
| LV SUBSTATION - DISTRIBUTION CABINETS AND SWITCHBOARDS |  | 1
| Total amount |  | 1
D20.A20.A40 |  | lump sum
LOW VOLTAGE SWITCHBOARD In accordance with standards: CEI 17-13 / 1 and subsequent amendments. Rated operating voltage: up to 690V ac. Rated insulation voltage: up to 1000V ac. Rated impulse withstand voltage of at least 8 kV.
Manufacturing characteristics: - supporting modular structure consisting of a metal frame made of profiled steel or pressed sheet metal parts of at least 20/10, with slots to enable fixing the plates,
folds, pipes, profiled brackets for fixing the equipment; - fixing frame for floor and / or leveling of welded profiled steel plates, coated twice with base coat and finally
with black paint, with adjustable lugs and a cut stone base, with holes that allow fixing to the floor with wedges and glue (if necessary); - coating the entire structure in the furnace with epoxy powder that solidifies in the heat before
the process of degreasing, cleaning, phosphating, drying sheet metal; flanged sheet metal cover plates, with hinged hole at the front and rear (front with the key, rear with tool), coated
and with flexible earthing; structure with previously separated cells at the front and rear for circuit breakers and separate units for auxiliary equipment, for the busbar zone and for
power cables (pursuant to paragraph 4 of CEI 17-13 / 1 Art.7.7); - base plates, planks and the door drilled for the installation of the equipment without additional making of holes and adaptations; natural system
of ventilation of the switchboard with appropriate holes at the front and routes along the units; - copper busbars with rounded edges installed on insulating busbar brackets, which can withstand electrodynamic
stimuli caused by a short circuit; - lighting of auxiliary units with fluorescent lamps; - no. 1 terminal 2x10 / 16A + T, 230V in each auxiliary unit; auxiliary heat-resistant resin cable termination, mounted on
hoses and with upper jumpers; - auxiliary cable terminations for voltmeter and ammeter circuits, respectively, disconnecting and short-circuiting, connected in adequate complexes protected by transparent resin; - eventual
auxiliary cable terminations, usable in the case of central control of installations, detachable individually and with a crimp-on terminal for a portable instrument; multi led signal lamps, circuit breakers and
control equipment of auxiliary circuits with the characteristicsdescribed in a special chapter of this elaborate; - degree of external protection: as indicated in the graphic tables, including the base; - degree of internal protection of
open front and rear doors (including auxiliary equipment units) IP20; the degree of protection IP20 must also be maintained on the fixed contacts of removable and disconnecting circuit breakers
with the removed circuit breaker. Wiring diagram with one wire, characteristics and calibration of the equipment, auxiliary devices, instruments, etc. are marked in graphic tables.
The switchboard consists of the following structures and equipment: - metal structure a parete of overall dimensions (HxBxP): 900x750x200, degree of protection IP40; - No.1 automatic thermomagnetic circuit breaker with adjustable differential relay in box 4x160A with circuit breaker, auxiliary contacts and signal lamps;
- No.1 modular base of 2x20A fusebracket with fuses; - busbar for earthing inside the switchboard.
H_CB
| LV SUBSTATION - DISTRIBUTION CABINETS AND SWITCHBOARDS |  | 1
| Total amount |  | 1
D20.A20.A5 |  | lump sum
LOW VOLTAGE SWITCHBOARD In accordance with standards: CEI 17-13 / 1 and subsequent amendments. Rated operating voltage: up to 690V ac. Rated insulation voltage: up to 1000V ac. Rated impulse withstand voltage of at least 8 kV.
Manufacturing characteristics: - supporting modular structure consisting of a metal frame made of profiled steel or pressed sheet metal parts of at least 20/10, with slots to enable fixing the plates,
folds, pipes, profiled brackets for fixing the equipment; - fixing frame for floor and / or leveling of welded profiled steel plates, coated twice with base coat and finally
with black paint, with adjustable lugs and a cut stone base, with holes that allow fixing to the floor with wedges and glue (if necessary); - coating the entire structure in the furnace with epoxy powder that solidifies in the heat before
the process of degreasing, cleaning, phosphating, drying sheet metal; flanged sheet metal cover plates, with hinged hole at the front and rear (front with the key, rear with tool), coated
and with flexible earthing; structure with previously separated cells at the front and rear for circuit breakers and separate units for auxiliary equipment, for the busbar zone and for
power cables (pursuant to paragraph 4 of CEI 17-13 / 1 Art.7.7); - base plates, planks and the door drilled for the installation of the equipment without additional making of holes and adaptations; natural system
of ventilation of the switchboard with appropriate holes at the front and routes along the units; - copper busbars with rounded edges installed on insulating busbar brackets, which can withstand electrodynamic
stimuli caused by a short circuit; - lighting of auxiliary units with fluorescent lamps; - no. 1 terminal 2x10 / 16A + T, 230V in each auxiliary unit; auxiliary heat-resistant resin cable termination, mounted on
hoses and with upper jumpers; - auxiliary cable terminations for voltmeter and ammeter circuits, respectively, disconnecting and short-circuiting, connected in adequate complexes protected by transparent resin; - eventual
auxiliary cable terminations, usable in the case of central control of installations, detachable individually and with a crimp-on terminal for a portable instrument; multi led signal lamps, circuit breakers and
control equipment of auxiliary circuits with the characteristicsdescribed in a special chapter of this elaborate; - degree of external protection: as indicated in the graphic tables, including the base; - degree of internal protection of
open front and rear doors (including auxiliary equipment units) IP20; the degree of protection IP20 must also be maintained on the fixed contacts of removable and disconnecting circuit breakers
with the removed circuit breaker. Wiring diagram with one wire, characteristics and calibration of the equipment, auxiliary devices, instruments, etc. are marked in graphic tables.
The switchboard consists of the following structures and equipment: -metal structure with 1 cabinet and 1 unit for cables of overall dimensions (HxBxP): 2100x1300x350, degree of protection IP40; - No.1 manual main circuit breaker in box 4x160A with auxiliary contacts and signal lamps; - No.1 measuring instrument multimeter; - No.1 modular base of 4x32A fuse bracket with fuses; - No.1 modular base of fuse bracket 2x20A with fuses and auxiliary contact;
-No.1 automatic thermomagnetic circuit breaker in box 4x160A, with circuit breaker, auxiliary contacts and signal lamps; - No.1 main manual modular circuit breaker 4x63A, with auxiliary contact; - No.8 automatic thermomagnetic differential modular circuit breaker 2x10A, Id = 300mA with auxiliary contact; - No.2 automatic thermomagnetic modular circuit breaker with change curveB 4x32A, with auxiliary contacts; - No.6 automatic thermomagnetic modular circuit breaker with change curveB 2x32A, with auxiliary contacts; - No.7 modular power contactor 3x9A AC3 with auxiliary contact; - busbar for earthing inside the switchboard .
M_EL_SB - Emergency light switchboard
| LV SUBSTATION - DISTRIBUTION CABINETS AND SWITCHBOARDS |  | 1
| Total amount |  | 1
D40.A10.A3 |  | lump sum
METAL DISTRIBUTION BOX In accordance with standards: CEI 17-13 / 1 (95) and subsequent amendments. Manufacturing characteristics: - load-bearing modular structure consisting of metal frames from parts
made of profiled steel or pressed sheet metal parts of at least 20/10, with slots to enable fixing of plates,folds, trunkings, profiled brackets for fixing the equipment; - fixing frame
for the floor and / or for leveling the profiled welded steel panels, coated twice with the base and then with the black paint, with adjustable feet and a cut stone base, drilled to enable fixing to the floor
using dowel screws and glue (if necessary); -lateral and rear cover plates of flanged and coated sheet metal with flexible earthing; - front plates for various flanged and coated sheet metal partitions,
which can be open with a tool or a special key and with flexible earthing; perforated plates with seals and lids for holes to close unused space; - front door made of edging and
coated sheet metal, opaque or transparent, made of plastic (according to graphic tables), which can be open fold, with a handle, a lock for a special key and flexible earthing; - copper grids
designated in accordance with CEI-UNEL standards (some observations must be pointed out in order to avoid oxidation at the points of joints); degree of external protection: as specified in the graphical tables
including base; - degree of protection on front open plates: not less than IP20, provided with adequate round terminal covers, headphones, screens, protections, etc. for all appliances and live parts. Typology of performance
(inside the wall, protruding, on the floor or on the wall), wire diagram with one wire, characteristics and calibration of the equipment, auxiliary eqipment, instruments, etc., are marked in the graphic tables. The price does not include only
The price does not include only special devices such as electromedical devices, devices for busbar control systems, control panels for light flux control, control panels from the central control system, etc. which will be calculated separately
The switchboard consists of the following structures and equipment: - metal structure sa due armadi e un vano cavi centrale of overall dimensions (HxBxP): 2100x2250x400, degree of protection IP40; - n°3 manual main circuit breaker in box 4x160A with auxiliary contacts and signal lamps; - n ° 1 circuit breaker for manual main circuit breaker in box 4x160A; - n ° 1 adjustable differential relay with toroid Id = 0.3-10A; - n ° 1 voltage arrester type 2 with auxiliary contact; - n ° 1 measuring instrument multimeter; - n ° 1 voltmeter measuring group 500V, class 1.5; - n ° 1 ammeter measuring group 50A, class 1.5;
- n°1 modular base of 4x125A fuse bracket with fuses with auxiliary contact; - n ° 1 modular base of 4x80A fuse bracket with fuses with auxiliary contact; - n ° 2 modular base of 4x32A fuse bracket with fuses; - n ° 2 modular base of fuse bracket 2x20A with fuses and auxiliary contact; - n ° 1 main manual modular circuit breaker 4x80A with auxiliary contacts and signal lamps; - n ° 1 main manual modular circuit breaker 2x32A with auxiliary contacts and signal lamps; - n ° 1 modular circuit breaker 4x80A with auxiliary contacts and signal lamps;
- n°1 automatic thermomagnetic differential modular circuit breaker 4x63A, Id = 1A selettivo, Icn> 12kA, with auxiliary contact; - n ° 1 automatic thermomagnetic differential modular circuit breaker 4x25A, Id = 1A selettivo Icn> 12kA, with auxiliary contact; - n ° 2 automatic thermomagnetic differential modular circuit breaker 4x10A, Id = 300mA, Icn> 12kA, with auxiliary contact; - n ° 17 automatic thermomagnetic differential modular circuit breaker 2x10A, Id = 300mA, Icn> 12kA, with auxiliary contact; - n ° 1 modular power contactor4x12A AC3 with auxiliary contact; - n ° 14 modular power contactor3x12A AC3 with auxiliary contact;
- n°5 automatic thermomagnetic differential modular circuit breaker 2x16A change curve B, Id = 30mA, Icn> 12kA, with auxiliary contact; - n ° 1 automatic thermomagnetic differential modular circuit breaker 2x10A change curve B, Id = 30mA, Icn> 12kA, with auxiliary contact; - n ° 1 transformer 230 / 24V power 400VA; - n ° 4 automatic thermomagnetic modular circuit breaker 2x20A, Icn> 12kA, with auxiliary contact; - n ° 2 automatic thermomagnetic modular circuit breaker 2x20A, Icn> 12kA, with auxiliary contact; - busbar for earthing inside the switchboard.
DB_AS
| LV SUBSTATION - DISTRIBUTION CABINETS AND SWITCHBOARDS |  | 1
| Total amount |  | 1
TOTAL SWITCHBOARDS
DEVICES AND EQUIPMENT FOR SUBSTATION
F10.A10.A1 |  | lump sum
SIGN BOARDS, SCHEMES, AUXILIARY ACCESSORIES AND SUPPLY MAINTENANCE ACCESSORIES Procurement and installation of signaling, sign boards and schemes and auxiliary and maintenance materials. Delivery will have to include: a sign board having
the name of the facility written on it; - a sign board with the mark of the rated voltage at the entrances to the facility; - a sign board on which the ban on entering the facility by unauthorised persons is displayed; - warning of danger sign board; - sign board with instructions for firefighting,
sign boards with instructions for help; - possible warning sign boards for facilities containing batteries; - one-line diagram of large dimensions of standard colours, on a plasticised plate protected by glass with basic
data (voltage, range, breaking capacity, protection) with markings that are fully compliant with those listed on the installed sign boards; - cabinet with main single-line diagrams, functional diagrams
diagrams for installation of all substation devices, manuals and instructions for use, maintenance and replacement of substation parts and a list of all suppliers with models of individual devices;
a journal in which all regular and emergency maintenance interventions carried out in the substation itself will be registered; - AUXILIARY MATERIAL; - non-combustible fiberglass blanket in a canvass cover
stored in a suitable box fixed to the wall; - portable lamp with rechargeable batteries powered from the FM socket installed in the facility (which is separately calculated); - 2 sandbags (in facilities where there is a risk of spillage of hazardous liquids such as
gasoline, fuels, acids); -The price refers to 1 facility and includes the installation of total material and possible verification of the correctness of functioning
Sign boards, diagrams and maintenance accessories
| LV CABINET |  | 1
| total |  | 1
F10.A30.A1 |  | m
INSULATION MAT Electrical characteristics: operating voltage: 20kV - test voltage: 42kV, breakdown voltage 50kV: Manufacturing characteristics: - insulating mat made of high dielectric rubber
not less than 5 mm thick, 1000 mm high, with non-slip surface.
20kV insulation mat
| MV / LV SS - LV CABINETS |  | 4
| Total |  | 4
TOTAL DEVICES AND ACCESSORIES FOR THE SUBSTATION
07 - TRASFORMERS
G30.A10.A12 |  | n
THREE-PHASE DRY TRANSFORMER number of primary and secondary phases: 3. Number of coils 2. 50 Hz. 10 kV. Rated secondary voltage: 0.4 kV. Insulation voltage
: 12 kV (primary) and 1 kV (secondary). Primary thermal degree: F. Secondary thermal degree: F. No-load loss (Wfe) V = Vn less than 0.3%. No-load loss (Wcc) V = Vn less than 0.6%. Short circuit voltage
: 6%. No-load current (Io): 0,8%. Reference: -: E0; - climate: C1; - fire protection: F0. - Connection: - Yd 11 with neutral point earthing access
primary coil adjustment +3x2.5%, -3x2.5%
1000kVA transformer, I^ingl., II^impr., Vcc=6%, Io=0,9%
| MV/LV Substation |  | 1
| total |  | 1
TOTAL TRANSFORMERS
CORRECTION DEVICES
L20.A10.A12 |  | n
AUTOMATIC POWER FACTOR CORRECTION PANEL Compliance with standards: CEI 33-9, 33-10, 33-23 and subsequent options. Manufacturing characteristics: Sheet metal cabinet
chemically treated and coated with epoxy powder, which in separate units contains a control panel for regulation, control devices and capacitors; doors that can be opened,
lock and special key; - forced ventilation by a ventilator of appropriate range installed on the upper side of the device, with a thermostat; - (possibly) support frame made of profiled rods made of welded lacquered steel;
degree of protection: min. IP30 (with open door IP20); CONTROL PANEL - rated voltage: 400V c.a. +/- 10%. - rated frequency: 50Hz; - absorption less than 10VA; . load on output relays 6A at 250V;
a control system consisting of a comparator and a static-type power factor and / or reactive energy controller with integrated technology; CMOS series integrated circuits are mounted on fiberglass plates;
with components adequately processed before or after assembly; illuminated network presence indicator; - illuminated indicator of batteries of built-in capacitors; - illuminated indicator of inductive and capacitive resistance; - marking the power factor (cos fi) via the display or LED display;
constant regulation of power factor via control or push-button with threshold visualisation from 0.80 capacitive to 0.90 inductive; C / K regulation from 0.05 to 1; light overload indicator due to current harmonics
over 30% of those that capacitors can withstand with automatic reset upon cessation of occurrence; - light indicator and sound signaling for improper correction of power factor values <0.80 inductive> 0.80 capacitive;
light indicator of unallowable increase of temperature with switching off of capacitor batteries when exceeding the allowed temperature threshold; - insensitivity field in relation to the predetermined power factor +/- 0.05, switch-on time
with correction carried out every second and whose mean value is calculated after 30 seconds; - device for canceling interventions in the absence of line voltage; diverter for manual or automatic battery activation (MAN-AUT) 30 "
and switches to manually turn on each battery or a double push-button switch to sequentially turn the batteries on and off; - regulation of the internal temperature threshold for activating the ventilator;
regulation of the maximum value of the temperature for switching off the capacitor batteries; - 2 outputs, one of which is for remote alarm transmission for incorrect correction, and the other for ventilator control; -
voltage circuit powered via insulation transformer; rear connectors with gold-plated contacts; - protective dome for connection boards equipped with danger signs;
or insulated faston connectors; - distribution line fuses for protection of regulators on the voltage circuit and short-circuit terminals on the circuit; .- GENERATING UNITS AND CONTROL DEVICES - circuit breaker with rated capacity 1.5 times higher than the maximum required capacitive current
three-pole electromagnetic contactors with double break, suitable for switching capacitive load on and off; rated voltage 400V,
rated current about twice the required capacity; distribution line fuses to protect connectors. CAPACITORS - rated voltage around 415V + 10%; low dielectric losses (tg delta <0,5x10 exp (-3) at 75 ^ C) three-phase capacitors
connected in a provided unit with three busbars separated in a special box or otherwise protected from accidental contacts; fire-proof and explosion-proof tin container;
;fast discharge resistance of the type shown in the graphic tables - insulator made of plastic film with metallised armor of self - regenerative type, in a container with N2 (nitrogen).
three distribution line fuses of high breaking capacity and a "slow blow" type to protect each of the capacitor batteries. Capacitor battery protection fuses will be individually equipped with auxiliary contacts to be connected to
an auxiliary terminal board intended for remote signaling; in addition, cumulative signaling will be provided for each battery on the control panel; finally, the action of one fuse will have to turn off the corresponding capacitor.
100 kVAR automatic power factor correction panel
| LV SUBSTATION - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 1
| Total amount |  | 1
L20.A20.A6 |  | n
FIXED AUTOMATIC POWER FACTOR CORRECTION PANEL Compliance with standards: CEI 33-9 (94) and subsequent options. Rated voltage: about 400V +/- 10%. Rated frequency: 50Hz. Reactive power: as described in types.
Manufacturing characteristics: chemically treated metal container coated with epoxy powder, with a lock, ventilation blades for capacitors and danger warning sign boards ; dielectric type capacitors
in plastic film and metallised reinforcement, equipped with appropriate discharge resistances in a container with N2 (nitrogen) or resin, tin equipped, fire-proof and explosin -proof, with low losses <<3 .5x10 exp (-3) a 75 ^ C)
three-pole disconnector combined with fuse bracket and disconnection on the upper and lower side of the fuses themselves, breaking capacity of the disconnector> 500A and 660V (cosfi '= 0.35) and with rated current
at least 2 times larger than a capacitor battery; - "slow blow" type fuses; - signal melting lamp of one or more fuses; front rotary control and door lock; repeating the signaling of the melting
of one or more fuses by remote transmission. Degree of protection: IP 30. The unit will be installed near the devices where the correction is to be performed or in some other place that will be defined at headquarters of the supervisory authority. Procurement should also include
connections for devices that need to be corrected
15 kVAR fixed power factor correction unit
| MV/LV SUBSTATION - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 1
| Total amount |  | 1
TOTAL CORRECTION DEVICES
04 - AUXILIARY SYSTEMS AND PROTECTION SYSTEMS
L30.A20.A2 |  | n
RECTIFIER WITH TWO BRANCHES OF CHOPPER TYPE (BATTERY BRANCH) AND SCR RECTIFIER (BRANCH OF DEVICE) FOR POWER SUPPLY OF AUXILIARY ELEMENTS IN THE SUBSTATION Compliance with standards: CEI 22-9, 17-13 / 1, 21-24, 21-48
Electrical characteristics: uninterruptible power supply of the installation branch, as indicated. Uninterruptible power supply of battery branches: as indicated in types. Input: - rated voltage: about 400V +/- 15%; rated frequency
50 +/- 5% Hz Batteries: hermetically sealed, lead-acid battery, high efficiency, maintenance-free; voltage: 2.27 V / el; intervention time (in case of network failure) 0.5 seconds; Output: voltage: as described
voltage stability (for variations +/- 15% of the mains voltage and 10-100% of rated resistance: 1% - ripple <1% Effect:> 80%. Manufacturing characteristics: Cabinet: unique structure divided into two cells
(cell for electronic part, auxiliary elements, terminal boards and cell for batteries) divided by a metal wall firmly built into the structure of the panel, which can be accessed through two separate doors equipped with suitable keys.
floor assembling with the possibility of approaching the wall; - structure made of steel panels (minimum thickness 15/10 mm) treated with anti-rust agents and coated with powder paint; - a ventilation hole capable of facilitating
the flow of air both in the battery unit and in the rectifier unit; - galvanized steel screws 8.8; exterior painted with RAL paint as stated in the specifications or RAL7030 in the absence of instructions,
following effective anti-rust treatment; - processing of internal panels and structures made of galvanized sheet metal. Interior equipment: - rectifier with voltage regulator type "Chopper" on the battery branch; - rectifier with
SCR voltage regulator on the installation branch; - lead hermetically sealed battery. Rectifier modules (common characteristics): metal box with degree of protection IP20, connected with cables via a terminal board; -
galvanic isolation transformer with a crystal core and an electrostatic shield between the primary and secondary; - current limiter and related voltage reduction in case of its intervention;
control and monitoring of the module in order to determine the correct minimum and maximum output voltage, signaling via internal LED lights exceeding the predicted limits in the mains supply voltage
the possibility of blocking the module in case of exceeding the maximum allowed level while maintaining the protection of the maximum voltage of the battery / installation and in case of failure; - charge on the battery resistor with characteristics of the "constant voltage" type; "limited current"
with stabilised maintenance voltage (IU-DIN) suitable for maintenance and charging of lead hermetically sealed batteries with automatic correction of charging voltage in a function of the internal temperature of the battery unit.
Device branch rectifier module: - voltage regulation type rectification with phase partialisation with fully controlled three-phase SCR bridge and LC filter, dimensioned so as to guarantee correct battery power supply in all conditions
and constant conduction of rated current to external elements; - protection circuits against voltage surges during switching; extra fast distribution line fuses on three phases of the bridge with indication of their intervention over
via appropriate micro switches signaling devices that will enable possible interruption of supply; - diode cooling bodies with thermal probe for signaling and blocking supply in case of
exceeding the maximum predicted temperature, and with a thermal probe for start up the extraction ventilator; - predisposition to operate at the voltage level provided for the device branch. Rectifier module
battery branch: - stabiliser with stabilised voltage with PWM regulation via "chopper" module, IGBT technology, which can be connected in parallel to obtain the predicted power or due to the need for redundancy;
silicon rectifier cooling body and commutator cooled by natural air flow; - varistor protection against power surges; - capacitive filter-electrolytic capacitor for
equalisation of rectified voltage at the output from the diode connection. Batteries: hermetic, stationary type, lead, AGM technology. Instruments: 2 voltmeters and ammeters on the branch of the battery and the installation are powered (in the case of digital instruments)
via a DC / DC converter with a guarantee of operation even in the absence of a power network. Protection: - Non-automatic modular general input circuit breaker; modular magnetic-thermal circuit breaker of the device branch with coil;
disconnector with distribution line fuses on the battery side; Signaling (different for two branches) on the synoptic board for: regular grid; phase sequence; rectifier stabilisation; supply failure; surge; intervention of distribution line fuses for protection;
Temperature rise; overload; ventilation anomalies; Signal only for the battery branch on the synoptic board for: maintenance charge level; constant voltage; minimum battery voltage
Alarm contacts (without voltage) 0.2A 110V (different for two branches) for signaling: presence of the grid; too high temperatures; surge c.c .; interruption of supply (breakdown); overload; Alarm contact only for
battery branch: buffer charging mode active; Alarm contacts for service branch only: rectifier output. Terminal board: modular pre-insulated anti-vibration terminals made of polyamide; output terminals110Vcc for cable clamping up to 16 mmq;
power terminals for cable clamping as indicated in the graphic elaborates; earthing terminal for cable clamping up to 16 mmq. Maintenance regulations: access to the inside of the control panel (board)
may only happen in safety conditions for the operator; minimum degree of internal protection with open door: IP20 provided with the implementation of adequate measures (insulation, shelters, etc.) deployment of various devices
so as to guarantee their efficient locating; - easy access to electronic modules and parts that are most often controlled, such as maneuvering elements, relays, LED signal lights, etc., for possible replacement
Il and / or maintenance. The characteristics of the rectifier and the adjustment of the regulation must be explicitly approved by the battery manufacturer and confirmed as in accordance with the needs of the battery itself.
The cost of procurement and installation must contain verification of the correctness concerning the degree of insulation, firmness, stabilisation of the output voltage, voltage ripple, as well as in connection with checking the functioning of the start up procedure,
switching off and failure mode simulation.
Double rectifier with battery, Rp = 5kVA, Rv = 24Vdc
| LV SUBSTATION - UPS AND DEA |  | 1
| Total amount |  | 1
L40.A10.A1 |  | n
UPS UNINTERRUPTIBLE POWER SUPPLY SYSTEM uninterruptible power supply system consisting of 1 static group. Compliance with standards: CEI 21-39, 21-47, 21-48, 22-7, 22-26, 22-27, 22-29, 22-24, 74-2. Delivery must include:
rectifier-inverter and insulation transformer cabinets on the bypass side; protection equipment, circuit breakers, etc. lead-acid batteries, suitable for fast discharges stored in cabinets
(separately calculated), with the autonomy described in the types; automatic magnetic-thermal circuit breakers of modular type and corresponding rated currents; cable connections between batteries and rectifiers; (optionally) supporting frame made of profiled steel
welded and lacquered. The price must include the procurement, installation and start up of each segment.
Ups Rp=90kVA, Rv=400V, autonomy 15'
| LV SUBSTATION - UPS AND DEA |  | 1
| Total |  | 1
L40.A10.A10 |  | n
UPS UNINTERRUPTIBLE POWER SUPPLY SYSTEM uninterruptible power supply system consisting of 1 static group. Compliance with standards: CEI 21-39, 21-47, 21-48, 22-7, 22-26, 22-27, 22-29, 22-24, 74-2. Delivery must include:
rectifier-inverter and insulation transformer cabinets on the bypass side; protection equipment, circuit breakers, etc. lead-acid batteries, suitable for fast discharges stored in cabinets
(separately calculated), with the autonomy described in the types; automatic magnetic-thermal circuit breakers of modular type and corresponding rated currents; cable connections between batteries and rectifiers; (optionally) supporting frame made of profiled steel
welded and lacquered. The price must include the procurement, installation and start up of each segment.
Ups for emergency lighting, Rp=30kW, Rv=400V, autonomy 1 hour
| LV SUBSTATION - UPS AND DEA |  | 1
| Total |  | 1
L50.A10.A41 |  | n
EMERGENCY SYSTEM Emergency system consisting of: electric diesel generating unit, power specified in types, with automatic start up and shutdown. Delivery must include:
sound-proof cabin (if required) or damper filters to be installed at the air inlet and outlet; - cooling and ventilation system (including any air deflector); - lubrication system;
preheating system; - exhaust system for exhaust gases with damper; - speed regulator; - accumulator batteries, appropriate support frames and a rectifier battery charger; electric start up motor
with appropriate control devices; control and command panel (board); fuel tank with a capacity of 120l, filling pumps and a suitable support bracket; stand made of profiled rods and fixing accessories
of the generating unit, including any elastic non-vibrating brackets; - equipment and accessories for procured devices; - auxiliary electric circuits protected in metal ducts and connected to the terminal board which is fixed to the stand.
(terminals will be of non-vibrating type); - pipes and valves necessary for establishing internal connections; - varnishing; tools and special wrenches for maintenance; spare parts for 1000 hours of operation.
earthing terminals for each device and equipment; appropriate connections in accordance with current Italian legislation. Gas pipes running from a storage tank;
2000 l storage tank in accordance with the legal provisions in this area; - connection and lines between the machines and the command panel (board); The price must include: -
procurement, installation and commissioning of various specified devices comprising the delivery.
Test resistance Rp=200kW
| LV SUBSTATION - UPS AND DEA |  | 1
| Total |  | 1
L50.A10.A5 |  | n
DIESEL GENERATING UNIT EMERGENCY SYSTEM consisting of: electric diesel generating unit, power specified in types, with automatic start up and shutdown. Delivery must include:
sound-proof cabin (if required) or damper filters to be installed at the air inlet and outlet; - cooling and ventilation system (including any air deflector); - lubrication system;
preheating system; - exhaust system for exhaust gases with damper; - speed regulator; - accumulator batteries, appropriate support frames and a rectifier battery charger; electric start up motor
with appropriate control devices; control and command panel (board); fuel tank with a capacity of 120l, filling pumps and a suitable support bracket; stand made of profiled rods and fixing accessories
of the generating unit, including any elastic non-vibrating brackets; - equipment and accessories for procured devices; - auxiliary electric circuits protected in metal ducts and connected to the terminal board which is fixed to the stand.
(terminals will be of non-vibrating type); - pipes and valves necessary for establishing internal connections; - varnishing; tools and special wrenches for maintenance; spare parts for 1000 hours of operation.
earthing terminals for each device and equipment; appropriate connections in accordance with current Italian legislation. Gas pipes running from a storage tank;
2000 l storage tank in accordance with the legal provisions in this area; - connection and lines between the machines and the command panel (board); The price must include: -
procurement, installation and commissioning of various specified devices comprising the delivery.
diesel generating unit Rp=350kVA
| LV SUBSTATION - UPS AND DEA |  | 1
| Total amount |  | 1
TOTAL AUXILIARY SYSTEMS AND PROTECTION SYSTEMS
08 - ENERGY DISTRIBUTION AND DISSIPATION
M10.A10.A8 |  | n
LIGHT SOURCE Light source consists of: - part of a quota for a distribution box installed on a voltage pole; power lines running from the distribution box to
the lighting device (which is specially included); light source terminal box (if necessary): in case of power supply of two separate luminaires installed in the same lighting device, a higher price for a double light source that includes changes or integration of wiring will have to be included (for the light source
In the case of power supply with dimmable lighting devices, a higher price for the dimmable light source, which includes changes or integration of wiring (excluding dimmers and controls) must be applied (to the light source).
The typology of wiring cables must be as provided in specifications and tables)
The materials used must have the characteristics listed in the appropriate chapter of this study.
Visible light supply with rigid PVC pipe and cable, IP65
| LV SUBSTATION - LIGHTING |  | 4
| MV / LV SUBSTATION - LV FINAL DISTRIBUTION |  | 2
| Total amount |  | 6
M10.A10.A9 |  | n
LIGHT SOURCE Light source consists of: - part of a quota for a distribution box installed on a voltage pole; power lines running from the distribution box to
the lighting device (which is specially included); light source terminal box (if necessary): in case of power supply of two separate luminaires installed in the same lighting device, a higher price for a double light source that includes changes or integration of wiring will have to be included (for the light source
In the case of power supply with dimmable lighting devices, a higher price for the dimmable light source, which includes changes or integration of wiring (excluding dimmers and controls) must be applied (to the light source).
The typology of wiring cables must be as provided in specifications and tables)
The materials used must have the characteristics listed in the appropriate chapter of this elaborate.
Terminals with non-combustible cable, IP65
| LV SUBSTATION - LIGHTING |  | 5
| Total amount |  | 5
M20.A10.A32 |  | n
CONTROL CIRCUIT BREAKER Control circuit breaker consisting of the quota for the distribution box installed on the voltage pole; power lines running from the distribution box
to the socket box; socket boxes that are built into the wall, depending on the type if necessary and with cable connectors; - control modular circuit breaker with the following characteristics:
CIRCUIT BREAKERS, SECTOR SWITCHES AND PUSH-BUTTONS compliance with CEI 23-9 standards and the following options, voltage and rated frequency 250V, 50Hz. current 10A for push-buttons and 16A for circuit breakers; test voltage 2000V at 50Hz for 1 min; breaking capacity:
200 holes and closings at 1.25 In, 275V, power factor 0.3; function test 50,000 per In, 250 V, power factor 0.6; insulation resistance> 15Mohm at 500V; - identification signal lamp
(if required); LIGHT INTENSITY REGULATORS (DIMMER) Voltage and rated frequency 230V +/- 10%; controlled power 60-500W (for resistive loads) insulation resistance> 15Mohm at 500V; regulation via rotary control
or double function push-button; extended push to adjust the increase or decrease, with electronic storage after push-button interruption, short push to switch the luminaire on and off with
with the selected illumination value; safety fuse; self-extinguishing polycarbonate terminal box frame (UL94-V0) for snap in fixing and removal, with fixing holes
by screws that enable the correction of possible defects in the position of the box in the hole; - closing and final processing of the box with elements that guarantee the following level of protection: at least IP21
(if not specified) with cover plates of the supervisor's choice, fixed under pressure via screws by means of a tool; IP55, with covers having a transparent elastic layer made of silicone rubber or similar, moisture resistant and
and water jet resistant, which would allow the operation of control devices guaranteeing a degree of protection with the cover closed; IP67, with non-removable cover with an elastic elastomeric membrane resistant to atmospheric agents
(disasters, heat, sunlight, low temperatures, etc.) to saline and / or acidic environments, alkalis, mineral and vegetable oils, animal fats and oils, fuels and fire resistant, fixed to the socket box with stainless steel screws
of any distribution box. In the event that the control must be connected to the light source by a light signal, a higher price will be included. In case the dimming control must be applied to
the light source, a price supplement will be included for the control with the stated characteristics. The price must include internal wiring between sockets.
The typology of wiring cables must be as provided in specifications. The materials used must have the characteristics listed in the appropriate chapter of this elaborate. CONTROL CIRCUIT BREAKER Control circuit breaker consisting of:
a part of the quota for the distribution box installed on the voltage pole; power lines running from the distribution box to the socket box; socket boxes that are built into the wall, depending on the type if necessary and with cable connectors; - control modular circuit breaker with the following characteristics:
CIRCUIT BREAKERS, SECTOR SWITCHES AND PUSH-BUTTONS compliance with CEI 23-9 standards and the following options, voltage and rated frequency 250V, 50Hz. current 10A for push-buttons and 16A for circuit breakers; test voltage 2000V at 50Hz for 1 min; breaking capacity:
200 holes and closings at 1.25 In, 275V, power factor 0.3; function test 50,000 per In, 250 V, power factor 0.6; insulation resistance> 15Mohm at 500V; - identification signal lamp
(if required); LIGHT INTENSITY REGULATORS (DIMMER) Voltage and rated frequency 230V +/- 10%; controlled power 60-500W (for resistive loads) insulation resistance> 15Mohm at 500V; regulation via rotary control
or double function push-button; extended push to adjust the increase or decrease, with electronic storage after push-button interruption, short push to switch the luminaire on and off with
with the selected illumination value; safety fuse; self-extinguishing polycarbonate terminal box frame (UL94-V0) for snap in fixing and removal, with fixing holes
by screws that enable the correction of possible defects in the position of the box in the hole; - closing and final processing of the box with elements that guarantee the following level of protection: at least IP21
(if not specified) with cover plates of the supervisor's choice, fixed under pressure via screws by means of a device; IP55, with covers having a transparent elastic layer made of silicone rubber or similar, moisture resistant and
and water jet resistant, which would allow the operation of control devices guaranteeing a degree of protection with the cover closed; IP67, with non-removable cover with an elastic elastomeric membrane resistant to atmospheric agents
(disasters, heat, sunlight, low temperatures, etc.) to saline and / or acidic environments, alkalis, mineral and vegetable oils, animal fats and oils, fuels and fire resistant, fixed to the socket box with stainless steel screws
of any distribution box. In the event that the control must be connected to the light source by a light signal, a higher price will be included. In case the dimming control must be applied to
the light source, a price supplement will be included for the control with the stated characteristics. The price must include internal wiring between sockets.
The typology of wiring cables must be as provided in specifications. The materials used must
have the characteristics listed in the appropriate chapter of this elaborate
Visible switch or push-button switch with rigid PVC pipe and cable - IP55
| LV SUBSTATION - LIGHTING |  | 5
| MV / LV SS - LV CABLE TERMINALS |  | 2
| Total amount |  | 7
M30.A10.B18 |  | n
POWER SUPPLY SOURCE Power supply source for various uses consisting of: - part of the quota for the distribution box installed on the voltage pole; power lines running from the distribution box
to the place of use (separately calculated); -possible distribution boxes and socket boxes (terminal boxes). The type of wiring cables must be the one specified in the specifications and will be dimensioned in accordance with the effective power
used by appliances (doors / motorised awnings, distribution cabinets, etc.) In case of using the existing or already provided power grid, only the price of wiring will be applied. In case of procurement and installation
of power lines and boxes, the price of preparation will be applied. The materials used must have the characteristics indicated in the appropriate chapter of the given elaborate.
Terminals with non-combustible cable, IP65
8
| MV / LV SS - LV CABLE TERMINALS |  | 2
| Total amount |  | 10
M30.A10.B7 |  | n
POWER SUPPLY SOURCE Power supply source for various uses consisting of: - part of the quota for the distribution box installed on the voltage pole; power lines running from the distribution box
to the place of use (separately calculated); -possible distribution boxes and socket boxes (terminal boxes). The type of wiring cables must be the one specified in the specifications and will be dimensioned in accordance with the effective power
used by appliances (doors / motorised awnings, distribution cabinets, etc.) In case of using the existing or already provided power grid, only the price of wiring will be applied. In case of procurement and installation
of power lines and boxes, the price of preparation will be applied. The materials used must have the characteristics indicated in the appropriate chapter of the given elaborate.
Terminals with non-combustible cable, IP65
6
| MV / LV SS - LV CABLE TERMINALS |  | 2
| Total amount |  | 8
N10.A10.A65 |  | n
SOCKET AND HOUSEHOLD PROTECTIVE SOCKET BOX AND SIMILAR Terminal box consisting of: - modular sockets with the following characteristics: HOUSEHOLD SOCKETS AND SIMILAR USES: Compliance with standards
CEI 23-5, 23-16i of the subsequent option; compliance with tables: CEI-UNEL 47158, 47 V3. rated voltage and frequency: 230V c. a. +/- 10%, 50Hz. rated current: as described in types; degree of protection: min. IP21; test voltage: 2000V at 50Hz for 1min;
breaking capacity: min. 100 plug-in maneuvers at 275V, a power factor of 0.6 with a test current of 1.24In (10A sockets) and 2.0 In (for 16A sockets); insulation resistance> 15Mohm at 500V;
snap in fixing to the module bracket frame with tool removal; CIRCUIT BREAKERS (magnetic and thermal protection devices of differential current, depending on types); compliance with standards: CEI 23-3 and subsequent options
rated voltage and frequency: 230V c.a. +/- 10%, 50Hz; rated current: as described in types; breaking capacity: 3000A; differential current (optional): 10mA; insulation resistance:> 15Mohm at 500V;
snap-in fixing to the module carrier frame with tool removal distribution line fuse BRACKET AND FUSES compliance with standards: CEI 32-1, 32-4, 32-5 and subsequent options; rated voltage and frequency: 230V c.a. +/- 10%, 50Hz; rated current: as described
in types; breaking capacity 100kA with power factor 0.2; INSULATION TRANSFORMER (in sockets for electric razors); compliance with standards: CEI 14-6 and subsequent options; primary voltage 230V c.a. +/- 10%; rated frequency: 50Hz;
secondary voltage; a 110V double coil that can be connected in series (230V) or in parallel (110V) via a commutator; rated power 20VA; microswitch for switching on the transformer only after putting the plug into the socket; overload protection;
self-extinguishing polycarbonate module bracket frame (UL94-V0) with fixing holes by means of screws such as to allow adjustment of any faults in the installation of the embedded box; closing and final works around terminal boxes
for household or similar use, with covering elements guaranteeing the following degree of protection: IP21 with cover plates at the company's choice which are fixed by pressure or screws and removable by means of
tool;with the door with a transparent elastic cover made of silicone rubber or the like, or with the door made of thermoplastic material, resistant to moisture and water jets when the door is closed. POINT OF EQUIVALENT POWER SUPPLY
Point of equivalent power supply consisting of: part of the quota of the distribution box installed on the voltage pole; visible or hidden wires running from the distribution box installed on the voltage pole
to the place of use (separately calculated); possible transit boxes and distribution boxes. The typology of cables and wires is presented in the appropriate chapter of the elaborate "Descriptive specifications and performance specifications of technical elements".
The price must also include cable connections between sockets. The materials that make up the power supply point must have the characteristics listed in the appropriate chapter of this elaborate.
Socket 2x16 A+E, IP44
6
| MV / LV TS - LV CABLE TERMINALS |  | 2
| Total amount |  | 8
N10.A20.A50 |  | n
INDUSTRIAL SOCKET WITH PROTECTION Compliance with standards: CEI 23-12 (92) and subsequent options; UL94-V1: Compliance with tables: CEI -UNEL 47173, 47174, 47175, 47176. Rated voltage 230 / 400V c.a. +/- 10%.
Rated frequency: 50Hz; Rated current: as described in types. Degree of protection: as described in types. Manufacturing characteristics: - box of modular type for installation in walls, or covered with heat-resistant polyester resin
which is self-extinguishing, reinforced with fiberglass, or of light alloy cast under pressure and coated with epoxy resin after chrome plating treatment depending on the type; cover with the same characteristics as the box
connected by hinges to the box, with stainless steel screws and elastomer seals; pre-cut holes with connections and a pipe press for connection to power lines.
socket with bayonet connector for mechanical blocking when the circuit breaker is closed, metal ring and protective waterproof cover made of thermoplastic material with stainless steel self closing spring, rotary cam switch-disconnector with
rotary cam switch-disconnector with disc holder of contacts made of insulating heat-resistant material resistant to the action of an electric arc and contacts made of silver with double break; mechanical lock to avoid pulling out the plug when the circuit breaker is closed; box lid hole and access to
any distribution line fuses and, when the lid is open, closing the circuit breaker itself; if required, distribution line fuses made of ceramic or thermoplastic self-extinguishing material, with fusible insert
whose size is standardised at the international level; if required, a safety transformer (according to CEI 14-6) with a minimum power of 160VA to power supply the safety low voltage (SELV) plug; a protection device comprising
a circuit breaker on the primary coil of the transformer, which is activated by switching on the user's circuit breaker; protection of primary and secondary coils via distribution line fuses
Socket 2x16 A+E, IP44
6
| MV / LV SS - LV CABLE TERMINALS |  | 2
| Total amount |  | 8
N10.A20.A56 |  | n
INDUSTRIAL SOCKET WITH PROTECTION Compliance with standards: CEI 23-12 (92) and subsequent options; UL94-V1: Compliance with tables: CEI -UNEL 47173, 47174, 47175, 47176. Rated voltage 230 / 400V c.a. +/- 10%.
Rated frequency: 50Hz; Rated current: as described in types. Degree of protection: as described in types. Manufacturing characteristics: - box of modular type for installation in walls, or covered with heat-resistant polyester resin
which is self-extinguishing, reinforced with fiberglass, or of light alloy cast under pressure and coated with epoxy resin after chrome plating treatment depending on the type; cover with the same characteristics as the box
connected by hinges to the box, with stainless steel screws and elastomer seals; pre-cut holes with connections and a pipe press for connection to power lines.
socket with bayonet connector for mechanical blocking when the circuit breaker is closed, metal ring and protective waterproof cover made of thermoplastic material with stainless steel self closing spring, rotary cam switch-disconnector with
rotary cam switch-disconnector with disc holder of contacts made of insulating heat-resistant material resistant to the action of an electric arc and contacts made of silver with double break; mechanical lock to avoid pulling out the plug when the circuit breaker is closed; box lid hole and access to
any distribution line fuses and, when the lid is open, closing the circuit breaker itself; if required, distribution line fuses made of ceramic or thermoplastic self-extinguishing material, with fusible insert
whose size is standardised at the international level; if required, a safety transformer (according to CEI 14-6) with a minimum power of 160VA to power supply the safety low voltage (SELV) plug; a protection device comprising
a circuit breaker on the primary coil of the transformer, which is activated by switching on the user's circuit breaker; protection of primary and secondary coils via distribution line fuses
Socket 2x16 A+E, IP44
6
| MV / LV SS - LV CABLE TERMINALS |  | 2
| Total amount |  | 8
TOTAL DISTRIBUTION AND POWER DISSIPATION POINTS
09 - EARTHING AND ATMOSPHERIC DISCHARGE PROTECTION
O10.A50.A1 |  | lump sum
EARTHING INSTALLATION OF SUBSTATION Earthing installation consisting of: earthing electrode made of copper plate of approximate dimensions 40x5 mm2, rounded corners, shaped, painted yellow, fixed
or on the wall of the facility or on the wall of the passage at approximately 50 cm, via load-bearing insulators of dimensions 30 cm, which are fastened by means of screws and inserts made of steel or PVC material. Connection by foreign metal structures present in the cabin
(pipelines, frames, locks, cable trunkings, supporting profiled sheet metal rods, grids, etc.) by means of copper plates or wires with a cross-section of not less than 16 mm2; connection from the switchboard earthing rod to the earthing electrode
connection between the earthing electrode and the transformer housing and between the neutral point (end) and the earthing electrode by fire-resistant cables. Earthing at least 2 points of the equipotential bonding installed
in the floor; functional and protective earthing of all devices in the transformer station by fire-resistant cables; possible bare 35mmq wire for earthing of all closure plates
with appropriate equipotential bonding
Equipotential bonding
| MV / LV SS - EARTHING |  | 1
| Total amount |  | 1
O10.A60.A1 |  | n
Copper rod with a cross-section of at least 200 mm2 with rounded corners, with holes for fastening protective conductors and earthing conductors via the terminals, which is fixed to the wall of the earthing shaft
and supported by two insulators.
ROD copper
| MV / LV SS - EARTHING |  | 1
| Total amount |  | 1
O10.A80.A1 |  | n
REINFORCEMENT CONNECTION Equivalent connection point consisting of: a round or plate conductor with a cross-section of up to 150 mm2 if it is made of galvanized steel or with a cross-section of up to 10 mm2 if it is made of copper
For connection between earthing ring and reinforcement; equipotential bonding between all segments of the reinforcement and the earthing electrode created by welding by aluminothermy or with joints by means of terminals.
| MV / LV SS - EARTHING |  | 8
| Total amount |  | 8
O10.A90.A1 |  | n
EARTHING MEASUREMENT Manufacturing characteristics: square-shaped plate, dimensions 85x85, made of cast bronze with a joint on the rear side to enable connection to the reinforcement using the method of aluminothermy;
4 M12 holes with screws at the corners. The price includes part of the welding quota.
| MV / LV SS - EARTHING |  | 1
| Total amount |  | 1
TOTAL EARTHING AND ATMOSPHERIC DISCHARGE PROTECTION
C | TOTAL POWER BLOCK