## SPECIAL PLANTS
NOTE | PRICES TO BE INSERTED MUST BE WITHOUT V.A.T.
D | ELECTRICAL - LOW VOLTAGE
Notes:
If on some position material or equipment manufacturer is indicated, teneder can instal other materials or equiment if with same or equivalent caracteristics in line with project documentation. All materials and equipment to be used in construction must be authorised by the Investor.
All related preparaory works, finishings, cleanings, correction, testing of materials, instalations, equipment, providing of atests or similar would not be quoted or payed separately. All pricess are to be incorporated in positions of the BoQ of this Volume. For execution of all positions all relevant materials, tools, movements, connections, organisations, worksman, insurance and other related, are suposed to be included in order to execute works in defined conditions, finalisation with indicated guarantee periods - everything ready for technical taking over.
COD. | DESCRIPTION | u.m. | N. | UNIT PRICE | TOTAL AMMOUNT
01 | SPECIAL PLANTS - OUTDOOR AREAS
01 - CONDUCTORS, CABLES AND ACCESSORIES
A310.A31.A1 | SINGLE MODE OPTICAL FIBRES OS1 LOOSE | m
In accordance with standard: ITU-T Rec G652 C; IEC 60793-2-50 tipa B 1.3; CEI 20-38.
Cables for external use, made of fibres with coat 250 microns type loose tube.
External insulation: polyethylene of high density.
Mechanical features:
filling: gel which provides fibre protection from moisture and other external impacts;
mechanical protection: fiber glass or other materials with protective pipe which contains the fibre and which protect them from damage that small rodents can cause in the open;
maximum tensile force: 1000N;
Tread resistance minimum: 200N/cm.
Optical fibres of single mode typeOS1 od 9/125 microns, which can support the flow of 1Gb/s do 9000m.
Maximum attenuation per km:
1310nm; 0.4 dB;
1550nm: 0.4 dB.
Fire resistance:
non propagating fire;
low emission of smoke and toxic and corrosive gases LSZH.
12 OS1 fiber optic cable
| OUTDOOR AREA - CONDUCTORS, CABLES AND ACCESSORIES |  | 230
| Total amount |  | 230
TOTAL 01 - CONDUCTORS, CABLES AND ACCESSORIES
02 - CONDUITS
B30.A10.A5 | PVC FLEXIBLE PIPE | m
In accordance with standard: CEI 23-82, 23-39 and subsequent versions of norms
Classification less than 3321.
Fire resistance >= 750N.
Impact resistance: >= 2J.
Electrical resistance of insulator: >= 100Mohm a 500V per minute.
Dielectric strength: >= 2kV/mm pri 50Hz na 15 min.
Fire resistance :does not contribute to heating
Level of system protection: min. IP4X
PVC flexible pipe D=40mm
| OUTDOOR AREA - CONDUITS |  | 60
| Total amount |  | 60
B50.A20.A5 | PEHD FLEXIBLE PIPES FOR LAYING UNDERGROUND | m
PROTECTIVE FLEXIBLE POLYETHYLENE PIPE OF HIGH DENSITY FOR LAYING UNDERGROUND
In accordance with standard: CEI 23-39, 23-46 and subsequent versions of standards.
Classification not less than 3441.
Tread resistance: >= 450N.
Impact resistance : >= 6J.
Electrical resistance of insulator: >= 100Mohm.
Dielectric strength: >= 20kV/mm.
Resistance to chemical agents and effect of microorganisms.
Structural features:
polyethylene pipe of high density (PEHD), with double smooth wall inside and corrugated outside;
ring connector for connecting several elements manicotto di congiunzione per l'Unione di più elements.
Level of system protection: min. IP4X.
PEHD flexible pipe D=110mm
| OUTDOOR AREA - CONDUITS |  | 290
| Total amount |  | 290
B50.A20.A8 | PEHD FLEXIBLE PIPES FOR LAYING UNDERGROUND | m
PROTECTIVE FLEXIBLE POLYETHYLENE PIPE OF HIGH DENSITY FOR LAYING UNDERGROUND
In accordance with standard: CEI 23-39, 23-46 and subsequent variations of standards.
Classification not less than 3441.
Tread resistance: >= 450N.
Impact resistance: >= 6J.
Electrical resistance of insulator: >= 100Mohm.
Dielectric strength: >= 20kV/mm.
Resistance to chemical agents and effect of microorganisms.
Features of production:
polyethylene pipe of high density (PEHD), with double smooth wall inside and corrugated outside;
ring connector for connecting several elements manicotto di congiunzione per l'unione di più elementi.
Level of system protection: min. IP4X
PEHD flexible pipe D=160mm
| OUTDOOR AREA - CONDUITS |  | 30
| Total amount |  | 30
B50.A30.A7 | PEHD THREE CONNECTED FLEXIBLE PIPES FOR LAYING UNDERGROUND | m
MONO-PIPE AND FLEXIBLE TRIPLE PROTECTIVE PIPE OF HIGH DENSITY POLYETHYLENE, FOR LAYING UNDERGROUND.
In accordance with standard: UNI 10910, UNI 5642, ISO 6259, UNI EN 921.
Pressure resistance (pri 23°C+/- 2%): performed with engine dynamometer and the reduction of the internal diameter of the end of the test less than 5% for PN8 and 15% of PN12, 5 and refund of 95% of the outer diameter.
Impact resistance without perforation (na 23°C+/- 2%): >= 7,85J achieved by using a cylindrical perforator with round top range 5mm, released in free fall from height of 0,5m.
Impact resistance on low temperatures (-20°C): > 29,4J za PN8 i 132J for PN12,5.
Pressure resistance: >= 6 bar za PN8 i 10 bar za PN12,5.
Softening temperature: >115°C.
Elasticity to break: 350% a 23°C.
Features of production:
pipes PEAD (pure high density polyethylene) made ​​by pressure, the configuration of the mono-tube or triple-tube (3 tubes each connected to one side) suitable for underground installation and to protect the fiber optic cables;
absence of blisters, burns, holes, deformation, material shortages, air pockets, wrinkles, cracks, damages..
PEHD flexible three pipes attached D=50mm
| OUTDOOR AREA - CONDUITS |  | 195
| Total amount |  | 195
C10.A40.A4 | POLYESTER CABINETS | n
POLYESTER CABINET REINFORCED WITH FIBER GLASS SUITABLE FOR INSTALLATION OF NAVIGATION EQUIPMENT
In accordance with standard: CEI 17-13/1, 17-13/3 and subsequent variations; UL94-V1.
Impact resistance: > 6J.
Dielectric strength: > 500V.
Resistance of insulation: > 1000 Mohm.
Resistance to chemical and atmospheric agents.
Features of production:
case of polyester coated with resin, flame-resistant, reinforced with fiberglass molded in one piece;
front door (blank) or with a window, opening to 180 ͦ, protected by a waterproof neoprene and waterproof locks;
holders with threads for fixing case and accessories;
-door-adjustable equipment at a depth ';
-possible protective covers for screws where surface fixing is envisaged, in order to guarantee the required level of protection and insulation.
Surface fixing.
Insulation level: Class II.
Protection level: min.IP55
Polyester cabinet for connection to telecommunication system, size 350x500x250mm
| OUTDOOR AREA - CONDUITS |  | 1
| Total amount |  | 1
CD.A16.A1 | MECHANICAL EXCAVATION OF THE TRENCH | m3
SECTION EXCAVATION WITH LIMITED MECHANICAL EXCAVATION
Limited excavation,on standard soil,even in the presence of water in the layer lesser than 20 cm,mechanical excavation is feasible, except for rocks.
Price includes works and following expenses:
removing mass ( stone ) capacity below m³ 0,400;
removal of objects of all kind of volumes up to 0,400 m³ ;
tearing and removing trees and stumps ';
possible drying of the terrain' ;
breaking traffic areas;
leveling the terrain which is excavated ';
storage of excavated material on the side';
re-backfilling the trench with selected material from excavation ;
previous identification and signaling of electric cables , telecommunication cables , water pipes , gas lines, sewers, storm sewers , etc.;
Excavation of a trench with strutting and identification of excavated material ';
-Backfilling the trench with carefully selected material from excavation without stones and vessels of trees that may be present on the surface;
reinstatement of soil, mechanical
compacting the trench with a possible addition of material.'
Not included in the price:
transport of excavated material, which is a surplus and / or is not usable or which D.L. company does not consider important;
compensation for landfill';
possibly pre-cut of floor coverings made ​​of asphalt or concrete
The scope of excavation shall be calculated on the basis of standard width, which is determined on the basis of related sections and on the depth of the pipe, plus the size of the subase, which is also determined on the basis of related sections. Price includes all costs resulting from any increase in sections, except section associated types, which are a consequence of the nature of the terrain, the presence of water, rocks, objects, etc.. or as a consequence of the weather conditions of any kind, everything is performed in a professional manner and in accordance with the instructions of the company D.L.
During the excavation, the safety of workers from the demolition of the walls must always be guaranteed. In the case of risk, walls will need to be protected during the work on one of the following ways, selected depending on the need:
formwork and temporary protection;
with appropriate reinforcement (Scarpa) walls of excavations, which the largest scope is the consequence of slope, which will be compensated at the same price of this article;
Digging with excavator till 1,5 m depth
| OUTDOOR AREA - CONDUITS |  | 98
| OUTDOOR AREA - CONDUITS |  | 95
| Total amount |  | 193
CD.C12.A1 | CUTTING ASPHALT | m
CUTTING ASPHALT SURFACES
Cutting asphalt surfaces with cutting machine, customized for optimal cutting
The price includes following expenses:
marking of the trench in an appropriate manner;
checking the presence of groundwater systems in the area;;
cutting asphalt with machine for cutting asphalt;
Except for clear order by DL company, only the first cut of given subase will be performed, even if it is necessary to cut deeper for better connecting of the old and the new layer of asphalt.
Cutting of asphalt paving
| OUTDOOR AREA - CONDUITS |  | 145
| OUTDOOR AREA - CONDUITS |  | 150
| Total amount |  | 295
CD.D10.A1 | BACKFILLING OF THE TRENCH WITH EXCAVATED MATERIAL | m3
BACKFILLING OF THE TRENCH WITH MIXTURE OF EXCAVATED MATERIAL
The formation of the lower layer and / or filling with crushed material granularity of 0-30 mm, which comes from the excavation, and which company that DL considers appropriate.
The price includes following expenses and compensations:
transport;
mechanical spreading
forming slope
compaction (of excavation)
procurement and setting warning tapes;
everything else necessary to execute the work professionally
Backfilling with excavated material
| OUTDOOR AREA - CONDUITS |  | 62
| OUTDOOR AREA - CONDUITS |  | 64
| Total amount |  | 126
CD.D32.A1 | BACKFILLING THE TRENCH WITH SAND | m3
BACKFILLING THE TRENCH WITH SAND
Supply and installation of sand for the subase and coating of pipes.
The price includes following works and expenses:
transport;
mechanical spreading
compaction ;
supply and setting warning tape 30 cm below finished layer;
everything else necessary to execute the work professionally.
Backfilling with the sand
| OUTDOOR AREA - CONDUITS |  | 17
| OUTDOOR AREA - CONDUITS |  | 13
| Total amount |  | 30
CE.A11.A16 | PREFABRICATED CONCRETE BOX | n
PREFABRICATED CONCRETE BOX FOR INSTALLATION INTO ROAD
Prefabricated concrete box of vibrated and reinforced concrete thickness of 6-8 cm for tk sewerage.
The price includes:
costs relating to the marking of the hole with fencing;
forming a concrete surface ("lean concrete");
installation of frame with necessary protection.
Not included in the price:
mark;
excavation.
Prefabricated concrete box size 60x60x20cm
| OUTDOOR AREA - CONDUITS |  | 2
| Total amount |  | 2
CE.A11.A2 | PREFABRICATED CONCRETE BOX | n
PREFABRICATED CONCRETE BOX FOR INSTALLATION INTO ROAD
Prefabricated concrete box of vibrated and reinforced concrete thickness of 6-8 cm for tk sewerage.
The price includes:
costs relating to the marking of the hole with fencing;
forming a concrete surface ("lean concrete");
installation of frame with necessary protection.
Not included in the price:
mark;
excavation.
Prefabricated concrete box size 40x40x40cm
| OUTDOOR AREA - CONDUITS |  | 5
| OUTDOOR AREA - CONDUITS |  | 6
| Total amount |  | 11
CE.A11.A4 | PREFABRICATED CONCRETE BOX | n
PREFABRICATED CONCRETE TRANSPORTABLE BOX CARRABILE
Prefabricated concrete box of vibrated and reinforced concrete thickness of 6-8 cm for tk sewerage.
The price includes:
costs relating to the marking of the hole with fencing;
forming a concrete surface ("lean concrete");
installation of frame with necessary protection.
Not included in the price:
mark;
excavation.
Prefabricated concrete box size 60x60x60cm
| OUTDOOR AREA - CONDUITS |  | 3
| Total amount |  | 3
CE.C10.A43 | CAST IRON COVER | n
CAST IRON COVER
Spheroidal cover of cast iron that consists of a frame for fixing and the cover
In accordance with standards: UNI EN 124
In accordance with tables: UNI 4544.
Class of resistance (depending on the type):
B125 with endurance >= 125 kN (12,5t) for use in places such as sidewalks, pedestrian zones which are occasionally opened for traffic, parking lots and multi-level parking for motor vehicles;
C250 with endurance> = 250 kN (25 t) to be installed on the edges of roads that extend up to 0.5 m on traffic lanes and up to 0.2 m on the sidewalks, roads and parking lots for vehicles;
D400 with endurance> = 400 kN (40t) for use in places such as passing (provincial and national roads) parking for all vehicles;
Production
in the form of a frame or a frame basis or on the top, with:
* external frame that surrounds the cover on all four sides, with rounded corners, with a length of not less than 20 mm in order to better strenghten the cover with the base*
*where necessary, the profile frame U-shaped in order to limit the penetration of liquids (hermetic type);
special elastomer round-throat provides protection against noise and damage;
*hinge-zipper with a system which blocks the cover in the open position of 110 ͦ;
* case for locking system;
*non-slip surface on the surface of the pavement similar to that of the cover;
square cover with:
* non-slip subase;
* ring for key- opener cover;
* closing by rotating latch;
*supplement that guarantees removal of the frame with the ability to draw the cover;
*height of 20 mm for class endurance B125, 40 mm for Class C250 endurance, 60mm for D400.
Works:
fixing concrete box with cement plaster with minimum thickness of 2 cm and the final sealing along the cover frame;
‚‚- screw which is fixed to the ground (if requested by the company DL).
Marks: covers shall have a legible and permanent mark which indicates:
compliance with norms UNI EN 124;
- scritta sulla parte centrale del coperchio indicante il sottoservizio (es. ILLUMINAZIONE PUBBLICA) da definire in sede DL;
class endurance;
standard and/or manufacter's label;
possible sign of compliance of third authority for certification
Cast iron cover for box 40x40cm, grade C250
| OUTDOOR AREA - CONDUITS |  | 5
| OUTDOOR AREA - CONDUITS |  | 6
| Total amount |  | 11
CE.C10.A45 | CAST IRON COVER | n
CAST IRON COVER
Spheroidal cover of cast iron that consists of a frame for fixing and the cover
In accordance with standards: UNI EN 124
In accordance with tables: UNI 4544.
Class of resistance (depending on the type):
B125 with endurance >= 125 kN (12,5t) for use in places such as sidewalks, pedestrian zones which are occasionally opened for traffic, parking lots and multi-level parking for motor vehicles;
C250 with endurance> = 250 kN (25 t) to be installed on the edges of roads that extend up to 0.5 m on traffic lanes and up to 0.2 m on the sidewalks, roads and parking lots for vehicles;
D400 with endurance> = 400 kN (40t) for use in places such as passing (provincial and national roads) parking for all vehicles;
Production
in the form of a frame or a frame basis or on the top, with:
* external frame that surrounds the cover on all four sides, with rounded corners, with a length of not less than 20 mm in order to better strenghten the cover with the base*
*where necessary, the profile frame U-shaped in order to limit the penetration of liquids (hermetic type);
special elastomer round-throat provides protection against noise and damage;
*hinge-zipper with a system which blocks the cover in the open position of 110 ͦ;
* case for locking system;
*non-slip surface on the surface of the pavement similar to that of the cover;
square cover with:
* non-slip subase;
* ring for key- opener cover;
* closing by rotating latch;
*supplement that guarantees removal of the frame with the ability to draw the cover;
*height of 20 mm for class endurance B125, 40 mm for Class C250 endurance, 60mm for D400.
Works:
fixing concrete box with cement plaster with minimum thickness of 2 cm and the final sealing along the cover frame;
‚‚- screw which is fixed to the ground (if requested by the company DL).
Marks: covers shall have a legible and permanent mark which indicates:
compliance with norms UNI EN 124;
- scritta sulla parte centrale del coperchio indicante il sottoservizio (es. ILLUMINAZIONE PUBBLICA) da definire in sede DL;
class endurance;
standard and/or manufacter's label;
possible sign of compliance of third authority for certification
Cast iron cover for box 60x60cm, grade C250
| OUTDOOR AREA - CONDUITS |  | 3
| OUTDOOR AREA - CONDUITS |  | 2
| Total amount |  | 5
CF.E10.A1 | BINDER | m2
Purchasing, setting and compacting the layer of bitumen, which is stored in the warm, to form the bonding layer, the grain size of 0-25 mm and which is made up of an aggregate obtained by crushing the originally used, is mixed, if possible, with the bitumen.
The price includes compensations and following expenses:
cleaning and later spraying del piano d'appoggio;
guard/safe keeping and signs of security;
everything else necessary to perform the work professionally.
Binder depth 7 cm
| OUTDOOR AREA - CONDUITS |  | 116
| OUTDOOR AREA - CONDUITS |  | 120
| Total amount |  | 236
TOTAL 02 - CONDUITS
11 - TRANSMISSION DATA AND TELEPHONE DEVICES
X100.A21.A4 | TELEKOM SOCKET RJ45 CAT. 6A | n
Position for data transmission must contain the following:
sockets RJ45 cat.6A, (number is indicated in the individual short descriptions)
cables SFTP cat 6A rack od FD (terminal) to the end with the socket (average distance 70m);
framework of terminal box and protective cover for the number of units that will be installed on the box;
(possible) transit box;
markings on each socket
covers to close each socket to protect from dust;
flexible PVC pipe (for built-in installation) diameter 32 mm, rigid PVC pipe (for installation in prominent place) diameter 32 mm, the dorsal (back) of sewage to the box where it is collected.
The price includes certification "permanent link" the standard CEI EN 50173 and 50174 and closing sockets with adequate cover following the certification.
n.2 telecom outlet RJ45 cat.6a in vista per controllo accessi con tubo in PVC rigido
| OUTDOOR AREA - TRANSMISSION DATA AND TELEPHONE DEVICES |  | 2
| Total amount |  | 2
X100.A21.A5 | TELEKOM SOCKET RJ45 CAT. 6A | n
Position for data transmission must contain the following:
integrated box, in prominent place (indicated in the individual short descriptions)
sockets RJ45 cat.6A, (number is indicated in the individual short descriptions)
cables SFTP cat 6A rack od FD (terminal) to the end with the socket (average distance 70m);
framework of terminal box and protective cover for the number of units that will be installed on the box;
(possible) transit box;
markings on each socket
covers to close each socket to protect from dust;
flexible PVC pipe (for built-in installation) diameter 32 mm, rigid PVC pipe (for installation in prominent place) diameter 32 mm, the dorsal (back) of sewage to the box where it is collected.
The price includes certification "permanent link" the standard CEI EN 50173 and 50174 and closing sockets with adequate cover following the certification.
n.2 telecom outlet RJ45 cat.6a in vista per telecamere con tubo in PVC rigido
| OUTDOOR AREA - TRANSMISSION DATA AND TELEPHONE DEVICES |  | 5
| Total amount |  | 5
TOTAL 11 - TRANSMISSION DATA AND TELEPHONE DEVICES
13 - INSTALLATIONS FOR FIRE DETECTION
R10.A52.A3 | OPTICAL-ACOUSTIC PANEL FOR WARNING | n
OPTICAL-ACOUSTIC PANEL FOR FIRE SIGNALISATION
In accordance with standard: EN 54-3.
Electromechanical characteristics:
operating voltage: 20-30 V DC.;
level protection: min. IP30 for internal installation , IP65 for outdoor installation.
Features of production:
body of self-extinguishing thermoplastic material with the red front part and the inscription "ALLARME INCENDIO" or "ALLARME GAS" ("FIRE ALARM" or "ALARM GAS");
optical and acoustic signalisation, both adjustable (impulse or fixed);
acoustic signalisation: min. 90db;
LED for work signalisation;
rechargeable battery 24V.
Optical acoustic warning fire panel with self powering kit, outdoor installation
| OUTDOOR AREA - FIRE DETECTION |  | 1
| Total amount |  | 1
R10.A52.A4 | OPTICAL-ACOUSTIC PANEL FOR WARNING | n
OPTICAL-ACOUSTIC PANEL FOR FIRE SIGNALISATION
In accordance with standard: EN 54-3.
Electromechanical characteristics:
operating voltage: 20-30 V DC.;
protection level: min. IP30 for indoor installation, IP65 for outdoor installation.
Features of production:
body of self-extinguishing thermoplastic material with the red front part and the inscription "ALLARME INCENDIO" or "ALLARME GAS" ("FIRE ALARM" or "ALARM GAS");
optical and acoustic signalling, both adjustable (impulse or fixed);
acoustic signalisation: min. 90db;
LED for work signalisation;
rechargeable battery 24V.
Optical acoustic warning gas panel with self powering kit, outdoor installation
| OUTDOOR AREA - FIRE DETECTION |  | 1
| Total amount |  | 1
R10.A80.A4 | INPUT OUTPUT SYSTEM FOR CONTROL AND RECEPTION | n
MODULE WITH ANALOG CONNECTIONS FOR DEVICE CONTROL AND SIGNAL RECEPTION
Input / output modules shall comply with the requirements of and be approved to EN54-17.
Input / output modules should connect directly to the loop and not require further power supply connections.
Each input / output module shall take one address.
Input / output modules shall additionally include:
1. Inputs monitored for short & open circuit.
2. Inputs can be configured for normally open or normally closed operation.
3. Outputs to be rated at 250VAC 4A resistive & 30VDC 4A clean contacts.
4. Output to be selectable as continuous or as pulsed operation. Pulse duration to be selectable between 1 & 20 seconds.
5. Integral short circuit isolator.
6. LED indication of normal, fault, test, & activation conditions.
7. Module can be configured as fail safe.
8. Modules to be mounted in an IP66 housing with clear lid for device status indication.
9. Modules should additionally be suitable for DIN rail mounting.
10. Operating temperature: -25°C to +60°C
11. EMC compatibility: 50V/m
Analogical output module
| OUTDOOR AREA - FIRE DETECTION |  | 4
| Total amount |  | 4
R100.A10.A11 | CONNECTING DETECTOR POSITIONS | n
APPROPRIATE POSITION OF INDICATOR
Medium price point indicator (indicator equipment not included) includes:
Line signalisation and transmission from the switchboard to the indicator, connected in a loop by fire-resistant for 30 minutes, 2 x 18AWG (diameter 1 mm);
junction boxes and boxes for the reception and transmission installed in the rear of the channels in the interior;
conduit from the box on the back of the equipment for the indication.
The path of the conduit and location of indicator are shown in the graphic drawings.
Location of appropriate indicators will be determined by adding the total equipment (indicators, sensors, buttons, sirens, synoptic and signaling panels, etc.) and the subsequent application of the average value of each of them, which is why the price is useful for connecting any components.
Analogical detector point connection with PVC rigid pipe and cables
| OUTDOOR AREA - FIRE DETECTION |  | 4
| Total amount |  | 4
R100.A10.A2 | CONNECTING DETECTOR POSITIONS | n
APPROPRIATE POSITION OF INDICATOR
Medium price of point indicator (indicator equipment not included) includes:
Line signalisation and transmission from the switchboard to the indicator panel, connected in a loop fire-resistant for 30 minutes, 2 x 18AWG (diameter 1 mm);
junction boxes and boxes for the reception and transmission installed in the rear of the channels in the interior;
installed pipe from the box on the back of the equipment for the indication.
The path of the installation pipe and location of indicator are shown in the graphic drawings.
Location of appropriate indicator will be determined by adding the total equipment (indicators, sensors, buttons, sirens, synoptic and signaling panels, etc.) and for subsequent application of average value of each of them, which is why the price is useful for connecting any components.
Analogical detector point connection with PVC flexible pipe and cables
| OUTDOOR AREA - FIRE DETECTION |  | 2
| Total amount |  | 2
TOTAL 13 - INSTALLATIONS FOR FIRE DETECTION
14 - INSTALLATIONS OF A BURGLAR ALARM, ACCESS CONTROL AND TVCC CAMERA
R20.A100.A1 | MODULE FOR DOOR CONTROL | n
UNIT FOR CONTROL ACCESS
A Dual Reader Interface Module (DRIM) shall be available for each controlled door and provide the ability to connect up to two card readers or entry devices. This DRIM shall:
q Monitor the door position (door contact)
q Allow the connection of a Request-to-Exit (REX) switch for exit
q Control an electric door lock or strike
q Provide the facility for up to 3 auxiliary input devices to be connected
q Allow the connection of an alarm buzzer that can be triggered in the case of an alarm event, or more specifically locally trigger a buzzer for a door held event before this alarm is registered at the host.
All events that occur at the door must be reported from the DRIM to the ISC.
To allow for situations where an entry and exit reader may be required at the one door a DRIM will allow two readers to be connected. However, in circumstances where a door shall only require one reader the DRIM can be configured to operate in a two door mode, whereby a reader, door lock and door monitoring device can be connected for each door.
In addition, the DRIM shall also provide connection for single advanced reader that connects via an RS-485 or Wiegand / Clock/Data connections.
Finally, the DRIM shall also provide the ability to work offline in cases where communications with ISC has have been lost and still continue to accept a set of specified cards as being valid to the door(s) which it controls.
The device must contain all necessary power cables, Cat6 patch cable for connecting with vicinal cable systems, vertical cables, and all the necessary equipment for the professional completion of works.
Door control module
| OUTDOOR AREA - SECURITY SYSTEMS |  | 2
| Total amount |  | 2
R20.A102.A1 | PROXIMITY READER | n
TERMINAL OF PROXIMITY READER WITH A CARD
The terminal of proximity reader, which sends data to the peripheral unit, which controls the door to enable the operation of recognizing, authorization and executing commands of authorization.
 Transmission frequency 13.56 MHz
 The following card technologies are supported:
ISO14443-A:
 Mifare 1k and 4k (UID, S/B, MAD)
 Mifare UltraLight (UID, B)
 Mifare DesFire (UID)
 my-D proximity (UID, B) ISO14443-A+B
 my-C (UID) ISO15693:
 my-D vincinity (UID)
 I-Code SLI (UID)
 Tag-IT HFI (UID)
 LRI512 (UID)
 Configuration using configuration card or software tool
 Up to 7 cm read range, depending on mounting environment, card technology and card type
 DIP switch for functionality selection
 Flash memory for firmware updates
 Three-colour LED for status display and buzzer for audible signals
 Reader power from the power supply of the door controller
 "Touch and Go" operation
Proximity reader with code keypad
| OUTDOOR AREA - SECURITY SYSTEMS |  | 2
| Total amount |  | 2
R20.A50.A2 | DETECTION OF MASS USING MAGNETIC LOOP | n
SYSTEM CONTROL OF GATE USING MAGNETIC LOOP
Control system of door of entrance gate consists of:
central for control with a digital contact when leaving;
tin box (IP55);
power supply;
loop for the detection of metal mass installed under the road made ​​of cable H07V-K or cable H07S-K cross-section 1.5 mmq;
power cable for power supply of switchboard type FG7OM1 3x1, 5mmq;
signaling cable TRR 2x0, 60 mmq from the switchboard to the module to run the door.
Mass detection by magnetic spire
| OUTDOOR AREA - SECURITY SYSTEMS |  | 6
| Total amount |  | 6
R50.A16.A1 | IP FIXED CAMERA MINIDOME PoE | n
FIXED COLOR IP TELECAMERA MINIDOME
Fixed telecamera minidome for installation on the ceiling or on the wall, following characteristics:
case suitable for installation, with maximum cross-section ring 140 mm and height 128 mm;
power supply PoE according to standard IEEE 802.3 af;
communication with LAN Ethernet network, compatible to central video recording system as well as to central management station (BMS - Desigo CC)
with changing focus 3 - 9 mm;
sensor CMOS with progressive scanning.
Multiple stream which can be indvidually configured H.264 i Motion JPEG;
maximum resolution of at least SXGA 1,3MPixel, speed 12 fps. Possibility of sending at least two streaming videos, one for monitoring, and other for recording.
possibility of picture rotation;
resolution control of the picture: color, brightness, contrast, white level, etc.
motion detection function and anti-tamper alarm;
perfect integration with switchboard TVCC.
Camera must be equipped and installed with:
patch cord on the side of the camera and on the side of rack;
programming;
softwer licence.
IP fixed camera minidome PoE for indoor/outdoor installation
| OUTDOOR AREA - SECURITY SYSTEMS |  | 2
| Total amount |  | 2
R50.A40.A1 | FIXED COLOR CAMERA PoE FOR EXTERNAL INSTALLATION | n
FIXED IP CAMERA FOR EXTERNAL- VIDEO SURVEILLANCE
Fixed IP camera for installation on the wall or on the pillar, with following characteristics:
case IP66, external, equipped with system for temperature control,with sun protection, carrier on the wall or on the pillar;
power supply PoE according to standard IEEE 802.3 af + external power supply 230V AC for thermoregulation;
communication with LAN Ethernet network, compatible to central video recording system as well as to central management station (BMS - Desigo CC)
with changing focus 2,8-10 mm;
sensor CCD 1/3", Day/Night.
Multiple stream which can be individually configured Motion JPEG;
maximum resolution of at least 4CIF. Possibility of sending at least two streaming videos, one for monitoring, and other for recording.
possibility of picture rotation;
resolution control of the picture: color, brightness, contrast, white level, etc.
motion detection function and anti-tamper alarm;
perfect integration with switchboard TVCC.
Camera must be equipped and installed with:
patch cord na strani kamere i na strani rack;
programming;
softwer licence.
Fixed color D/N camera PoE for outdoor installation with protection box
| OUTDOOR AREA - SECURITY SYSTEMS |  | 3
| Total amount |  | 3
S60.A40.A3 | VIDEO INTERCOM SYSTEM | n
INSTALLATION OF VIDEO INTERCOM SYSTEM
The front door with a digital video intercom with two wires which can be used for a call from outside (the entrance to the residential area) with a camera, using the key that is activated from the inside.
In accordance with standard: CEI 12-13(88), 14-6(90) and subsequent variations; HD 195 S4.
Installation will include following equipment:
ELECTRONIC POWER SUPPLY SYSTEM
power supply and following frequencies: 230V AC +/-10%, 50Hz;
secondary outputs: 22V AC / 0.9 a continuous power of pulsing light and resistance to overheating; 22V AC / 0.5, service with interruptions for voice,calls, the brightness of the recording place, the camera; monitor; 22V DC/3A pulse electric lock; 25V DC / 0.8 A service with interruptions for the interior, necessary equipment, etc..
power of transformer: 60VA;
system for decoding the digitized calls for confirmation of dialed numbers;
Production:
*body of thermoplastic material with a modular structure suitable for installation of DIN or OMEGA carrier inside the box frame or extension (calculated separately) or on a wall inside the box;
*protective cover of input terminals;
* self-protection against the entry and exit using the fuse;
*Core of transformer consists of the conductor of poor conductivity;
EXTERNAL UNIT OF DIGITAL INTERCOM WITH VIDEO
External unit with modular elements (name tile, audio tile, tile-key, tile for recording, boxes, frames, module carrier, etc.) suitable for creating various configurations, consisting of:
Tiles made ​​of anodized aluminum in color choosen by the company DL, namely light alloy obtained under pressure, the minimum diameter of 15 mm, treated against corrosion with a mailbox with the name of polycarbonate with special screws for protection against burglary.
integrated box made of thermoplastic material;
audio units
* power supply: at least 6V DC +/-5%;
* level of noise in the background < 30mV;
* external key made of thermoplastic material:
* amplified microphone and speaker, with a particular control volume in communication inwards or outwards;
recording system:
* camera implemented in technology CCD 1 / 4" color;
* power supply: 16-20V DC.;
* consumption: 400mA pri radu, 70mA u funkciji stand-by;
* video output: modulated signal
*start time: < 6 sec.;
*mechanical screw for adjusting focus;
* screws for removal of mechanical cover in the event of failure of the latter;
* Installation (for external installation) vertical installation; (light version) on a wall or ceiling, complete with adjustable carrier and power plug where it is needed, case contains the thermostat to protect against rainfall
INTERNAL INSTALLATION
* power supply 18-23 V DC.;
* screen: LCD 3,5";
* start time: < 6 sec.;
* amplitude of video signal on the entrance: 0,5-1,5 V pp;
* vertical frequency : 50Hz synchronized with the network;
* activation time, at least 60 sec.;
* a white body made from thermoplastic material;
* micro phone with spiral cable;
* unit for protection of conversation;
* a possibility of call from another level or outside;
*keys to open doors, turn on the lights in the staircase, the ability to monitor the interior, the ability to call headquarters (where necessary);
*adjusting the brightness and contrast;
* accessories for installation;
*appropriate settings for simplified installation of cables;
* installation on the wall or on the table;
DELIVERY OF VIDEO SIGNALS
delivery of video signals, transmission of voice and data with a low coefficient of attenuation, for installations with two wires to separate the video signal taken from the vertical pipe to the inside.
ELECTRONIC CLOSING
power supply: 12V AC.
Outdoor video entry phone
| OUTDOOR AREA - SECURITY SYSTEMS |  | 2
| Total amount |  | 2
TOTAL 14 - INSTALLATIONS OF A BURGLAR ALARM, ACCESS CONTROL AND TVCC CAMERA
16 - CENTRALIZED SURVEILLANCE AND MANAGEMENT SYSTEM
Y100.A10.A2 | BUILDING MANAGEMENT SYSTEM (BMS) | n
CENTRALIZED SYSTEM OF INSTALLATION CONTROL (BMS SYSTEM)
Control system with an integrated command for automatic control of electrical installations, single software platform for fire and security systems, thermotechnical systems (described in Volume 3 (Book 3) of thermomechanical installations project) by using BACNet over IP protocol for fire and thermotechnics. Fully integrated with light control system using protocol communication (KNX/EIB) Building Management System, which consists of the following elements:
N.1 Computer for monitoring with software SCADA (Supervisory Control And Data Acquisition) WinCC, with the base for processing data from the electrical system, "high voltage", safety, security and thermomechanization that the graphical interface allows the user to visualize the following functions:
electrical installation of high voltage (high voltage):
* value and status that come directly from the bus line from the unit for a dialogue with the microprocessor installed in the electrical frames;
* status and alarms relay switches that control electronic boxes;
* status and alarms UPS;
*status values ​​and alarms photovoltage system;
*status and alarm of main apparatus of electrical cabine.
*safety installations (fire and gas indicators)
* status and alarms of switchboards;
* status of the serial lines and indicator loops;
* status and alarms of indicators, with planimetric representation of their positions;
* status and planimetric position of pulsing alarms;
* status of input and output modules
Installation of sound signalization for evacuation
* status of central unit;
* status of amplitude line;
safety installations (burglary, access control, CCTV)
* status and position of door control;
* status/alarm/planimetric position of indication elements;
* status of burglary switchboard.
Lighting system:
* status of individual control units;
* control and regulation of illuminotechnical status in different environments (ON/OFF/DIMM);
possibility of programming lighting scenario
night configuration
Display of alarms from all installations and keeping them in a database;
graphic display for the report:
*energy production from photovoltage (daily, hourly, monthly, annual);
* energy consumption of the building;
*alarms from external devices.
CONTROL UNIT OF ELECTRICAL HIGH VOLTAGE INSTALLATIONS consists of the following elements:
unit for receiving digital input, installed by the electrical boxes (unit in the open), connected to the PLC via lines Bus, Modbus or Profibus, will have to serve as electrical isolation (galvanic separation) between the low-voltage of maintained apparatus and the lowest voltages within the control modules, which include optical signals, which refers to signals that are received, and the functions in progress.
unit for receiving digital input, installed with different electrical boxes (external unit), connected to the PLC via Bus lines, Modbus or Profibus, will have to serve as electrical isolation (galvanic separation) between the low-voltage maintained apparatus and the lowest voltage within the control module, which contain optical signalization, which refers to signals that are received, and the functions in progress.
peripheral units for maintenance and automation of isolated functions (PLC) that are installed with various electrical boxes, consist of:
* power source 230 V AC 50 Hz with transformer on 24 VDC;
* scheme processor scheme with inputs of serial interface with a standard protocol Modbus or Profibus for connecting units in the open;
* scheme network with protocol serial port RS485 Modbus or Profibus for connection to a PC or supervision;
transmission mode with terminal setup and power supply modules interface and for connecting to the control modules, have the following features:
* plastic holder that allows easy installation on DIN supporter with base štamframeploče with lines for power and signal transmission, power plugs, fuses, broadband cables with connectors for connection to the control module, connect to the screw for connecting at precisely specified places;
* strength and frequence of power supply: 24V AC, +15/-10% - 50Hz;
* insulation level: class II;
* protection level: min. IP20.
Image bus lines with 4 conductors section 24 AWG, the serial connection of different elements that make up the system;
router for conversion of serial line to network TCP/IP for communication with supervisor computer, with patch cord in cat.6A;
dress package through conductors, accessories and special parts;
programming and system check;
LIGHTING CONTROL SYSTEM
Consists of the following parts:
POWER SUPPLY OF BUS LINES suitable for installation on DIN carriers 35mm (inside the electrical boxes) output voltage 640mA;
THE JOINTS BETWEEN MAIN AND SECONDARY BUS LINE with galvanic separation thereof, suitable for installation on DIN supporter 35mm (inside the electrical frames), suitable for data transmission through bus lines from one curcuit to another, and vice versa (potential short circuits on the secondary bus lines have been discovered and there is no transmission); ;
MODULE FOR MANAGEMENT OF ELECTRONIC REACTOR, SILENCERS AND STEERABLE (DALI) with the following characteristics:
* line management, each with 64 reactors/electrical transformers, in compliance with DALI, which can be split into 16 independent lighting;
* darkening 1÷100%;
* possibility of failure signalization in the system;
* command cables of changing polarities;
* connecting using clamps with screws;
* protection level min: IP20, dim: 40 x 30 x 270L mm.
* interface EIB/KNX;
MODULES INPUT MODELS WITH KEYS suitable for installation inside the box 503 with the following characteristics:
* 4 separate entrances with key;
*depending on the direction of the module, you can manage all the terminals of a system: Briefly pressing the appropriate button switches from one state to another (state "Missing" and state "Present"). A long press on the button increases or decreases shading of complete lighting or a group;
* cable long 5m prefabricated,for connecting module and key;
*protection level min: IP20, dim: 40 x 40 x 17 p mm.
DIGITAL OUTPUT MODULE WITH 4 POTENTIAL-FREE CONTACTS
has following characteristics:
*output relay with contacts for controlling and the independent directing for switching of electrical installations with voltage network up to 230/240V; komutaciju
* conductivity of contacts: 10A u AC1;
*connecting with clamps with screws;
* test key, LED for signalisation;
*installation into electrical box on DIN carrier 35 mm;
* protection level min: IP20, dim: 3 moduls.
PRESENCE OF LIGHT SENSOR (included in the BoQ Books (Book) 4 "high voltage") for inclusion of internal illumination system or control of the level of illumination as a function of contributions to natural light, with the following characteristics:
* installation in a prominent place on the ceiling or on the wooden beam by using particular carrier (the last one is included);
* auto power off function;
*the presence indicator is integrated with a time delay compared to the shutdown between 30 seconds and 20 minutes;
presence of indicator zone: dimensions around 4,0x4,0 m (when people are sitting) ili 6,0x6,0 m (people are moving) za Hinst=2,5m; dim. oko 4,5x4,5 m (people are sitting) ili 7,0x7,0 m (preople are moving)for Hinst=3,0m;
*indication field of illumination value: od 6 do 1.600 [lx];
* angle of sensor viewing around 120° (vertical); 360° (horizontal);
*protection level: IP20, dim. Oko 100x100x55 h mm.
router to convert a serial line EIB / KNX in the network ethernet TCP / IP to communicate with a computer for monitoring, which consists of di patch cord in cat. 6A;
bus network EIB/KNX implemented with certified cables;
bus network DALI implemented with certified cables;
INTERFACE DEVICES FOR LOW VOLTAGE INSTALLATIONS
Consists of:
BACNet over IP communication for fire detection, router for gas, embedded protocols for systems against burglary, which enable monitoring and full control for ALL data points by network LAN Ethernet with protocole TCP / IP; will also be equipped with a driver that will enable translation within the central database with the data obtained by the computer supervisor;
interface switchboard sound system using digital contacts at the entrance to the switchboard for fire detection;
interface access control system using the database within the computer for control that is dedicated to access control system;
Interface CCTV camera system using IP network and CCTV software modules which are ambedded in BMS software
CONTROL POINT FOR ELECTRICAL INSTALLATIONS OF HIGH VOLTAGE
Consists of:
a control units for the control with the schemes in the area of ​​the ports sufficient to manage controlled points , which are required for the control of a specific apparatus or an electrical frame;
bus line;
electric voltage of control apparatus;
part of the quota computer for supervision;
graphic station for review of controlled points;
licence.
CONTROL POINT OF ILLUMINATION INSTALLATION
Consists of:
regulation units installed on electrical frames on BUS DALI i EIB/KNX;
control units on the terrain for procurement of command keys and for presence indicators and illumination;
router;
bus DALI e EIB/KNX;
electrical voltage of control apparatus;
quota part of the computer for supervision;
graphic for mapping regulated systems and control of illuminotechnical configurations;
licence.
CONTROL PONT FOR SPECIAL INSTALLATIONS
Consists of:
router interface switchboard and supervisor;
quota part of the computer for supervision
graphic for mapping controlled devices and for visualization status/ alarm;
licence.
Control points are specificially indicated in special paragraph Address Points
BMS input/output address point for control lighting system
| OUTDOOR AREA - BMS |  | 1
| Total amount |  | 1
Y100.A10.A3 | CENTRALIZED CONTROL INSTALLATION SYSTEM (BMS SYSTEM) | n
Control system with integrated command for automatic management of electric installations, special and termomechanical, (described in book 3 (Book 3)of project thermomechanical installations), Building Management System, consists of the following elements:
N.1 Computer for monitoring with software SCADA (Supervisory Control And Data Acquisition), with the base for processing data from the electrical system, "high voltage", safety, security and thermomechanization that the graphical interface allows the user to visualize the following functions:
electrical installation of high voltage (high voltage):
* value and status that come directly from the bus line from the unit for a dialogue with the microprocessor installed in the electrical boxes;
* status and alarms relay switches that control electronic frames;
* status and alarms UPS;
*status values ​​and alarms photovoltage system;
*status and alarm of main apparatus of electrical cabine.
*safety installations (fire and gas indicators)
* status and alarms of switchboards;
* status of the serial lines and indicator loops;
* status and alarms of indicators, with planimetric representation of their position;
* status i planimetrijska pozicija pulsirajućih alarma;
* status of input and output modules
Installation of sound signalization for evacuation
* status of central unit;
* status of amplitude line;
safety installations (antiburglary, access control, CCTV)
* status and position of door control;
* status / alarm / planimtrijska position elements indications status/alarm/planimtrijska element positions of indication;
* status of anti burglary switchboard.
Lighting system:
* status of individual control units;
* control and regulation of illuminotechnical status in different environments (ON/OFF/DIMM);
possibility of programming lighting scenario
night configuration
Display of alarms from all installations and keeping them in a database;
graphic display for the report:
*energy production from photovoltage(daily, hourly, monthly, annual);
* energy consumption of the building;
*alarms from external devices.
CONTROL UNIT OF ELECTRICAL HIGH VOLTAGE INSTALLATIONS consists of the following elements:
unit for receiving digital input, installed by the electrical boxes (unit in the open), connected to the PLC via lines Bus, Modbus or Profibus, will have to serve as electrical isolation (galvanic separation) between the low-voltage of maintained apparatus and the lowest voltages within the control modules, which include optical signals, which refers to signals that are received, and the functions in progress.
unit for receiving digital input, installed with different electrical boxes (external unit), connected to the PLC via Bus lines, Modbus or Profibus, will have to serve as electrical isolation (galvanic separation) between the low-voltage maintained apparatus and the lowest voltage within the control module, which contain optical signalization, which refers to signals that are received, and the functions in progress.
peripheral units for maintanace and automation of isolated functions (PLC) that are installed with various electrical boxes, consist of:
* power source 230 V AC 50 Hz with transformer on 24 VDC;
*scheme processor with inputs of serial interface with a standard protocol Modbus or Profibus for connecting units in the open;
*scheme network with protocol serial port RS485 Modbus or Profibus for connection to a PC or supervision;
transmission mode with terminals for set-up and power supply of modules with interface and for connecting with the control modules, have the following characteristics:
* plastic holder that allows easy installation on DIN supporter with base štamframeploče with lines for power and signal transmission, power plugs, fuses, broadband cables with connectors for connection to the control module, connect to the screw for connecting at precisely specified places;
* strength and frequence of power supply: 24V AC, +15/-10% - 50Hz;
* insulation level: class II;
* protection level: min. IP20.
image of bus line with 4 conductors section 24 AWG, for the serial connection of different elements that make up the system;
router for conversion of serial line to network TCP/IP for communication with supervisor computer, with patch cord in cat.6A;
dress package through conductors, accessories and special parts;
programming and system check;
LIGHTING CONTROL SYSTEM
Consists of the following parts:
POWER SUPPLY OF BUS LINES suitable for installation on DIN carriers 35mm (inside the electrical box) output voltage 640mA;
THE JOINTS BETWEEN MAIN AND SECONDARY BUS LINE with galvanic separation thereof, suitable for installation on DIN supporter 35mm (inside the electrical boxes), suitable for data transmission through bus lines from one curcuit to another, and vice versa (potential short circuits on the secondary bus lines have been discovered and there is no transmission) ;
MODULE FOR MANAGEMENT OF ELECTRONIC REACTOR, SILENCERS AND STEERABLE (DALI) with the following characteristics:
* line management, each with 64 reactors/electrical transformes, in compliance with DALI, which can be split into 16 independent lighting;
* darkening 1÷100%;
* possibility of failure signalization in the system;
* command cables of changing polarities;
* connecting using clamps with screws;
* protection level min: IP20, dim: 40 x 30 x 270L mm.
* interface EIB/KNX;
MODULES INPUT MODELS WITH KEYS suitable for installation inside the box 503 with the following characteristics:
* 4 separate entrances with key;
*depending on the direction of the module, you can manage all the terminals of a system: Briefly pressing the appropriate button switches from one state to another (state "Missing" and state "Present"). A long press on the button increases or decreases shading of complete lighting or a group;
* cable long 5m prefabricated,for connecting module and key;
*protection level min: IP20, dim: 40 x 40 x 17 p mm.
DIGITAL OUTPUT MODULE WITH 4 POTENTIAL-FREE CONTACTS
has following characteristics:
*output relay with contacts for controlling and the independent directing for switching of electrical installations with voltage network up to 230/240V;
* conductivity of contacts: 10A u AC1;
*connecting with clamps with screws;
* test key, LED for signalisation;
*installation into electrical box on DIN carrier 35 mm;
* protection level min: IP20, dim: 3 moduls.
PRESENCE OF LIGHT SENSOR (included in the BoQ Books (Book) 4 "high voltage") for inclusion of internal illumination system or control of the level of illumination as a function of contributions to natural light, with the following characteristics:
* installation in a prominent place on the ceiling or on the wooden beam by using particular carrier (the last one is included);
* auto power off function;
*the presence indicator is integrated with a time delaycompared to the shutdown between 30 seconds and 20 minutes;
presence of indicator zone: dimensions oko 4,0x4,0 m (when people are sitting) ili 6,0x6,0 m (people are moving) for Hinst=2,5m; dim. oko 4,5x4,5 m (people are sitting) ili 7,0x7,0 m (preople are moving) za Hinst=3,0m;
*indication field of illumination value: od 6 do 1.600 [lx];
* angle of sensor viewing around 120° (vertical); 360° (horizontal);
*protection level: IP20, dim. Oko 100x100x55 h mm.
router to convert a serial line EIB / KNX in the network ethernet TCP / IP to communicate with a computer for monitoring, which consists of di patch cord in cat. 6A;
bus network EIB/KNX implemented with certified cables;
bus network DALI implemented with certified cables;
INTERFACE DEVICES FOR LOW VOLTAGE INSTALLATIONS
Consists of:
BACNet over IP communication for fire detection, gas and against burglary, which enable translation of serial line that comes from the individual switchboards in network LAN Ethernet with protocole TCP / IP; will also be equipped with a driver that will enable translation within the central database with the data obtained by the computer supervisor;
interface switchboard sound system using digital contacts at the entrance to theswitchboard for fire detection;
interface access control system using the database within the computer for control that is dedicated to access control system;
Interface CCTV camera system using a digital contacts on the door alarm system on the entrance of the burglar system.
CONTROL POINT FOR ELECTRICAL INSTALLATIONS OF HIGH VOLTAGE
Consists of:
a control units for the control with the schemes in the area of ​​the ports sufficient to manage controlled points , which are required for the control of a specific apparatus or an electrical frame;
bus line;
electric voltage of control apparatus;
part of the quota computer for supervision;
graphic station for review of controlled points;
licence.
CONTROL POINT OF ILLUMINATION INSTALLATION
Consists of:
regulation units installed on electrical frames on BUS DALI i EIB/KNX;
control units on the terrain for procurement of command keys and for presence indicators and illumination;
router;
bus DALI e EIB/KNX;
electrical voltage of control apparatus;
quota part of the computer for supervision;
graphic for mapping regulated systems and control of illuminotechnical configurations;
licence.
CONTROL POINT FOR SPECIAL INSTALLATIONS
Consists of:
router interface switchboard and supervisor;
quota part of the computer for supervision;
graphic for mapping controlled devices and for status visualization of status/alarm;
licence.
Control points are specificially indicated in special paragraph Address Points
BMS input/output address point for safety systems
| OUTDOOR AREA - BMS |  | 1
| Total amount |  | 1
TOTAL 16 - IMP SUPERVISIONE E CONTROLLO CENTRALIZZATO
TOTAL SPECIAL PLANTS - OUTDOOR AREAS
02 | SPECIAL PLANTS - UNDERGROUND AND SUBSTATIONS
01 - CONDUCTORS, CABLES AND ACCESSORIES
A230.A10.A22 | FTG10M1 0,6/1kV CEI 20-45 FIREPROOF CABLE | m
CABLE FTG10M1 0,6/1kV CEI 20-45, FTG10OM1 0,6/1kV CEI 20-45
Compliance with standards: CEI 20-22/3, 20-38, 20-45 and subsequent amendments and variations; EN50200.
Nominal voltage: 600/1000 V.
Insulator: a compound of ethylene-propylene rubber quality G10.
Coating: from a special thermoplastic polymer quality M1.
Filling: non-toxic rubber.
Conductor: flexible wire of coated copper coated with fireproof tape.
Behavior on the fire:
_does not spread flame;
_low emission of smoke, toxic and corrrosive gases;
_continuous work of minimum 180 minutes on the temperature 750°C in the presence of mechanical shock on every 5 min.
FTG10M1 0,6/1kV CEI 20-45 fire resistance cable 2x2.5 mmq
| UNDERGROUND LEVEL - CONDUCTORS, CABLES AND ACCESSORIES |  | 460
| Total amount |  | 460
A230.A10.A23 | FTG10M1 0,6/1kV CEI 20-45 FIREPROOF CABLE | m
CABLE FTG10M1 0,6/1kV CEI 20-45, FTG10OM1 0,6/1kV CEI 20-45
Compliance with standards: CEI 20-22/3, 20-38, 20-45 and subsequent amendments and variations; EN50200.
Nominal voltage: 600/1000 V.
Insulator: a compound of ethylene-propylene rubber quality G10.
Coating: from a special thermoplastic polymer quality M1.
Filling: non-toxic rubber.
Conductor: flexible wire of coated copper coated with fire resistance tape.
Behavior on the fire:
_does not spread flame;
_low emission of smoke, toxic and corrrosive gases;
_continuous work of minimum 180 minutes on the temperature 750°C in the presence of mechanical shock on every 5 min.
FTG10M1 0,6/1kV CEI 20-45 fire resistance cable 2x4 mmq
| UNDERGROUND LEVEL - CONDUCTORS, CABLES AND ACCESSORIES |  | 20
| Total amount |  | 20
A310.A22.A1 | CABLE FOR DATA TRANSIMISSION CAT.6a | m
CABLE FOR DATA TRANSIMISSION CAT.6A
Compliance with standards: ISO/IEC 11801- 2^ August edition 2002. andcompliance with requests of Addendum 1 - February 2008. (New Standard Cat. 6A Class EA), CEI 20-35, IEC 60332.1, CEI 20-22, CEI 20-37, IEC 61034, NES 713, IEC 60754.
Copper LSZH cable coated in four pairs Cat. 6A SFTP with following characteristics:
_the external layer flame resistant and low content of halogen gases L.S.0.H.;
_nominal impedance of 100 Ohm, covered intertwined pair (SFTP) with four intertwined pairs;
_diameter of copper conductor 23 AWG;
_Characteristics of maximum signal attenuation [dB] at different frequencies [MHz]:
* 1MHz: 4dB;
* 10 MHz: 6,4 dB;
* 100 MHz: 20,8dB;
* 200 MHz: 30 dB;
* 500 MHz: 49,3 dB.
_ Characteristics of paradijafonije NEXT [dB] on various frenquencies [MHz]:
* 1MHz: 674dB;
* 10 MHz: 58,6 dB;
* 100 MHz: 41,9dB;
* 200 MHz: 36,8 dB;
* 500 MHz: 29,9 dB.
Behavior on the fire:
_ does not spread flame;
_ low emission of smoke, toxic and corrrosive gases.
Cable FTP 4x2xAWG24 cat.6a
| UNDERGROUND LEVEL - CONDUCTORS, CABLES AND ACCESSORIES |  | 432
| Total amount |  | 432
A310.A31.A2 | SINGLE-MODE OPTICAL FIBRES OS1 LOOSE TUBE | m
Compliance with standards: ITU-T Rec G652 C; IEC 60793-2-50 tip B 1.3; CEI 20-38.
Conductor for external, made ​​of fibers coated with protection 250micron loose type (loose).
External cover: polyethylene of high density.
Mechanical characteristics:
_ filling: gel which provides fibre protection on the entrance from moisture and other external impacts;
_ mechanical protection: glass yarn or other material deposited around the pipes that carry fiber against the effects of small rodents, the type for external;
_ effort for maximum drive: 1000N;
_minimal resistance to crushing: 200N/cm.
Optical fibres: single-mode type OS1 od 9/125 micron for transmission support 1Gb/s up to 9000m.
Maximal attenuation per km:
- 1310nm; 0.4 dB;
- 1550nm: 0.4 dB.
Behavior on the fire:
_ does not spread flame;
_ low emission of smoke, toxic and corrrosive gases LSZH.
6 OS1 fiber optic cable
| UNDERGROUND LEVEL - CONDUCTORS, CABLES AND ACCESSORIES |  | 108
| Total amount |  | 108
TOTAL CONDUCTORS, CABLES AND ACCESSORIES
02 - CONDUITS FOR CABLES
B10.A10.A24 | METAL TRUNKING IN CLOSED VERSION, ZINC PLATED | m
SUPPORTING STRUCTURE FOR CABLES MADE OF HOT-DIP GALVANIZED STEEL FOR DROWNING AFTER TREATMENT
Compliance with standards: CEI 23-76, CEI 7-6 and subsequent variations.
Impact resistance: > 1J on room temperature (20°C ±5).
Mechanical resistance: minimum allowed load (values ​​measured for maximum arrow 1/200 medium capacity, the composition at 1/5 of the opening) measured in accordance with the appropriate performance standards:
_ closed channel with h. 75mm, light between two supporters 1,5m:
* 145 kg/m for channels wide 50-75 mm;
* 149 kg/m for channels wide 100 mm;
* 158 kg/m for channels wide 150 mm;
* 165 kg/m for channels wide 200 mm;
* 204 kg/m for channels wide 300 mm;
* 208 kg/m for channels wide 400 mm;
* 214 kg/m for channels wide 500-600 mm;
_ hollow channel with h. 75mm, light between two supporters 1,5m:
* 145 kg/m for channels wide 50-75 mm;
* 156 kg/m for channels wide 100 mm;
* 170 kg/m for channels wide 150 mm;
* 190 kg/m for channels wide 200-300 mm;
* 201 kg/m for channels wide 400 mm;
* 208 kg/m for channels wide 500 mm;
* 217 kg/m for channels wide 600 mm.
Electrical characteristics:
_ electric continuity guaranteed by the constructor with the electrical resistance (at 12V max ca 50Hz, 25A) = <0.005 ohm per meter <= 0.05 ohm nearby compound.
Structural characteristics:
_ body made ​​of one piece of sheet metal, hollow or closed, depending on the types, with rounded edges or reinforced edges against cut obtained by rolling and galvanized on fire after processing zinc quality Zn B132 A 99.90%;
_thickness of sheet metal: min.0,8 mm (up to 150x75) and 1 mm and over (for larger widths);
_ average thickness of zinc layer: 57 micron +/-10% for individual front side;
_ average mass of zink layer: 400 g/m2 +/-10% for individual front side;
_ cover (when required) of galvanized steel with the same treatment and structural characteristics of s.d., with the closure with the latch, i.e. by hook that can not be lost.
Protection level (in case of constructions with permanent full-bottom / closed and with a cover): min. IP30 for the entire system.
Metal trunking cover 200 mm
| UNDERGROUND LEVEL - CONDUITS FOR CABLES |  | 268
| Total amount |  | 268
B10.A10.A31 | METAL TRUNKING IN CLOSED VERSION, ZINC PLATED | m
SUPPORTING STRUCTURE FOR CABLES MADE OF HOT-DIP GALVANIZED STEEL FOR DROWNING AFTER TREATMENT
Compliance with standards: CEI 23-76, CEI 7-6 and subsequent variations.
Impact resistance: > 1J on room temperature (20°C ±5).
Mechanical resistance: minimum allowed load (values ​​measured for maximum arrow 1/200 medium capacity, the composition at 1/5 of the opening) measured in accordance with the appropriate performance standards:
_ closed channel with h. 75mm, light between two supporters 1,5m:
* 145 kg/m for channels wide 50-75 mm;
* 149 kg/m for channels wide 100 mm;
* 158 kg/m for channels wide 150 mm;
* 165 kg/m for channels wide 200 mm;
* 204 kg/m for channels wide 300 mm;
* 208 kg/m for channels wide 400 mm;
* 214 kg/m for channels wide 500-600 mm;
_ hollow channel with h. 75mm, light between two supporters 1,5m:
* 145 kg/m for channels wide 50-75 mm;
* 156 kg/m for channels wide 100 mm;
* 170 kg/m for channels wide 150 mm;
* 190 kg/m for channels wide 200-300 mm;
* 201 kg/m for channels wide 400 mm;
* 208 kg/m for channels wide 500 mm;
* 217 kg/m for channels wide 600 mm.
Electrical characteristics:
_ electric continuity guaranteed by the constructor with the electrical resistance (at 12V max ca 50Hz, 25A) = <0.005 ohm per meter <= 0.05 ohm nearby compound.
Structural characteristics:
_ body made ​​of one piece of sheet metal, hollow or closed, depending on the types, with rounded edges and reinforced edges against cut obtained by rolling and galvanized on fire after processing zinc quality Zn B132 A 99.90%;
_thickness of sheet metal: min.0,8 mm (up to 150x75) and 1 mm and over (for larger widths);
_ average thickness of zinc layer: 57 micron +/-10% for individual front side;
_ average mass of zink layer: 400 g/m2 +/-10% for individual front side;
_ cover (when required) of galvanized steel with the same treatment and structural characteristics of s.d., with the closure with the latch, i.e. by hook that can not be lost.
Protection level (in case of constructions with permanent full-bottom / closed and with a cover): min. IP30 for the entire system.
Divider H=75 mmm
| UNDERGROUND LEVEL - CONDUITS FOR CABLES |  | 268
| Total amount |  | 268
B10.A10.A4 | METAL TRUNKING IN CLOSED VERSION, ZINC PLATED | m
SUPPORTING STRUCTURE FOR CABLES MADE OF HOT-DIP GALVANIZED STEEL FOR DROWNING AFTER TREATMENT
Compliance with standards: CEI 23-76, CEI 7-6 and subsequent variations.
Impact resistance: > 1J on room temperature (20°C ±5).
Mechanical resistance: minimum allowed load (values ​​measured for maximum arrow 1/200 medium capacity, the composition at 1/5 of the opening) measured in accordance with the appropriate performance standards:
_constructions with h. 50 mm, light between two supporters 1,5m;
* 18 kg/m for channels wide 50-100 mm;
* 27 kg/m for channels wide 150 mm;
* 33 kg/m for channels wide 200 mm;
* 63 kg/m for channels wide 300 mm;
* 104 kg/m for channels wide 400 mm;
* 120 kg/m for channels wide 500-600 mm;
_ constructions with h. 100mm, light between two supporters 1,5m:
* 37 kg/m for channels wide 100 mm;
* 53 kg/m for channels wide 150 mm;
* 73 kg/m for channels wide 200 mm;
* 104 kg/m for channels wide 300-400 mm; * 125 kg/m for channels wide 500-600 mm.
Electrical characteristics:
_ electric continuity guaranteed by the constructor with the electrical resistance (at 12V max ca 50Hz, 25A) = <0.005 ohm per meter <= 0.05 ohm nearby compound.
Structural characteristics:
_structure is made of welded steel wire, hot-dipped galvanized for drowning after treatment with prior degreasing and pickling, and the final painting (for types that are required) epoxy resin or polyester;
_ safety edge without parts that contains sharp edges;
_ minimum mass of zink layer: 330 g/m2 +/-10%;
_ average thickness of zink layer: 50 micron +/- 10%.
_ cover (when required) of galvanized steel with the same treatment and structural characteristics of s.d., with the closure with the latch, i.e. by hook that can not be lost.
Protection level (in the case of full continue bottom /closed and with cover): min. IP30, for the entire system.
Zinc plated metal trunking, perforated base, size 200x75mm
| UNDERGROUND LEVEL - CONDUITS FOR CABLES |  | 268
| Total amount |  | 268
B10.A40.A12 | ZINC PLATED WIRE MESH | m
CONSTRUCTION FOR CABLES MADEOF HOT-DIP GALVANIZED STEEL FOR DROWNING AFTER TREATMENT
Compliance with standards: CEI 23-76, CEI 7-6 and subsequent variations.
Impact resistance: > 1J on room temperature (20°C ±5).
Mechanical resistance: minimum allowed load (values ​​measured for maximum arrow 1/200 medium capacity, the composition at 1/5 of the opening) measured in accordance with the appropriate performance standards:
_ constructions with h. 50mm, light between two supporters 1,5m:
* 18 kg/m for channels wide 50-100 mm;
* 27 kg/m for channels wide 150 mm;
* 33 kg/m for channels wide 200 mm;
* 63 kg/m for channels wide 300 mm;
* 104 kg/m for channels wide 400 mm;
* 120 kg/m for channels wide 500-600 mm;
_ constructions with h. 100 mm, light between two supporters 1,5m:
* 37 kg/m for channels wide 100 mm;
* 53 kg/m for channels wide 150 mm;
* 73 kg/m for channels wide 200 mm;
* 104 kg/m for channels wide 300-400 mm; * 125 kg/m for channels wide 500-600 mm.
Electrical characteristics:
_ electric continuity guaranteed by the constructor with the electrical resistance (at 12V max ca 50Hz, 25A) = <0.005 ohm per meter <= 0.05 ohm nearby compound.
Structural characteristics:
_structure is made of welded steel wire, hot-dipped galvanized for drowning after treatment with prior degreasing and pickling, and the final painting (for types that are required) epoxy resin or polyester;
_ safety edge without parts that contains sharp edges;
_ minimum mass of zink layer: 330 g/m2 +/-10%;
_ average thickness of zink layer: 50 micron +/- 10%.
_ cover (when required) of galvanized steel with the same treatment and structural characteristics of s.d., with the closure with the latch, i.e. by hook that can not be lost.
Behavior on the fire collor (upon request) auto extinguishing.
Zinc plated wire mesh, size 100x105mm
| UNDERGROUND LEVEL - CONDUITS FOR CABLES |  | 11
| Total amount |  | 11
B10.A40.A14 | ZINC PLATED WIRE MESH | m
CONSTRUCTION FOR CABLES MADEOF HOT-DIP GALVANIZED STEEL FOR DROWNING AFTER TREATMENT
Compliance with standards: CEI 23-76, CEI 7-6 and subsequent variations.
Impact resistance: > 1J on room temperature (20°C ±5).
Mechanical resistance: minimum allowed load (values ​​measured for maximum arrow 1/200 medium capacity, the composition at 1/5 of the opening) measured in accordance with the appropriate performance standards:
_ constructions with h. 50mm, light between two supporters 1,5m:
* 18 kg/m for channels wide 50-100 mm;
* 27 kg/m for channels wide 150 mm;
* 33 kg/m for channels wide 200 mm;
* 63 kg/m for channels wide 300 mm;
* 104 kg/m for channels wide 400 mm;
* 120 kg/m for channels wide 500-600 mm;
_ constructions with h. 100 mm, light between two supporters 1,5m:
* 37 kg/m for channels wide 100 mm;
* 53 kg/m for channels wide 150 mm;
* 73 kg/m for channels wide 200 mm;
* 104 kg/m for channels wide 300-400 mm; * 125 kg/m for channels wide 500-600 mm.
Electrical characteristics:
_ electric continuity guaranteed by the constructor with the electrical resistance (at 12V max ca 50Hz, 25A) = <0.005 ohm per meter <= 0.05 ohm nearby compound.
Structural characteristics:
_structure is made of welded steel wire, hot-dipped galvanized for drowning after treatment with prior degreasing and pickling, and the final painting (for types that are required) epoxy resin or polyester;
_ safety edge without parts that contains sharp edges;
_ minimum mass of zink layer: 330 g/m2 +/-10%;
_ average thickness of zink layer: 50 micron +/- 10%.
_ cover (when required) of galvanized steel with the same treatment and structural characteristics of s.d., with the closure with the latch, i.e. by hook that can not be lost.
Behavior on the fire collor (upon request) auto extinguishing.
Zinc plated wire mesh, size 200x105mm
| UNDERGROUND LEVEL - CONDUITS FOR CABLES |  | 14
| Total amount |  | 14
B10.A40.A3 | ZINC PLATED WIRE MESH | m
CONSTRUCTION FOR CABLES MADEOF HOT-DIP GALVANIZED STEEL FOR DROWNING AFTER TREATMENT
Compliance with standards: CEI 23-76, CEI 7-6 and subsequent variations.
Impact resistance: > 1J on room temperature (20°C ±5).
Mechanical resistance: minimum allowed load (values ​​measured for maximum arrow 1/200 medium capacity, the composition at 1/5 of the opening) measured in accordance with the appropriate performance standards:
_ constructions with h. 50mm, light between two supporters 1,5m:
* 18 kg/m for channels wide 50-100 mm;
* 27 kg/m for channels wide 150 mm;
* 33 kg/m for channels wide 200 mm;
* 63 kg/m for channels wide 300 mm;
* 104 kg/m for channels wide 400 mm;
* 120 kg/m for channels wide 500-600 mm;
_ constructions with h. 100 mm, light between two supporters 1,5m:
* 37 kg/m for channels wide 100 mm;
* 53 kg/m for channels wide 150 mm;
* 73 kg/m for channels wide 200 mm;
* 104 kg/m for channels wide 300-400 mm; * 125 kg/m for channels wide 500-600 mm.
Electrical characteristics:
_ electric continuity guaranteed by the constructor with the electrical resistance (at 12V max ca 50Hz, 25A) = <0.005 ohm per meter <= 0.05 ohm nearby compound.
Structural characteristics:
_structure is made of welded steel wire, hot-dipped galvanized for drowning after treatment with prior degreasing and pickling, and the final painting (for types that are required) epoxy resin or polyester;
_ safety edge without parts that contains sharp edges;
_ minimum mass of zink layer: 330 g/m2 +/-10%;
_ average thickness of zink layer: 50 micron +/- 10%.
_ cover (when required) of galvanized steel with the same treatment and structural characteristics of s.d., with the closure with the latch, i.e. by hook that can not be lost.
Behavior on the fire collor (upon request) auto extinguishing.
Zinc plated wire mesh, size 150x55mm
| UNDERGROUND LEVEL - CONDUITS FOR CABLES |  | 44
| Total amount |  | 44
B10.A40.A4 | ZINC PLATED WIRE MESH | m
CONSTRUCTION FOR CABLES MADE OF HOT-DIP GALVANIZED STEEL FOR DROWNING AFTER TREATMENT
Compliance with standards: CEI 23-76, CEI 7-6 and subsequent variations.
Impact resistance: > 1J on room temperature (20°C ±5).
Mechanical resistance: minimum allowed load (values ​​measured for maximum arrow 1/200 medium capacity, the composition at 1/5 of the opening) measured in accordance with the appropriate performance standards:
_ constructions with h. 50mm, light between two supporters 1,5m:
* 18 kg/m for channels wide 50-100 mm;
* 27 kg/m for channels wide 150 mm;
* 33 kg/m for channels wide 200 mm;
* 63 kg/m for channels wide 300 mm;
* 104 kg/m for channels wide 400 mm;
* 120 kg/m for channels wide 500-600 mm;
_ constructions with h. 100 mm, light between two supporters 1,5m:
* 37 kg/m for channels wide 100 mm;
* 53 kg/m for channels wide 150 mm;
* 73 kg/m for channels wide 200 mm;
* 104 kg/m for channels wide 300-400 mm; * 125 kg/m for channels wide 500-600 mm.
Electrical characteristics:
_ electric continuity guaranteed by the constructor with the electrical resistance (at 12V max ca 50Hz, 25A) = <0.005 ohm per meter <= 0.05 ohm nearby compound.
Structural characteristics:
_structure is made of welded steel wire, hot-dipped galvanized for drowning after treatment with prior degreasing and pickling, and the final painting (for types that are required) epoxy resin or polyester;
_ safety edge without parts that contains sharp edges;
_ minimum mass of zink layer: 330 g/m2 +/-10%;
_ average thickness of zink layer: 50 micron +/- 10%.
_ cover (when required) of galvanized steel with the same treatment and structural characteristics of s.d., with the closure with the latch, i.e. by hook that can not be lost.
Behavior on the fire collor (upon request) auto extinguishing .
Zinc plated wire mesh, size 200x55mm
| UNDERGROUND LEVEL - CONDUITS FOR CABLES |  | 16
| Total amount |  | 16
B10.A40.A51 | ZINC PLATED WIRE MESH | m
CONSTRUCTION FOR CABLES MADE OF HOT-DIP GALVANIZED STEEL FOR DROWNING AFTER TREATMENT
Compliance with standards: CEI 23-76, CEI 7-6 and subsequent variations.
Impact resistance: > 1J on room temperature (20°C ±5).
Mechanical resistance: minimum allowed load (values ​​measured for maximum arrow 1/200 medium capacity, the composition at 1/5 of the opening) measured in accordance with the appropriate performance standards:
_ constructions with h. 50mm, light between two supporters 1,5m:
* 18 kg/m for channels wide 50-100 mm;
* 27 kg/m for channels wide 150 mm;
* 33 kg/m for channels wide 200 mm;
* 63 kg/m for channels wide 300 mm;
* 104 kg/m for channels wide 400 mm;
* 120 kg/m for channels wide 500-600 mm;
_ constructions with h. 100 mm, light between two supporters 1,5m:
* 37 kg/m for channels wide 100 mm;
* 53 kg/m for channels wide 150 mm;
* 73 kg/m for channels wide 200 mm;
* 104 kg/m for channels wide 300-400 mm; * 125 kg/m for channels wide 500-600 mm.
Electrical characteristics:
_ electric continuity guaranteed by the constructor with the electrical resistance (at 12V max ca 50Hz, 25A) = <0.005 ohm per meter <= 0.05 ohm nearby compound.
Structural characteristics:
_structure is made of welded steel wire, hot-dipped galvanized for drowning after treatment with prior degreasing and pickling, and the final painting (for types that are required) epoxy resin or polyester;
_ safety edge without parts that contains sharp edges;
_ minimum mass of zink layer: 330 g/m2 +/-10%;
_ average thickness of zink layer: 50 micron +/- 10%.
_ cover (when required) of galvanized steel with the same treatment and structural characteristics of s.d., with the closure with the latch, i.e. by hook that can not be lost.
Behavior on the fire collor (upon request) auto extinguishing.
Divider, H = 55 mm
| UNDERGROUND LEVEL - CONDUITS FOR CABLES |  | 16
| Total amount |  | 16
B10.A40.A6 | ZINC PLATED WIRE MESH | m
CONSTRUCTION FOR CABLES MADE OF HOT-DIP GALVANIZED STEEL FOR DROWNING AFTER TREATMENT
Compliance with standards: CEI 23-76, CEI 7-6 and subsequent variations.
Impact resistance: > 1J on room temperature (20°C ±5).
Mechanical resistance: minimum allowed load (values ​​measured for maximum arrow 1/200 medium capacity, the composition at 1/5 of the opening) measured in accordance with the appropriate performance standards:
_ constructions with h. 50mm, light between two supporters 1,5m:
* 18 kg/m for channels wide 50-100 mm;
* 27 kg/m for channels wide 150 mm;
* 33 kg/m for channels wide 200 mm;
* 63 kg/m for channels wide 300 mm;
* 104 kg/m for channels wide 400 mm;
* 120 kg/m for channels wide 500-600 mm;
_ constructions with h. 100 mm, light between two supporters 1,5m:
* 37 kg/m for channels wide 100 mm;
* 53 kg/m for channels wide 150 mm;
* 73 kg/m for channels wide 200 mm;
* 104 kg/m for channels wide 300-400 mm; * 125 kg/m for channels wide 500-600 mm.
Electrical characteristics:
_ electric continuity guaranteed by the constructor with the electrical resistance (at 12V max ca 50Hz, 25A) = <0.005 ohm per meter <= 0.05 ohm nearby compound.
Structural characteristics:
_structure is made of welded steel wire, hot-dipped galvanized for drowning after treatment with prior degreasing and pickling, and the final painting (for types that are required) epoxy resin or polyester;
_ safety edge without parts that contains sharp edges;
_ minimum mass of zink layer: 330 g/m2 +/-10%;
_ average thickness of zink layer: 50 micron +/- 10%.
_ cover (when required) of galvanized steel with the same treatment and structural characteristics of s.d., with the closure with the latch, i.e. by hook that can not be lost.
Behavior on the fire collor (upon request) auto extinguishing.
Zinc plated wire mesh, size 400x55mm
| UNDERGROUND LEVEL - CONDUITS FOR CABLES |  | 6
| Total amount |  | 6
B30.A20.A25 | PVC RIGID PIPE | m
PROTECTIVE MEDIUM RIGID INSTALLATION PVC PIPE OR FOR SETTING ON THE WALL
Compliance with standards: 23-51, 23-54 and subsequent variations.
Compliance with tables: CEI-UNEL 37118, 37119, 37120.
Classification: not less than 3321.
Tread resistence: >= 750N.
Impact resistance: >= 2J.
Electrical resistance of insulation: >= 100Mohm on 500V for 1 min.
Dielectric rigidity: >= 2kV/mm na 50Hz za 15 min.
Behavior on the fire:
_ does not spread flame;
_ low content of halogen gases (in accordance with CEI 20-37).
System level protection: indicated in types.
PVC rigid pipe IP65 D=40mm
| UNDERGROUND LEVEL - CONDUITS FOR CABLES |  | 288
| Total amount |  | 288
B50.A20.A5 | PEHD FLEXIBLE PIPE TO BURY | m
PROTECTIVE FLEXIBLE PIPE OF HIGH-DENSITY POLYETHYLENE FOR LAYING UNDERGROUND
Compliance with standards: CEI 23-39, 23-46 and subsequent variations.
Classification: not less than 3441.
Tread resistance: >= 450N.
Impact resistance: >= 6J.
Dialectric resistance of insulator : >= 100Mohm.
Dialectric rigidity: >= 20kV/mm.
Resistance to chemical agents and effect of micro-organisms.
Structural characteristics:
_ pipe of high density polyethylene (HDPE), double-walled, smooth on the inside and corrugated on the outside;
_ joint for connecting multiple elements.
System level protection: min. IP4X.
PEHD flexible pipe D=110mm
| UNDERGROUND LEVEL - CONDUITS FOR CABLES |  | 230
| UNDERGROUND LEVEL - CONDUITS FOR CABLES |  | 14
| Total amount |  | 244
CE.A11.A4 | PREFABRICATED CONCRETE BOX | n
PREFABRICATED CONCRETE BOX FOR INSTALLATION INTO ROAD
Prefabricated concrete frame of vibrated reinforced concrete thickness of 6-8 cm for connecting pipes.
Total price includes:
_ costs associated with marking holes with fencing closure
forming a concrete surface ("lean concrete");
installation of frames with necessary protection.
The price does not include:
_ markings;
_ excavation.
Prefabricated concrete box size 60x60x60cm
| UNDERGROUND LEVEL - CONDUITS FOR CABLES |  | 4
| Total amount |  | 4
CE.C10.A45 | CAST IRON COVER | n
SPHEROIDAL CAST IRON COVER
Spheroidal cast iron cover made of frame for strengthening and cover.
Compliance with standard: UNI EN 124
Compliance with tables: UNI 4544.
Resistance class (depending on the type):
_ B125 with tensile strength> = 125 kN (12.5 t) for the use on places like sidewalks, pedestrian zone occasionally opened for traffic, parking areas and multi-storey parking lots for vehicles;
_ C250 with tensile strength> = 250 kN (25 t) to be installed on the edges of streets that extend maximum 0.5 m on traffic lanes and up to 0.2 m on the sidewalks, street shoulders and parking lots for vehicles;
_ D400 with tensile strength>= 400 kN (40t) to be used in a places like traffic roads (regional and national roads), parking space for all types of vehicles.
Structural characteristics:
_ frame in the form of a square in the base and at the top which comprises of:
* perimetrical continuous external spatula on all four sides and rounded corners, with a width of not less than 20 mm in order to allow a better fastening of the base with a foundation;
* if required, the profile of the frame U shaped to prevent the penetration of liquids (hermetic type);
* elastomer seal against noise and against leaning, placed in the corresponding semicircular canal;
*section for the compound with the bottom of a closed system blockage of the cover in the open position at 110 ^;
* seat to accommodate closing system;
* bumps against slipping on the surface for stepping analog to cover;
_ square shaped cover which has:
* bumps against slipping;
* groove for the key for lifting;
* closure mechanism is made by means of a rotating circular zasovnice;
* appropriate supplement able to guarantee articulating frame and its opening with the possibility of drawing the cover;
* height: starting from 20 mm for resistance class B125, 40 for resistance class C250, 60mm za D400.
Treatment:
_ fixing the manhole with cement mortar of at least 2 cm thick, and the final sealing along the entire scope of the frame;
_ grounding screw (if the company requires it).
Markings: closures will have to have a legible and permanent mark that indicates:
_ connection with standard UNI EN 124;
_inscription on the central part of the cover, which describes sub-service (e.g. STREET LIGHTING) to be defined in the company;
_ resistance class;
_ standard and / or abbreviation of the constructor;
_ possible marking of compliance with a third certificated institution.
Cast iron cover for box 60x60cm, grade C250
| UNDERGROUND LEVEL - CONDUITS FOR CABLES |  | 4
| Total amount |  | 4
TOTAL CONDUITS FOR CABLES
08 - DISTRIBUTION TERMINALS AND CONNECTION POINTS
M30.A10.A1 | POWER SUPPLY | n
POSITIONS OF POWER CONNECTION
Power point of different users comprised of:
_ part of the quota of the transit box and junction box installed along the riser;
_ conductor starting from the junction box installed along the riser to the point of use (particularly calculated);
_ possible junction boxes and installation boxes
Typology cable for setting will have to be the one provided in the specification and shall be sized based on the actual absorbed power of devices (door / motorized canopy, cabinet permutators, etc..)
In the case of the use of existing or pre-designed networks only the cost of setting up the cables will be calculated.
In the case of delivery and launching of installation pipes themselves for cables and box, price of predisposition will also be calculated.
The materials that make up point must have characteristics indicated in the relevant sections of a given study
Wall embedded power with PVC flexible pipe and 2x1.5 cable
| UNDERGROUND LEVEL - DISTRIBUTION TERMINALS AND CONNECTION POINTS |  | 16
| UNDERGROUND LEVEL - DISTRIBUTION TERMINALS AND CONNECTION POINTS |  | 2
| Total amount |  | 18
TOTAL DISTRIBUTION TERMINALS AND CONNECTION POINTS
12 - SOUNDSPEAKER SYSTEM
Q100.A10.A1 | CONNECTION FOR SOUND SPEAKER | n
SOUND SPEAKER POINT EQUIVALENT
Equivalent point for the spread of sound, consists of:
_ part of quota of junction box installed in the riser;
_ installation pipes for cables that start from the junction box installed along the riser to the speakers (separately calculated);
_ the junction of the head terminal (unless otherwise indicated);
_ lines that start from the junction box installed along the riser to the speakers (types in which it is required);
_ final box (if necessary) with matching cover with a hole for the outlet and cable gland
In the case of point for the spread of sound for an audible alarm in accordance with EN 60849 will have to provide the following changes / additions:
_ junction terminals (unless otherwise indicated) of the ceramics;
_lines that start from the junction box installed along the riser to the speakers (types in which it is required) from cable FTG10(O)M1 CEI 20-45 fireproof;
_ protective fuses and fuse box, both made of ceramics
Connection for wall sound speaker with PVC flexible pipe and cables
| UNDERGROUND LEVEL - SOUNDSPEAKER SYSTEM |  | 10
| UNDERGROUND LEVEL - SOUNDSPEAKER SYSTEM |  | 1
| Total amount |  | 11
Q100.A10.A3 | CONNECTION FOR SOUND SPEAKER | n
SOUND SPEAKER POINT EQUIVALENT
Equivalent point for the spread of sound, consists of:
_ part of quota of junction box installed in the riser; usponski vod;
_ installation pipes for cables that start from the junction box installed along the riser to the speakers (separately calculated);
_ the junction of the head terminal (unless otherwise indicated);
_ lines that start from the junction box installed along the riser to the speakers (types in which it is required);
_ final box (if necessary) with matching cover with a hole for the outlet and cable gland kablovska uvodnica
In the case of point for the spread of sound for an audible alarm in accordance with EN 60849 will have to provide the following changes / additions:
_ junction terminals (unless otherwise indicated) of the ceramics;
_lines that start from the junction box installed along the riser to the speakers (types in which it is required) from cable FTG10(O)M1 CEI 20-45 fireproof;
_ protective fuses and fuse box, both made of ceramics
Connection for false ceiling sound speaker with PVC flexible pipe and cables
| UNDERGROUND LEVEL - SOUNDSPEAKER SYSTEM |  | 1
| Total amount |  | 1
Q100.A10.A5 | CONNECTION FOR SOUND SPEAKER | n
SOUND SPEAKER POINT EQUIVALENT
Equivalent point for the spread of sound, consists of:
_ part of quota of junction box installed in the riser; usponski vod;
_ installation pipes for cables that start from the junction box installed along the riser to the speakers (separately calculated);
_ the junction of the head terminal (unless otherwise indicated);
_ lines that start from the junction box installed along the riser to the speakers (types in which it is required);
_ final box (if necessary) with matching cover with a hole for the outlet and cable gland kablovska uvodnica
In the case of point for the spread of sound for an audible alarm in accordance with EN 60849 will have to provide the following changes / additions:
_ junction terminals (unless otherwise indicated) of the ceramics;
_lines that start from the junction box installed along the riser to the speakers (types in which it is required) from cable FTG10(O)M1 CEI 20-45 fireproof;
_ protective fuses and fuse box, both made of ceramics
Connection for wall sound speaker with PVC rigid pipe and cables
| UNDERGROUND LEVEL - SOUNDSPEAKER SYSTEM |  | 16
| Total amount |  | 16
Q20.A30.A1 | SPEAKERS | n
BUILT IN SOUND SYSTEM FOR DEVICES FOR AUDIBLE ALARM DISTRIBUTION
6 W 5" ceiling loudspeaker EN 54 with fire dome, metal
Ceiling loudspeaker specifically designed for use in buildings where performance of systems for voice evacuation announcements is governed by regulations.
It is designed for flush mounting in suspended ceiling
Ideal for even sound distribution.
The fire dome increases protection of the cable termination.
The driver unit is impregnated against moisture.
Ceramic terminal block
Thermal fuse.
Compliant with EN 54-24 standard
_ rated voltage: 100/70V;
_ impedance: at least 8 ohm;
_ IP protection: min IP32.
Constructive characteristics:
_dual cone speakers with wide frequency response and diffusion.
Ambient temperature -25 °C ... 55 °C
Rated Power 6 W
Transformer power taps 6 / 3 / 1,5 / 0,75 W
Material: Metal
Loudspeakers for flush mounting into suspended ceilings, power 6W
| UNDERGROUND LEVEL - SOUNDSPEAKER SYSTEM |  | 1
| Total amount |  | 1
Q20.A30.A2 | SPEAKERS | n
BUILT IN SOUND SYSTEM FOR DEVICES FOR AUDIBLE ALARM DISTRIBUTION
6 W 6.5" round wall or ceiling surface mount loudspeaker, metal
The loudspeaker for voice alarm made of powder-coated metal in white with high degree of efficiency and a high-quality 200 mm broadband loudspeaker chassis.
Can be installed on ceiling and walls, where recessed mounting is not possible.
Flat and elegant design for unobtrusive installations provided with a metal back plate.
The loudspeaker is equipped for highest security requirements with a ceramic terminal and a thermal fuse.
The Chassis is protected against moisture by impregnation. EN 54 luodspeaker offers a powerful sound besides the high safety standard.
Ambient temperature -20 °C ... 80 °C
Rated Power 10 W
Transformer power taps 10 / 6 / 3 / 1,5 W
Loudspeaker for wall mounting, power 10W
| UNDERGROUND LEVEL - SOUNDSPEAKER SYSTEM |  | 10
| UNDERGROUND LEVEL - SOUNDSPEAKER SYSTEM |  | 1
| Total amount |  | 11
Q20.A35.A1 | SIREN - SPEAKER | n
SPEAKER IN THE FORM OF THE HORN MADE OF THERMOPLASTIC MATERIAL
HORN LOUDSPEAKER EN 54, ABS
The horn loudspeaker offers a high sound pressure and long-lasting weather resistance, ideal for use in industrial projects, garages, etc
The IP 66 high protection class guarantees operational safety even under the most difficult conditions.
The loudspeaker is also equipped with a ceramic terminal block and a thermal fuse for increased safety.
The shock-resistant ABS enclosure according to UL94V0 ensures long-lasting stability.
A U-shaped non-corrosive universal bracket is enclosed for flexible mounting.
The cable connection is done without need for an additional junction box.
The flexible power adjustment can be easily done with the rotary switch on the back side of the loudspeaker.
The loudspeaker is also suitable for outdoors use.
The loudspeaker complies with standard BS 5859 Part 8, and is certified in accordance with EN 54 Part 24.
Ambient temperature -25 °C ... 55 °C
Rated Power 15 W
Transformer power taps 15 / 10 / 5 W
Type of protection IP 66
Material ABS
SIREN - wall mount loudspeaker, IP65, power 15W
| UNDERGROUND LEVEL - SOUNDSPEAKER SYSTEM |  | 16
| Total amount |  | 16
TOTAL SOUNDSPEAKER SYSTEM
13 - DEVICE FOR FIRE DETECTION
R10.A32.A1 | TERMIC ANALOG DETECTOR | n
Heat detectors shall be intelligent devices with integrated ASA algorithms for comparison with actual sensor signals ensuring reliable detection, FDNet communication
Detectors should fulfill and be approved to EN54-5.
In addition the detector shall include:
1. Selectable application specific ASA parameter sets.
2. Communication of 3 different danger levels for differentiated alarm activation.
3. Programmable time related switching of detector behavior.
4. The facility to detect if the detector is in an unsuitable environment and give a separate warning of such to the panel.
5. An internal self test facility to ensure correct operation of the thermal sensor & electronics. Faults shall be reported with separate signals to the control panel.
6. Redundant operation with twin thermal sensors.
7. An integral short circuit isolator.
8. A separately controllable remote indicator output for activation from this or other detectors.
9. An integral response indicator with 360° viewing angle.
10. Wireless communication device to facilitate testing; enable readout of current status and wiring diagnostics. In addition the detector shall give data on its length of time in service to aid scheduled maintenance routines.
11. Operation in the temperature ranges -25°C to + 65°C
12. EMC compatibility of 50V/m
| UNDERGROUND LEVEL - FIRE DETECTION |  | 80
| LV SUBSTATION - FIRE DETECTION |  | 1
| Total amount |  | 81
R10.A40.A1 | ADDRESSABLE SMOKE DETECTOR | n
ADDRESSABLE OPTICAL ANALOG DETECTOR
Optical smoke detectors shall incorporate Advanced Signal Analysis (ASA) whereby the signals from the detectors sensors are compared with a dynamic algorithm set thus enhancing detection speed and false alarm rejection. FDNet communication
Detectors should fulfill and be approved to EN54-7.
The detector shall have been designed to have high tolerance to dust, dirt, temperature fluctuations and air currents.
In addition the detector shall include:
1. Selectable application specific ASA parameter sets.
2. Programmable time related switching of detector behavior.
3. 3 different danger levels for differentiated alarm activation.
4. Compensation for the gradual build up of dust & dirt to ensure a consistent level of detection over time. When the detector reaches a point where it can no longer retain this consistent detection a separate warning signal shall be given to the control equipment.
5. The facility to detect if the detector is in an unsuitable environment and give a separate warning of such to the panel.
6. An internal self test facility to ensure correct operation of the optics & electronics. Faults will be reported with separate signals to the control panel.
7. An integral short circuit isolator.
8. A separately controllable remote indicator output for activation from this or other detectors.
9. An integral response indicator with 360° viewing angle.
10. Wireless communication device to facilitate testing; enable readout of current status and wiring diagnostics. In addition the detector shall give data on its length of time in service to aid scheduled maintenance routines.
11. Operation in the temperature ranges -10°C to + 60°C
12. EMC compatibility of 50V/m
| UNDERGROUND LEVEL - FIRE DETECTION |  | 18
| LV SUBSTATION - FIRE DETECTION |  | 5
| MV/LV SUBSTATION - FIRE DETECTION |  | 1
| UNDERGROUND LEVEL - FIRE DETECTION |  | 11
| Total amount |  | 35
R10.A50.A1 | RESPONSE INDICATOR | n
OPTICAL REPETITOR
Alarm indicators are connected to automatic fire detectors in order to indicate quickly the source of an alarm signal from detectors which are not easily accessible or visible.
Alarm indicators are connected to automatic fire detectors in order to indicate quickly the source of an alarm signal from detectors which are not easily accessible or visible
Alarm indicators are mounted with two screws either directly to a door frame
operating voltage:5-8 V c.c.;
protection level: min. IP55.
current ma 35mA
Connection terminals max 1.5mm2
Response led indicator
| UNDERGROUND LEVEL - FIRE DETECTION |  | 11
| LV SUBSTATION - FIRE DETECTION |  | 5
| UNDERGROUND LEVEL - FIRE DETECTION |  | 9
| Total amount |  | 25
R10.A52.A1 | OPTICAL ACOUSTIC WARNING TABLE | n
OPTICAL ACOUSTIC COMMAND TABLE FOR FIRE SIGNALIZATION
Compliance with standards: EN 54-3.
Electromechanical characteristics:
operating voltage: 20-30 V c.c.;
protection level: min. IP30 for indoor installations,IP65 for outdoor installation.
Structural characteristics:
body of self-extinguishing thermoplastic material with red front part with the inscription "FIREPROOF ALARM" or "ALARM FOR GAS";
optical and acoustic signals that can be adjusted (pulse or fixed);
acoustic signalization: min. 90db;
led for operating signalization;
rechargeable battery 24V.
Optical acoustic warning fire panel with self powering kit, indoor installation
| UNDERGROUND LEVEL - FIRE DETECTION |  | 7
| Total amount |  | 7
R10.A52.A2 | OPTICAL ACOUSTIC WARNING TABLE | n
OPTICAL ACOUSTIC COMMAND TABLE FOR FIRE SIGNALIZATION
Compliance with standards: EN 54-3.
Electromechanical characteristics:
operating voltage: 20-30 V c.c.;
protection level: min. IP30 for indoor installations,IP65 for outdoor installation.
Structural characteristics:
body of self-extinguishing thermoplastic material with red front part with the inscription "FIREPROOF ALARM" or "ALARM FOR GAS";
optical and acoustic signals that can be adjusted (pulse or fixed);
acoustic signalization: min. 90db;
led for operating signalization;
rechargeable battery 24V.
Optical acoustic warning fire panel with self powering kit, indoor installation
| UNDERGROUND LEVEL - FIRE DETECTION |  | 7
| Total amount |  | 7
R10.A52.A3 | OPTICAL ACOUSTIC WARNING TABLE | n
OPTICAL ACOUSTIC COMMAND TABLE FOR FIRE SIGNALIZATION
Compliance with standards: EN 54-3.
Electromechanical characteristics:
operating voltage: 20-30 V c.c.;
protection level: min. IP30 for indoor installations,IP65 for outdoor installation.
Structural characteristics:
body of self-extinguishing thermoplastic material with red front part with the inscription "FIREPROOF ALARM" or "ALARM FOR GAS";
optical and acoustic signals that can be adjusted (pulse or fixed);
acoustic signalization: min. 90db;
led for operating signalization;
rechargeable battery 24V.
Optical acoustic warning fire panel with self powering kit, indoor installation
| LV SUBSTATION - FIRE DETECTION |  | 1
| Total amount |  | 1
R10.A70.A1 | MANUAL CALL WARNING | n
MANUAL SWITCH FOR WARNING -BREAK A GLASS
Manual call points will be break glass and press button type suitable for surface mounting and approved to EN54-11 and EN54-17.
It shall be suitable for use in Hazardous Area Zones 0, 1 and 2 and zones 20, 21 and, 22. The call point shall include a test key feature for the rapid testing of the device without removing the glass. The call point shall also incorporate the following:
1. Alarm response indicator.
2. Facility for adding additional protective flap.
3. Wireless communication device to facilitate testing; enable readout of current status and wiring diagnostics.
4. Operating temperature: -35°C to + 70°C
5. An EMC Compatibility of at least 50V/m
6. Ingress protection of at least IP44 (IP64 with protection seal)
| UNDERGROUND LEVEL - FIRE DETECTION |  | 9
| MV/LV SUBSTATION - FIRE DETECTION |  | 1
| UNDERGROUND LEVEL - FIRE DETECTION |  | 1
| Total amount |  | 11
R10.A80.A2 | INPUT/OUTPUT MODULE FOR CONTROL AND RECEPTION | n
INTERFACE ANALOGICAL MODULE FOR DEVICE MANAGEMENT AND SIGNAL RECEPTION
Input / output modules shall comply with the requirements of and be approved to EN54-17.
Input / output modules should connect directly to the loop and not require further power supply connections.
Each input / output module shall take one address.
Input / output modules shall additionally include:
1. Inputs monitored for short & open circuit.
2. Inputs can be configured for normally open or normally closed operation.
3. Outputs to be rated at 250VAC 4A resistive & 30VDC 4A clean contacts.
4. Output to be selectable as continuous or as pulsed operation. Pulse duration to be selectable between 1 & 20 seconds.
5. Integral short circuit isolator.
6. LED indication of normal, fault, test, & activation conditions.
7. Module can be configured as fail safe.
8. Modules to be mounted in an IP66 housing with clear lid for device status indication.
9. Modules should additionally be suitable for DIN rail mounting.
10. Operating temperature: -25°C to +60°C
11. EMC compatibility: 50V/m
Analogical input module
| UNDERGROUND LEVEL - FIRE DETECTION |  | 6
| Total amount |  | 6
R10.A80.A4 | INPUT/OUTPUT MODULE FOR CONTROL AND RECEPTION | n
INTERFACE ANALOGICAL MODULE FOR DEVICE MANAGEMENT AND SIGNAL RECEPTION
Input / output modules shall comply with the requirements of and be approved to EN54-17.
Input / output modules should connect directly to the loop and not require further power supply connections.
Each input / output module shall take one address.
Input / output modules shall additionally include:
1. Inputs monitored for short & open circuit.
2. Inputs can be configured for normally open or normally closed operation.
3. Outputs to be rated at 250VAC 4A resistive & 30VDC 4A clean contacts.
4. Output to be selectable as continuous or as pulsed operation. Pulse duration to be selectable between 1 & 20 seconds.
5. Integral short circuit isolator.
6. LED indication of normal, fault, test, & activation conditions.
7. Module can be configured as fail safe.
8. Modules to be mounted in an IP66 housing with clear lid for device status indication.
9. Modules should additionally be suitable for DIN rail mounting.
10. Operating temperature: -25°C to +60°C
11. EMC compatibility: 50V/m
Analogical output module
| UNDERGROUND LEVEL - FIRE DETECTION |  | 25
| LV SUBSTATION - FIRE DETECTION |  | 1
| Total amount |  | 26
R100.A10.A11 | CONNECTING DETECTOR POSITIONS | n
EQUIVALENT DETECTION POINT
The average price per position detector (detection apparatus excluded) consists of:
_ lines for power supply and signal beginning of the zone switchboard to the detector made ​​of loop cable for detection resistant to fire for 30 minutes, 2 x 18AWG (diameter 1 mm);
_ junction boxes and transmission boxes installed on the channels of riser and inside the premises;
_ installation pipes for cable boxes from the riser to the device detection.
The place where the pipes go through the installation pipes for cables and the location of the detector are indicated in the graphics tables.
Equivalent point detection is estimated by the body via calculating of all apparatus (detectors, sensors keys, horns, synoptic tables and tables for signaling. etc..) and the subsequent attribution of some average value for each of them, and therefore the price should be used to connect any component.
Analogical detector point connection with PVC rigid pipe and cables
| UNDERGROUND LEVEL - FIRE DETECTION |  | 154
| LV SUBSTATION - FIRE DETECTION |  | 8
| MV/LV SUBSTATION - FIRE DETECTION |  | 1
| UNDERGROUND LEVEL - FIRE DETECTION |  | 1
| Total amount |  | 164
R100.A10.A2 | CONNECTING DETECTOR POSITIONS | n
EQUIVALENT DETECTION POINT
The average price per position detector (detection apparatus excluded) consists of:
_ lines for power supply and signal beginning of the zone switchboard until the detector made ​​of loop cable for detection resistant to fire for 30 minutes, 2 x 18AWG (diameter 1 mm);
_ junction boxes and transmission boxes installed on the channels of riser and inside the premises;
_ installation pipes for cable boxes from the riser to the device detection.
The place where the pipes go through the installation pipes for cables and the location of the detector are indicated in the graphic tables.
Equivalent point detection is estimated by the body via calculating of all apparatus (detectors, sensors keys, horns, synoptic tables and tables for signaling. etc..) and the subsequent attribution of some average value for each of them, and therefore the price should be used to connect any component.
Analogical detector point connection with PVC flexible pipe and cables
| UNDERGROUND LEVEL - FIRE DETECTION |  | 11
| UNDERGROUND LEVEL - FIRE DETECTION |  | 11
| Total amount |  | 22
R30.A22.A1 | ADDRESSABLE CO DETECTOR FOR PARKING | n
DETECTOR - CARBON MONOXIDE (CO) FOR PARKING
Technology 8 bits microprocessor and electrochemical sensor with filter for SOx/NOx/H2S
Voltage From 9V to 15V DC
Consumption 8mA (stand-by) 15mA (alarm).
Measurement range From 0 to 400 ppm
Resolution ±2 ppm
Reproductiveness 1% bottom of scale
Linearity Linear in all the scale
Calibration gas Precise mixture 200 ppm CO + N2 150 ml / min
Sensor life expectancy 4 years in normal working conditions
Relative humidity From 15% to 90% (continuous) & from 0% to 99%
(intermittent).
Atmospheric pressure ±10%.
Working temperature From –15ºC to +50ºC
Time response T90 < 40 s.
Cable entry PG9 stopping plug IP67 self-blocking
Communication RS485 addressable (1 to 16).
Protection grade IP65
Presentation ABS & Makrolon
Weight (gr) &
Dimensions (mm)
325 grs.
120-150-63 (including sensor head & cable entry)
Height of installation 1,8 - 2 m from floor
Cover 200 m2 (according with current standard).
Addressable carbon monoxide detector
| UNDERGROUND LEVEL - FIRE AND GAS DETECTION |  | 13
| Total amount |  | 13
R30.A23.A1 | ADDRESSABLE DETECTOR OF FLAMMABLE FUMES FROM PETROL FOR PARKINGS | n
DETECTOR OF FLAMMABLE FUMES FOR PARKINGS
Technology Microprocessor and catalytic sensor resistant to H2S
Voltage From 10V to 30V
Maximum consumption 60mA at 12V DC
Resolution 1% L.E.L. of measurement range
Measurement range 0-100% LEL (5% Vol. Methane)
Relative Humidity 0% al 90% without condensation
Working temperature From –10ºC to +50ºC
Cable entry PG9 stopping plug IP67 self-blocking
Protection grade IP65
Presentation Makrolon & ABS
Weight (gr) y Dimensions (mm) 288 gr aprox. / 120-150-63
| UNDERGROUND LEVEL - FIRE AND GAS DETECTION |  | 20
| Total amount |  | 20
TOTAL DEVICE FOR FIRE DETECTION
14 - BURGLAR SYSTEM, SYSTEM FOR ACCESS CONTROL AND CCTV SYSTEM
R20.A100.A1 | MODULE FOR DOOR CONTROL | n
UNIT FOR TRANSITION CONTROL
A Dual Reader Interface Module (DRIM) shall be available for each controlled door and provide the ability to connect up to two card readers or entry devices. This DRIM shall:
q Monitor the door position (door contact)
q Allow the connection of a Request-to-Exit (REX) switch for exit
q Control an electric door lock or strike
q Provide the facility for up to 3 auxiliary input devices to be connected
q Allow the connection of an alarm buzzer that can be triggered in the case of an alarm event, or more specifically locally trigger a buzzer for a door held event before this alarm is registered at the host.
All events that occur at the door must be reported from the DRIM to the ISC.
To allow for situations where an entry and exit reader may be required at the one door a DRIM will allow two readers to be connected. However, in circumstances where a door shall only require one reader the DRIM can be configured to operate in a two door mode, whereby a reader, door lock and door monitoring device can be connected for each door.
In addition, the DRIM shall also provide connection for single advanced reader that connects via an RS-485 or Wiegand / Clock/Data connections.
Finally, the DRIM shall also provide the ability to work offline in cases where communications with ISC has have been lost and still continue to accept a set of specified cards as being valid to the door(s) which it controls.
The device must contain all necessary power cables, Cat6 patch cable for connecting with vicinal cable systems, vertical cables, and all the necessary equipment for the professional completion of works.
Door control module
| UNDERGROUND LEVEL - BURGLAR SYSTEM, SYSTEM FOR ACCESS CONTROL AND CCTV SYSTEM |  | 9
| UNDERGROUND LEVEL - BURGLAR SYSTEM, SYSTEM FOR ACCESS CONTROL AND CCTV SYSTEM |  | 1
| Total amount |  | 10
R20.A102.A1 | PROXIMITY READER | n
TERMINAL FOR READER OF PROKSI CARDS
The terminal of proximity reader, which sends data to the peripheral unit, which controls the door to enable the operation of recognizing, authorization and executing commands of authorization.
 Transmission frequency 13.56 MHz
 The following card technologies are supported:
ISO14443-A:
 Mifare 1k and 4k (UID, S/B, MAD)
 Mifare UltraLight (UID, B)
 Mifare DesFire (UID)
 my-D proximity (UID, B) ISO14443-A+B
 my-C (UID) ISO15693:
 my-D vincinity (UID)
 I-Code SLI (UID)
 Tag-IT HFI (UID)
 LRI512 (UID)
 Configuration using configuration card or software tool
 Up to 7 cm read range, depending on mounting environment, card technology and card type
 DIP switch for functionality selection
 Flash memory for firmware updates
 Three-colour LED for status display and buzzer for audible signals
 Reader power from the power supply of the door controller
 "Touch and Go" operation
Proximity reader with code keypad
| UNDERGROUND LEVEL - BURGLAR SYSTEM, SYSTEM FOR ACCESS CONTROL AND CCTV SYSTEM |  | 10
| UNDERGROUND LEVEL - BURGLAR SYSTEM, SYSTEM FOR ACCESS CONTROL AND CCTV SYSTEM |  | 1
| Total amount |  | 11
R20.A80.A1 | KEY FOR LOCKING THE DOOR | n
COMMAND POINT FOR OPENING THE DOOR
Command point made of:
_ part of the quota distribution and junction box installed along the riser;
_ conductor starting from the junction box installed along the riser and mounting box;
_ prefabricated boxes,built in or on the wall, depending on the types, which they possess, if required, connections for installation pipes for cables;
_ modular command fuses that have the following characteristics:
* Compliance with standards: CEI 23-9 and subsequent variations;
* voltage and nominal frequency: 250V c.a., 50Hz;
* nominal power : 10A for buttons and 16A for switches;
* test voltage: 2000V on 50Hz for 1 min.;
*switching power: 200 performed opening and closing to 1.25 In, 275V CA, cosfi'0, 3;
* testing functioning: 50000 maneuvers In, 250V CA, cosfi'0, 6;
* resistance of insulation: >15Mohm for 500V.
The price should include the internal wiring between fuses.
Door locking pushbutton
| UNDERGROUND LEVEL - BURGLAR SYSTEM, SYSTEM FOR ACCESS CONTROL AND CCTV SYSTEM |  | 7
| UNDERGROUND LEVEL - BURGLAR SYSTEM, SYSTEM FOR ACCESS CONTROL AND CCTV SYSTEM |  | 1
| Total amount |  | 8
R40.A31.A1 | PASSIVE INFRARED DETECTOR | n
PASSIVE INFRARED DETECTOR
Supply voltage (12 V nom.)
– Max. ripple (0 … 100 Hz)
– Voltage monitoring
8.0 … 16.0 VDC
2.0 VPP
Alarm at < 5.5 … 7.5 V
Current consumption (at 8 …16 VDC)
– Quiescent / when alarm occurs (with LED)
2.8 mA / <10 mA
Alarm output, semiconductor relay 30 VDC / 100 mA / Ri <45 Ohm
Alarm holding time 2 … 3 s
Walktest indicator LED
Tamper contact 30 VDC / 100 mA
Control inputs LOW ≤1.5 V / HIGH ≥3.5 V
Walking speeds
– Wide angle / Curtain
0.1 … 4.0 m/s / 0.1 … 4.0 m/s
Ambient conditions
Operation temperature -20 … +55 °C
Storage temperature -20 … +60 °C
Humidity (EN60721) <95 % r.h., non condensing
EMI rejection up to 1 GHz / up to 2 GHz >30 V/m / >10 V/m
Housing protection EN60529, EN50102 IP41
Approvals VdS class B, wide angle: G 103506,
curtain: G 103507
| UNDERGROUND LEVEL - BURGLAR SYSTEM, SYSTEM FOR ACCESS CONTROL AND CCTV SYSTEM |  | 3
| UNDERGROUND LEVEL - BURGLAR SYSTEM, SYSTEM FOR ACCESS CONTROL AND CCTV SYSTEM |  | 1
| Total amount |  | 4
R40.A41.A1 | MAGNETIC CONTACT FOR DOOR CONTROL | n
BUILT MAGNETIC CONTACT FOR DOOR CONTROL
Approval: IMQ I Level
Electromechanical characteristics:
_ operating distance: min. 20 mm.
_ dimensions min: 34x diameter 20 mm.
Structural characteristics:
_ "cigarette" body made ​​of brass, for flush mounting on a metal door, including armored, equipped with mounts;"cigaret" tijelo od mesinga, za uzidno postavljanje na metalnim vratima, uključujući i blindirana, opremljeno i odbojnikom;
_ connection via 4 wires (n.1 pair for sensor and n.1 pair forsabotage).
Magnet contact for door control
| UNDERGROUND LEVEL - BURGLAR SYSTEM, SYSTEM FOR ACCESS CONTROL AND CCTV SYSTEM |  | 7
| UNDERGROUND LEVEL - BURGLAR SYSTEM, SYSTEM FOR ACCESS CONTROL AND CCTV SYSTEM |  | 2
| Total amount |  | 9
R40.A80.A1 | DEVICE FOR ADDRESSING ELEMENTS | n
ADDRESSABLE CARD
The I/O Expander shall enable 8 additional Alarm Inputs and 2 relay outputs (30V / 1A) to be added onto the BUS. The input types and the outputs shall be fully programmable. The PCB shall have an on-board buzzer, status LED; tamper switch and thermal fuse to protect auxiliary devices. Power to the I/O Expander shall be provided via the BUS cable from the controller or by locally based intelligent power supply units. The PCB shall be housed in a robust plastic enclosure.
The Alarm Inputs shall be capable of supporting a range of EOL resistor values to be able to take into account 3rd party legacy systems.
The Expanders may also be installed in the controller enclosure. This enclosure shall accommodate the standby battery, controller and I/O Expander(s).
Number of on-board zones 8
EOL resistor Dual 4k7 (default), other resistor combinations configurable
Number of on-board relays 2 (single-pole changeover, 30 VDC / max. 1 A resistive switching current)
Field bus X-BUS on RS-485 (307 kb/s)
Tamper contact Front spring tamper
Operating voltage 9.5 ~ 14 VDC
Operating temperature -10 ~ +50 °C
Standards / approval EN50131-1, Grade 3, class II
| UNDERGROUND LEVEL - BURGLAR SYSTEM, SYSTEM FOR ACCESS CONTROL AND CCTV SYSTEM |  | 7
| UNDERGROUND LEVEL - BURGLAR SYSTEM, SYSTEM FOR ACCESS CONTROL AND CCTV SYSTEM |  | 2
| Total amount |  | 9
R50.A16.A1 | IP FIXED MINIDOME CAMERA PoE | n
FIXED IP MINIDOME COLOR CAMERA
Fixed telecamera minidome for installation on the false ceiling or on the wall, following characteristics:
case suitable for installation, with maximum cross-section ring 140 mm and height 128 mm;
_power supply PoE according to standard IEEE 802.3 af;
_communication with LAN Ethernet network, compatible to central recording system as well as central monitoring system (BMS - Desigo CC)
_with changing focus 3 - 9 mm;
_sensor CMOS with progressive scanning.
_multiple stream which can be indvidually configured H.264 i Motion JPEG;
_maximum resolution of at least SXGA 1,3MPixel, speed 12 fps. Possibility of sending at least two streaming videos, one for monitoring, and other for recording.
_possibility of picture rotation;
_resolution control of the picture: color, brightness, contrast, white level, etc.
_motion detection function and anti-tamper alarm;
_perfect integration with switchboard TVCC.
Camera must be equipped and installed with:
_patch cord on the side of the camera and on the side of rack;
_programming;
_softwer licence.
IP fixed camera minidome PoE for indoor/outdoor installation
| UNDERGROUND LEVEL - BURGLAR SYSTEM, SYSTEM FOR ACCESS CONTROL AND CCTV SYSTEM |  | 4
| Total amount |  | 4
R60.A70.A1 | KEYBOARD FOR TURNING OFF BURGLAR ALARM | n
ELECTRONIC KEY - KEYBOARD
The system Keypad(s) shall be remote from the controller and the system shall be capable of allowing up to 32 Keypads on each controller. The Keypad shall be configurable per User & per Area/Multiple Areas, allowing each User to see only the menu options or events that apply to that User/Area.
A range of systems keypads shall be available with options for optional display and control features.
The standard keypad range shall support the following features;
LCD display with 2 x lines of 16 characters to show all alert and warning messages with alphanumeric Keys to allow for both text and numeric data entry.
Soft function keys that can change function depending upon the menu selected.
The user shall be able to (Depending on user rights) System Set – Unset, Part A/B Set –Unset, Area Set –Unset.
The illumination shall be programmable to allow one of three states (Always on, always off or by Key press).
When multiple Keypads are used, the option to be able to silence the on board buzzer for quiet environments shall be capable of being deployed.
Integral EM proximity reader for keypad logon resp. setting / unsetting (PACE)
Local Wireless Access Point to support local wireless devices.
The enhanced keypad range shall have the following features;
Graphical LCD display with 128 x 64 dots providing space for alert and warning messages with alphanumeric Keys to allow for both text and numeric data entry.
Soft function keys (minimum of four) that can change function depending upon the mode of the system.
The user shall be able to (Depending on user rights) System Set – Unset, Part A/B Set –Unset, Area Set –Unset.
The illumination shall be programmable to allow one of three states (Always on, always off or by Keypress).
When multiple Keypads are used, the option to be able to silence the on board buzzer for quiet environments shall be capable of being deployed.
Integral EM proximity reader for keypad logon resp. setting / unsetting
Integral speaker to provide voice annunciation
Capable of displaying the installers logo
Capable of showing the status of four Areas / Partitions at any one time.
Support for locally attached key-switch and indication modules
The status of each Keypad on the system shall be viewable and this shall include;
Tamper status
Firmware Version
Input Voltage
Address ID
Capability to disable keypads based on various conditions
LCD-display 2 x 16 characters
Special keys 2 soft keys, 1 multi-dimensional navigation key
LED indicators 3 status LEDs
Card reader Integrated (125kHz, EM 4102)
Field bus X-BUS on RS-485 (307 kb/s)
Tamper contact Front / back spring tamper
Operating voltage 9.5 ~ 14 VDC
Operating temperature 5 ~ +40 °C
Standards / approval compliance EN50131-1, Grade 3, class II, SE: SFF1014, Larmklass 2, HU: MABISZ, CZ: TESTALARM, TREZORTEST,NBU
| UNDERGROUND LEVEL - BURGLAR SYSTEM, SYSTEM FOR ACCESS CONTROL AND CCTV SYSTEM |  | 2
| Total amount |  | 2
S60.A40.A3 | VIDEO-INTERCOM SYSTEM | n
VIDEO-INTERCOM SYSTEM
Električni digitalni video-interfonski portir sa dvije žice u stanju da obavi poziv sa spoljašnjih mjesta (ulazi u stambene zone) sa kamerom, posredstvom izbora sredstva željene tipke u unutrašnjosti.
Compliance with standards: CEI 12-13(88), 14-6(90)and subsequent variations; HD 195 S4.
The system will be composed of the following devices:
ELECTRONIC GROUP FOR POWER SUPPLY
_ nominal voltage and frequency: 230V c.a. +/-10%, 50Hz;
_ secondary outputs: 22V AC / 0,9 a continuous power supply of light on the panel with switches and resistance to overheating; 22V c.a. / 0,5 intermittent performance for power supply for sound,calls, the brightness of the recording place, the camera; monitor; 22V c.a./3A impulses for electric locks; 25V c.c. / 0.8 A intermittent performance for the interior premises,derivatives, etc..;
_ transformer power: 60VA;
_ group for decoding digitized calls for enabling dialed numbers;
_Structural characteristics :
*body of thermoplastic material of a modular structure suitable for installation on DIN or OMEGA guide inside the box frame or local plan (calculated separately) or on a wall zaporna kutija
* round protective cover of input terminals;
*Self-protection inputs and outputs through a fuse;
*transformer core is made of small sheet metals with low loss;
EXTERNAL DIGITAL VIDEO-INTERCOM SPACE
External space with modular elements (tile with indicated names, audio tile, tile with table with switches, tile for recording, boxes, frames, module carrier construction, etc.) suitable for creating various configurations, consisting of:
_ tiles of anodized aluminum in color selected by the company, or of light alloys obtained by casting under press, thickness min. 15mm, which are subjected to anti corrosion treatment, with a small glass which contains the name of the polycarbonate, notched burglar bolts with the head of a flat plate, anti-vandal version;zarezani protivprovalni zavrtnji sa glavom u ravni ploče, anti-vandal verzija;
_bricked in case made of thermoplastic material;
_ voice group:
* power supply: at least 6V c.c. +/-5%;
* level of noise in the background: < 30mV;
* body of thermoplastic material placed in the outer panel with switches;
* amplified microphone and speaker, with separate tone control in communications inward and outward;
_ recording group:
* camera made in technology CCD 1 / 4" color;
* power supply: 16-20V c.c.;
* apsorpcija: 400mA tokom funkcionisanja, 70mA tokom stand-by-a;
* video izlaz: moduliran na isprepletanom paru;
* starting time: < 6 sec.;
* screw for mechanical control of focus;
* screw for turning off the mechanical okluzinog element in the event of failure;
* installation (in the version included in an external site) vertical installation; (in separate version) on the wall or on the ceiling, with adjustable cramps and power supply point; where required, thermostat waterproof housing, with protection from penetration of rain;
INNER SPACE
* power supply 18-23 V c.c.;
* screen: LCD 3,5";
* activation time: < 6 sec.;
* range of video signals at the entrance: 0,5-1,5 V pp;
* vertical frequency: 50Hz synchronized with the network;
* activation time: at least 60 sec.;
* white body of thermoplastic material;
* microphone with spiral cable;
* unit for confidential conversations;
*ability of differential calls from the floor or from the outside;
* keys for the command of opening the door, turn on lights on the stairs, turn on the monitor from the inside, calling the switchboard (if required);
* differential regulation of the brightness and contrast;
* additional equipment for installation;
* appropriate measures in order to implement a simplified installation of the cable system;
* installation on the table or on the wall;
DERIVATOR OF VIDEO SIGNALS
Derivator of video signal, voice and data with low attenuation coefficient,for two-wire devices to separate the video signals, taken from a column of supporter, towards inside spaces.
ELECTRICAL LOCK
_ power supply: 12V c.a.
Outdoor video entry phone
| UNDERGROUND LEVEL - BURGLAR SYSTEM, SYSTEM FOR ACCESS CONTROL AND CCTV SYSTEM |  | 8
| Total amount |  | 8
TOTAL BURGLAR SYSTEM, SYSTEM FOR ACCESS CONTROL AND CCTV SYSTEM
11 - SYSTEMS FOR DATA TRANSMISSION AND TELEPHONE
X10.A10.A1 | RACK 19" FOR DATA COMMUNICATION | n
RACK 19" FOR SWITCHING
Compliance with standards: DIN 41488, 41494/1.
Structural characteristics:
_modular supporting structure is made of extruded profiles aluminum and angular elements that can be composed of living under the aluminum strainer;
_ roof, lateral, back and floor panel to cover the steel minimum thickness of 1.5 mm;
_ basic processing of sheet metal and structures obtained by electrophoresis color RAL 7044; finish painting with epoxy powder RAL 7035;
_ execution on the floor (equipped with screw-in part for the support of painted sheet metal) or on a wall, depending on how it is provided in graphic tables;
_ lateral and rear panels of blind type;
_ front panel blind type of painted steel or anodized aluminum, for the completion and closure of premises that are not used by setting;
_ front door of a transparent type with a frame whose edges on all sides are coated colored sheet; safety glass thickness min. 3mm; joints that are able to provide a door opening angle of at least 105 °, in the number 2 on the panel up to 1200mm, no. 3 h. from 1400 to 1600mm, no.4 by h. 1800 to 2000; point of closure on the side of hitting the same number of joints;
_ handle for closing with a unique key (if there is no lock that is controlled by access control system);
_ flexible grounding or earthing systems on all movable panels for sealing and sliding surfaces as well as in all the metallic elements that serve as support to active devices in the network;
_ shelves for placement of network devices from galvanized, perforated, painted steel, fixed or type to pull using groove for sliding made ​​of galvanized plated steel, which has a handle to pull the chrome galvanized steel;
_ box for placing a keyboard that has the same characteristics as pulling shelves , equipped with a folding vertical part of the step;
_ legs for control at the bottom with a lock-nut for blocking;
_ grids for ventilation with filter with fine grid against dust (if inside the panel there is no air conditioning system);
_ forced ventilation system with a load capacity of air 150mc / h installed on the roof (if inside the panel there is no air conditioning system) with power supply 230V + / -10% c.a. 50Hz, connected to the panel for power and managrd by the internal thermostat;
_ panel for power supply made of:
* no. 2 overall switches (input line UPS and output line UPS) automatic modular type 2x16 curve C, Pi 6kA, Id 30mA type A;
* no. .. 7 sockets of universal type (bipolar conflict with a hole in the earth at the center) to the axis of polarity leaned compared to to the axis of panels to be m + allow the use of all sockets without obstacles or interference on the cables that come out from within the plugs;
_ pocket for placing documents from hard plastic (excluding flexible transparent bags made ​​of nylon or similar) installed in panels or in a place defined by the company;
_ blind panels in at least 15% of available frontal surface (excluding ventilation panels and panels for power supply);
_ additional elements for setting cables such as:
* constructions for setting PVC cbales, which have spare space in the amount of at least 50% of the space they occupy;
* vertical cable management rings for every 25 cm height of the panels installed on both sides;
* round covers for covering strip, surge protectors, protective screens, etc.., for all of the devices and power supply parts in order to still guarantee a degree of protection not less than IP20 on open panels;
_ external level protection : IP40 or as indicated in graphic tables, including the bottom;
_ dimensions as described in the types with the indicated base in mm (width x depth) and height in units of standard 19 "(each unit corresponds to the size of 44.45 mm).
Communication data rack 19" 600x600mm 22U
| UNDERGROUND LEVEL - DATA TRANSMISSION AND TELEPHONE |  | 2
| Total amount |  | 2
X10.A10.A2 | RACK 19" FOR DATA COMMUNICATION | n
RACK 19" FOR SWITCHING
Compliance with standards: DIN 41488, 41494/1.
Structural characteristics:
_modular supporting structure is made of extruded profiles aluminum and angular elements that can be composed of living under the aluminum strainer;
_ roof, lateral, back and floor panel to cover the steel minimum thickness of 1.5 mm;
_ basic processing of sheet metal and structures obtained by electrophoresis color RAL 7044; finish painting with epoxy powder RAL 7035;
_ execution on the floor (equipped with screw-in part for the support of painted sheet metal) or on a wall, depending on how it is provided in graphic tables;
_ lateral and rear panels of blind type;
_ front panel blind type of painted steel or anodized aluminum, for the completion and closure of premises that are not used by setting;
_ front door of a transparent type with a frame whose edges on all sides are coated colored sheet; safety glass thickness min. 3mm; joints that are able to provide a door opening angle of at least 105 °, in the number 2 on the panel up to 1200mm, no. 3 h. from 1400 to 1600mm, no.4 by h. 1800 to 2000; point of closure on the side of hitting the same number of joints;
_ handle for closing with a unique key (if there is no lock that is controlled by access control system);
_ flexible grounding or earthing systems on all movable panels for sealing and sliding surfaces as well as in all the metallic elements that serve as support to active devices in the network;
_ shelves for placement of network devices from galvanized, perforated, painted steel, fixed or type to pull using groove for sliding made ​​of galvanized plated steel, which has a handle to pull the chrome galvanized steel;
_ box for placing a keyboard that has the same characteristics as pulling shelves , equipped with a folding vertical part of the step;
_ legs for control at the bottom with a lock-nut for blocking;
_ grids for ventilation with filter with fine grid against dust (if inside the panel there is no air conditioning system);
_ forced ventilation system with a load capacity of air 150mc / h installed on the roof (if inside the panel there is no air conditioning system) with power supply 230V + / -10% c.a. 50Hz, connected to the panel for power and managrd by the internal thermostat;
_ panel for power supply made of:
* no. 2 overall switches (input line UPS and output line UPS) automatic modular type 2x16 curve C, Pi 6kA, Id 30mA type A;
* no. .. 7 sockets of universal type (bipolar conflict with a hole in the earth at the center) to the axis of polarity leaned compared to to the axis of panels to be m + allow the use of all sockets without obstacles or interference on the cables that come out from within the plugs;
_ pocket for placing documents from hard plastic (excluding flexible transparent bags made ​​of nylon or similar) installed in panels or in a place defined by the company;
_ blind panels in at least 15% of available frontal surface (excluding ventilation panels and panels for power supply);
_ additional elements for setting cables such as:
* constructions for setting PVC cbales, which have spare space in the amount of at least 50% of the space they occupy;
* vertical cable management rings for every 25 cm height of the panels installed on both sides;
* round covers for covering strip, surge protectors, protective screens, etc.., for all of the devices and power supply parts in order to still guarantee a degree of protection not less than IP20 on open panels;
_ external level protection : IP40 or as indicated in graphic tables, including the bottom;
_ dimensions as described in the types with the indicated base in mm (width x depth) and height in units of standard 19 "(each unit corresponds to the size of 44.45 mm).
Communication data rack 19" 800x800mm 42U
| UNDERGROUND LEVEL - DATA TRANSMISSION AND TELEPHONE |  | 1
| Total amount |  | 1
X10.A23.A4 | CONNECTION PANEL FOR RJ45 SOCKETS | n
PANEL FOR CABLE SWITCHING CAT.6
Compliance with standards: TIA/EIA 568-B-2.1 e ISO/IEC11801/2
Structural characteristics:
_ structure of painted sheet metal thickness of 10mm, equipped with support for rack 19 "1U;
_ holes for confirmation at least br.24 sockets RJ45;
_ horizontal panel for conducting cables, size 1U;
_ sockets RJ45 with following characteristics:
* contact for confirmation of conductors with a diameter of 0.4 to 0.65 mm;
* display on the monitor cat.6A;
* marks and label brackets for identification initialed outlet switching oznake i nosači etiketa za identifikaciju parafiranih utičnica za komutaciju.
The price includes:
_ testing of connectors.
RJ45 jack panel, empty, rack mountable
| UNDERGROUND LEVEL - DATA TRANSMISSION AND TELEPHONE |  | 6
| UNDERGROUND LEVEL - DATA TRANSMISSION AND TELEPHONE |  | 5
| Total amount |  | 11
X10.A23.A6 | CONNECTION PANEL FOR RJ45 SOCKETS | n
SWITCHING PANEL MADE OF COPPER CAT.6
Compliance with standards: TIA/EIA 568-B-2.1 e ISO/IEC11801/2
Structural characteristics:
_ structure of painted sheet metal thickness of 10mm, equipped with support for rack 19 "1U;
_ holes for confirmation at least br.24 sockets RJ45;
_ horizontal panel for cable management, size 1U;
_ sockets RJ45 with following characteristics:
* contact for confirmation of conductors with a diameter of 0.4 to 0.65 mm;
* display on the monitor cat.6A;
* marks and label brackets for identification initialed sockets for comutation.
The price includes:
_ testing of connectors.
RJ45 category outlet for jack panel and connection
| UNDERGROUND LEVEL - DATA TRANSMISSION AND TELEPHONE |  | 66
| UNDERGROUND LEVEL - DATA TRANSMISSION AND TELEPHONE |  | 116
| Total amount |  | 182
X10.A26.A11 | CONNECTION PANEL FOR OPTICAL CABLES | n
PANEL FOR SWITCHING OPTICAL FIBRES
Compliance with standards: EIA/TIA 568-A I B, IEC 874/14, ISO 11801, DIN41488.
Structural characteristics:
_ modular metal box in version rack 19 "1U of at least two entries for fiber optical cables;
_ No.24 holes for installation of single mode optocoupler type LC; optokapleri
_ upper transparent sliding cover;
_ module capsule cable for optical suspenders;
_ rails for fibers and internal fixation system for fixing individual fibers;tračnica
_ blind plugs for closing unused hole;
_ panel for cable management, size 1U;
* marks and label brackets for identifying sockets for comutation. komutaciju.
The price includes:
_ single mode LC-type connectors;
_ testing of connectors;
_ testing with OTDR technique.
6 singlemode fiber optic cable jack panel and connection
| UNDERGROUND LEVEL - DATA TRANSMISSION AND TELEPHONE |  | 2
| Total amount |  | 2
X10.A26.A13 | CONNECTION PANEL FOR OPTICAL CABLES | n
PANEL FOR SWITCHING OPTICAL FIBRES
Compliance with standards: EIA/TIA 568-A I B, IEC 874/14, ISO 11801, DIN41488.
Structural characteristics:
_ modular metal box in version rack 19 "1U of at least two entries for fiber optical cables;
_ No.24 holes for installation of single mode optocoupler type LC; optokapleri
_ upper transparent sliding cover;
_ module capsule cable for optical suspenders;
_ rails for fibers and internal fixation system for fixing individual fibers;tračnica
_ blind plugs for closing unused hole;
_ panel for cable management, size 1U;
* marks and label brackets for identifying sockets for comutation. komutaciju.
The price includes:
_ single mode LC-type connectors;
_ testing of connectors;
_ testing with OTDR technique.
12 singlemode fiber optic cable jack panel and connection
| UNDERGROUND LEVEL - DATA TRANSMISSION AND TELEPHONE |  | 2
| Total amount |  | 2
X100.A21.A2 | TELECOM SOCKET RJ45 CAT. 6A | n
Point of equivalent socket for data transmission composed of:
_ shut-off boxes, built or visible (indicated in short individual descriptions);
_ socket RJ45 cat.6A, (number indicatedin short individual descriptions)
_ cables SFTP cat 6A from the closet rack FD to the points of sockets (average distance 70m);
_ circuit box and cover plates for the number of connections that will be installed on the box;;
_ (eventualna) razvodna kutija;
_ placing marks on each socket;
_ plugs for closing each outlet in order to prevent the introduction of dust;
_ flexible PVC pipe (za ugradnu instalacij) diameter 32 mm, solid PVC pipe (za instalaciju zidno) diameter 32 the network riser to shut off boxesod mreže usponskog voda do zaporne kutije.
Price includes testing of "constant connection" by the standards CEI EN 50173 is 50174 and closing socket with appropriate plug after completed works related to testing.
n.2 telecom outlet RJ45 cat.6a in vista per WiFi con tubo in PVC rigido
| UNDERGROUND LEVEL - DATA TRANSMISSION AND TELEPHONE |  | 1
| Total amount |  | 1
X100.A21.A4 | TELECOM SOCKET RJ45 CAT. 6A | n
Point of equivalent socket for data transmission composed of:
_ shut-off boxes, built or visible (indicated in short individual descriptions);
_ socket RJ45 cat.6A, (number indicatedin short individual descriptions)
_ cables SFTP cat 6A from the closet rack FD to the points of sockets (average distance 70m);
_circuit box and cover plates for the number of connections that will be installed on the box;
_ (possible) junction box;
_ placing marks on each socket;
_ plugs for closing each outlet in order to prevent the introduction of dust;
_ flexible PVC pipe (for built installation) diameter 32 mm, solid PVC pipe (for installation on the wall) diameter 32 the network riser to shut off box.
Price includes testing of "constant connection" by the standards CEI EN 50173 is 50174 and closing socket with appropriate plug after completed works related to testing.
n.2 telecom outlet RJ45 cat.6a in vista per controllo accessi con tubo in PVC rigido
| UNDERGROUND LEVEL - DATA TRANSMISSION AND TELEPHONE |  | 9
| UNDERGROUND LEVEL - DATA TRANSMISSION AND TELEPHONE |  | 1
| Total amount |  | 10
X100.A21.A5 | TELECOM SOCKET RJ45 CAT. 6A | n
Point of equivalent socket for data transmission composed of:
_ shut-off boxes, built or visible (indicated in short individual descriptions);
_ socket RJ45 cat.6A, (number indicatedin short individual descriptions)
_ cables SFTP cat 6A from the closet rack FD to the points of sockets (average distance 70m);
_circuit box and cover plates for the number of connections that will be installed on the box;;
_ (eventualna) razvodna kutija;
_ placing marks on each socket;
_ plugs for closing each outlet in order to prevent the introduction of dust; ;
_ flexible PVC pipe (za ugradnu instalacij) diameter 32 mm, solid PVC pipe (za instalaciju zidno) diameter 32 the network riser to shut off box.
Price includes testing of "constant connection" by the standards CEI EN 50173 is 50174 and closing socket with appropriate plug after completed works related to testing.
n.2 telecom outlet RJ45 cat.6a in vista per telecamere con tubo in PVC rigido
| UNDERGROUND LEVEL - DATA TRANSMISSION AND TELEPHONE |  | 4
| Total amount |  | 4
X100.A21.A6 | TELECOM SOCKET RJ45 CAT. 6A | n
Point of equivalent socket for data transmission composed of:
_ shut-off boxes, built or visible (indicated in short individual descriptions);
_ socket RJ45 cat.6A, (number indicatedin short individual descriptions)
_ cables SFTP cat 6A from the closet rack FD to the points of sockets (average distance 70m);
_ circuit box and cover plates for the number of connections that will be installed on the box;;
_ (eventualna) razvodna kutija;
_ placing marks on each socket;
_ plugs for closing each outlet in order to prevent the introduction of dust;
_ flexible PVC pipe (za ugradnu instalacij) diameter 32 mm, solid PVC pipe (za instalaciju zidno) diameter 32 the network riser to shut off box.
Price includes testing of "constant connection" by the standards CEI EN 50173 is 50174 and closing socket with appropriate plug after completed works related to testing.
n.3 telecom outlet RJ45 cat.6a ad incasso su canale attrezzato a parete in PVC
| UNDERGROUND LEVEL - DATA TRANSMISSION AND TELEPHONE |  | 9
| Total amount |  | 9
X100.A21.A7 | TELECOM SOCKET RJ45 CAT. 6A | n
Point of equivalent socket for data transmission composed of:
_ shut-off boxes, built or visible (indicated in short individual descriptions);
_ socket RJ45 cat.6A, (number indicatedin short individual descriptions)
_ cables SFTP cat 6A from the closet rack FD to the points of sockets (average distance 70m);
_ circuit box and cover plates for the number of connections that will be installed on the box;;
_ (eventualna) razvodna kutija;
_ placing marks on each socket;
_ plugs for closing each outlet in order to prevent the introduction of dust;
_ flexible PVC pipe (za ugradnu instalacij) diameter 32 mm, solid PVC pipe (za instalaciju zidno) diameter 32 the network riser to shut off box.
Price includes testing of "constant connection" by the standards CEI EN 50173 is 50174 and closing socket with appropriate plug after completed works related to testing.
n.2 telecom outlet RJ45 cat.6a in vista con tubo in PVC rigido
| UNDERGROUND LEVEL - VIDEO ENTRY PHONE SYSTEM |  | 6
| LV SUBSTATION - VIDEO ENTRY PHONE SYSTEM |  | 4
| UNDERGROUND LEVEL - DATA TRANSMISSION AND TELEPHONE |  | 1
| Total amount |  | 11
TOTAL SYSTEMS FOR DATA TRANSMISSION AND TELEPHONE
16 - SYSTEM FOR SURVEILLANCE AND CENTRALIZED CONTROL
Y100.A10.A1 | BUILDING MANAGEMENT SYSTEM (BMS) | n
CENTRALIZED SYSTEM OF INSTALLATION CONTROL (BMS SYSTEM)
Control system with an integrated command for automatic control of electrical installations, single software platform for fire and security systems, thermotechnical systems (described in Volume 3 (Book 3) of thermomechanical installations project) by using BACNet over IP protocol for fire and thermotechnics. Fully integrated with light control system using protocol communication (KNX/EIB) Building Management System, which consists of the following elements:
N.1 Computer for monitoring with software SCADA (Supervisory Control And Data Acquisition) WinCC, with the base for processing data from the electrical system, "high voltage", safety, security and thermomechanization that the graphical interface allows the user to visualize the following functions:
_electrical installation of high voltage (high voltage):
* value and status that come directly from the buses, from connected units to the microprocessor installed in the electrical command panels;
* status and alarm of clicking relay which is emitted by switches managed by the control panels;
* status and alarms UPS;
*status values ​​and alarms photovoltage system;
*status and alarm of main apparatus on substation.
_safety installations (fire and gas indicators)
* status and alarms of switchboards;
* status of the serial lines and indicator curcuits;
* status and alarms of indicators, with planimetric representation of their positions;
* state and planimetric position of buttons for alarm;
* status of input and output modules
_installation of sound signalization for evacuation
* status of central unit;
* status of amplitude line;
_safety installations (burglary, access control, CCTV)
* status and position of module for transition management;
* status/alarm/planimetric position of indication elements;
* status of burglary switchboard.
_Lighting system:
* status of individual control units;
* control and regulation of illuminotechnical status in different environments (ON/OFF/DIMM);
*possibility of programming lighting scenario
*night configuration
_Part with alarms for display of alarms from all installations and keeping them in a database;
_Part with trend graphic for transition:
*energy production from photovoltage (daily, hourly, monthly, annual);
* energy consumption of the building;
*alarms from external devices.
CONTROL UNIT OF ELECTRICAL HIGH VOLTAGE INSTALLATIONS consists of the following elements:
unit for receiving digital input, installed by the electrical boxes (unit in the open), connected to the PLC via lines Bus, Modbus or Profibus, will have to serve as electrical isolation (galvanic separation) between the low-voltage of maintained apparatus and the lowest voltages within the control modules, which include optical signals, which refers to signals that are received, and the functions in progress.
unit for receiving digital input, installed with different electrical boxes (external unit), connected to the PLC via Bus lines, Modbus or Profibus, will have to serve as electrical isolation (galvanic separation) between the low-voltage maintained apparatus and the lowest voltage within the control module, which contain optical signalization, which refers to signals that are received, and the functions in progress.
_peripheral units for management and automation of operating island (PLC) that are installed with various electric command panles, consist of:
* power supply units 230 V AC 50 Hz with transformer on 24 VDC;
* scheme processors with inputs of serial interface with a standard protocol Modbus or Profibus for connecting units at the terrain;
* network cards with protocol serial port RS485 Modbus or Profibus for connection to a PC for supervision;
terminal module with terminal setup and power supply modules interface and for connecting to the control modules, have the following features:
* plastic holder for snap installation on guide DIN with a mesh insulating plates (stripboard) with the runway for the power supply and data transmission terminals for power supply, fuses, broadband cable connector for connection to the control module, connector screw for connection of interfaces is not the spaces provided
* voltage and frequence of power supply: 24V AC, +15/-10% - 50Hz;
* insulation level: class II;
* protection level: min. IP20.
_bus line protected with 4 conductors section 24 AWG, the serial connection of different elements that make up the system;
_router for conversion of serial line to network TCP/IP for communication with supervisor computer, with patch cord in cat.6A;
_dress package through conductors, accessories and smallparts;
_programming and techical system check;
LIGHTING CONTROL SYSTEM
Consists of the following parts:
_POWER SUPPLY OF BUS LINES suitable for installation on supporter DIN 35mm (inside the electrical panels) output voltage 640mA;
_THE JOINTS BETWEEN MAIN AND SECONDARY BUS LINE with galvanic separation thereof, suitable for installation on DIN 35mm (inside the electrical panels), suitable for data transmission of bus telegrams from one curcuit to another, and vice versa (potential short circuits on the secondary bus lines have been discovered and there is no transmission); ;
_MODULE FOR MANAGEMENT OF ELECTRONIC REACTOR, SILENCERS AND STEERABLE (DALI) with the following characteristics:
* line management, each with 64 reactors/electrical transformes DALI, which can be split into 16 independent illuminotechnical conditions;
* darkening 1÷100%;
* possibility of failure signalization in the system;
* command cables of changing polarities;
* connecting using clamps with screws;
* protection level min: IP20, dim: 40 x 30 x 270L mm.
* interface EIB/KNX;
MODULES INPUT MODELS WITH KEYS suitable for installation inside the box 503 with the following characteristics:
* 4 entrances separated from keys ;
*depending on the direction of the module, you can manage all the terminals of a system: Briefly pressing the appropriate button switches from one state to another (state "Missing" and state "Present"). A long press on the button increases or decreases shading of complete lighting or a group;
* cable long 5m prefabricated,for connecting module and key;
*protection level min: IP20, dim: 40 x 40 x 17 p mm.
DIGITAL OUTPUT MODULE WITH 4 POTENTIAL-FREE CONTACTS
has following characteristics:
*output relay with contacts for controlling and the independent directing for switching of electrical installations with voltage network up to 230/240V;
* conductivity of contacts: 10A u AC1;
*connecting with clamps with screws;
* test key, LED for signalisation;
*installation into electrical box on DIN carrier 35 mm;
* protection level min: IP20, dim: 3 moduls.
PRESENCE OF LIGHT SENSOR (included in the BoQ Books (Book) 4 "high voltage") for inclusion of internal illumination system or control of the level of illumination as a function of contributions to natural light, with the following characteristics:
* installation in a prominent place on the ceiling or on the wooden beam by using particular carrier (the last one is included);
* auto power off function;
*the presence indicator is integrated with a time delay compared to the shutdown between 30 seconds and 20 minutes;
presence of indicator zone: dimensions around 4,0x4,0 m (when people are sitting) ili 6,0x6,0 m (people are moving) za Hinst=2,5m; dim. oko 4,5x4,5 m (people are sitting) ili 7,0x7,0 m (preople are moving)for Hinst=3,0m;
*indication field of illumination value: od 6 do 1.600 [lx];
* angle of sensor viewing around 120° (vertical); 360° (horizontal);
*protection level: IP20, dim. Oko 100x100x55 h mm.
router to convert a serial line EIB / KNX in the network ethernet TCP / IP to communicate with a computer for monitoring, which consists of di patch cord in cat. 6A;
bus network EIB/KNX implemented with certified cables;
bus network DALI implemented with certified cables;
INTERFACE DEVICES FOR LOW VOLTAGE INSTALLATIONS
Consists of:
BACNet over IP communication for fire detection, router for gas, embedded protocols for systems against burglary, which enable monitoring and full control for ALL data points by network LAN Ethernet with protocole TCP / IP; will also be equipped with a driver that will enable translation within the central database with the data obtained by the computer supervisor;
interface switchboard sound system using digital contacts at the entrance to the switchboard for fire detection;
interface access control system using the database within the computer for control that is dedicated to access control system;
Interface CCTV camera system using IP network and CCTV software modules which are ambedded in BMS software
CONTROL POINT FOR ELECTRICAL INSTALLATIONS OF HIGH VOLTAGE
Consists of:
a control units for the control with the schemes in the area of ​​the ports sufficient to manage controlled points , which are required for the control of a specific apparatus or an electrical frame;
bus line;
electric voltage of control apparatus;
part of the quota computer for supervision;
graphic station for review of controlled points;
licence.
CONTROL POINT OF LIGHTING DEVICES
Consists of:
regulation units installed on electrical frames on BUS DALI i EIB/KNX;
_ units for management at the terrain for procurement of keys and presence and lighting indicators;
_ router;
_ bus DALI i EIB/KNX;
_ electric power supply of command devices;
_ part of the quota computer for supervision;;
_ graphic for mapping of configured system and systems for control of lighting and technical configurations;
_ licence.
CONTROL POINT OF SPECIAL DEVICES
Consists of:
_ interface router switchboard with supervisor;
_ part of the quota computer for supervision;
_ graphic for mapping controlled devices and for status visualization of status/alarm;
_ licence.
Control points are specificially indicated in appropriate paragraph Address Points
BMS input/output address point for electrical plants
UNDERGROUND LEVEL - BMS SYSTEM
LV SUBSTATION - BMS SYSTEM
LV SUBSTATION - BMS SYSTEM
| Total licences |  | 1
Y100.A10.A2 | CENTRALIZED CONTROL INSTALLATION SYSTEM (BMS SYSTEM) | n
Control system with integrated command for automatic management of electric installations, special and termomechanical, (described in book 3 (Book 3)of project thermomechanical installations), Building Management System, consists of the following elements:
N.1 Computer for monitoring with software SCADA (Supervisory Control And Data Acquisition), with the base for processing data from the electrical system, "high voltage", safety, security and thermomechanization that the graphical interface allows the user to visualize the following functions:
electrical installation of high voltage (high voltage):
* value and status that come directly from the bus line from the unit for a dialogue with the microprocessor installed in the electrical boxes;
* status and alarms relay switches that control electronic frames;
* status and alarms UPS;
*status values ​​and alarms photovoltage system;
*status and alarm of main apparatus of electrical cabine.
*safety installations (fire and gas indicators)
* status and alarms of switchboards;
* status of the serial lines and indicator loops;
* status and alarms of indicators, sa planimetrijskom representation of their position;
* status and planimetric position the pulsating alarms;
* status of input and output modules
Installation of sound signalization for evacuation
* status of central unit;
* status of amplitude line;
safety installations (antiburglary, access control, CCTV)
* status and position of door control;
* status / alarm / planimtrijska position elements indicationsstatus/alarm/planimtrijska element positions of indication;
* status of anti burglary switchboard.
Lighting system:
* status of individual control units;
* control and regulation of illuminotechnical status in different environments (ON/OFF/DIMM);
possibility of programming lighting scenario
night configuration
Display of alarms from all installations and keeping them in a database;
graphic display for the report:
*energy production from photovoltage(daily, hourly, monthly, annual);
* energy consumption of the building;
*alarms from external devices.
CONTROL UNIT OF ELECTRICAL HIGH VOLTAGE INSTALLATIONS consists of the following elements:
unit for receiving digital input, installed by the electrical boxes (unit in the open), connected to the PLC via lines Bus, Modbus or Profibus, will have to serve as electrical isolation (galvanic separation) between the low-voltage of maintained apparatus and the lowest voltages within the control modules, which include optical signals, which refers to signals that are received, and the functions in progress.
unit for receiving digital input, installed with different electrical boxes (external unit), connected to the PLC via Bus lines, Modbus or Profibus, will have to serve as electrical isolation (galvanic separation) between the low-voltage maintained apparatus and the lowest voltage within the control module, which contain optical signalization, which refers to signals that are received, and the functions in progress.
peripheral units for maintanace and automation of isolated functions (PLC) that are installed with various electrical boxes, consist of:
* power source 230 V AC 50 Hz with transformer on 24 VDC;
*scheme processor schema with inputs of serial interface with a standard protocol Modbus or Profibus for connecting units in the open;
*scheme network with protocol serial port RS485 Modbus or Profibus for connection to a PC or supervision;
transmission mode with terminals for set-up and power supply of modules with interface and for connecting with the control modules, have the following characteristics:
* plastic holder that allows easy installation on DIN supporter with base štamframeploče with lines for power and signal transmission, power plugs, fuses, broadband cables with connectors for connection to the control module, connect to the screw for connecting at precisely specified places;
* strength and frequence of power supply: 24V AC, +15/-10% - 50Hz;
* insulation level: class II;
* protection level: min. IP20.
image of bus line with 4 conductors section 24 AWG, for the serial connection of different elements that make up the system;
router for conversion of serial line to network TCP/IP for communication with supervisor computer, with patch cord in cat.6A;
dress package through conductors, accessories and special parts;
programming and system check;
LIGHTING CONTROL SYSTEM
Consists of the following parts:
POWER SUPPLY OF BUS LINES suitable for installation on DIN carriers 35mm (inside the electrical box) output voltage 640mA;
THE JOINTS BETWEEN MAIN AND SECONDARY BUS LINE with galvanic separation thereof, suitable for installation on DIN supporter 35mm (inside the electrical boxes), suitable for data transmission through bus lines from one curcuit to another, and vice versa (potential short circuits on the secondary bus lines have been discovered and there is no transmission) ;
MODULE FOR MANAGEMENT OF ELECTRONIC REACTOR, SILENCERS AND STEERABLE (DALI) with the following characteristics:
* line management, each with 64 reactors/electrical transformes, in compliance with DALI, which can be split into 16 independent lighting;
* darkening 1÷100%;
* possibility of failure signalization in the system;
* command cables of changing polarities;
* connecting using clamps with screws;
* protection level min: IP20, dim: 40 x 30 x 270L mm.
* interface EIB/KNX;
MODULES INPUT MODELS WITH KEYS suitable for installation inside the box 503 with the following characteristics:
* 4 separate entrances with key;
*depending on the direction of the module, you can manage all the terminals of a system: Briefly pressing the appropriate button switches from one state to another (state "Missing" and state "Present"). A long press on the button increases or decreases shading of complete lighting or a group;
* cable long 5m prefabricated,for connecting module and key;
*protection level min: IP20, dim: 40 x 40 x 17 p mm.
DIGITAL OUTPUT MODULE WITH 4 POTENTIAL-FREE CONTACTS
has following characteristics:
*output relay with contacts for controlling and the independent directing for switching of electrical installations with voltage network up to 230/240V;
* conductivity of contacts: 10A u AC1;
*connecting with clamps with screws;
* test key, LED for signalisation;
*installation into electrical box on DIN carrier 35 mm;
* protection level min: IP20, dim: 3 moduls.
PRESENCE OF LIGHT SENSOR (included in the BoQ Books (Book) 4 "high voltage") for inclusion of internal illumination system or control of the level of illumination as a function of contributions to natural light, with the following characteristics:
* installation in a prominent place on the ceiling or on the wooden beam by using particular carrier (the last one is included);
* auto power off function;
*the presence indicator is integrated with a time delaycompared to the shutdown between 30 seconds and 20 minutes;
presence of indicator zone: dimensions oko 4,0x4,0 m (when people are sitting) ili 6,0x6,0 m (people are moving) for Hinst=2,5m; dim. oko 4,5x4,5 m (people are sitting) ili 7,0x7,0 m (preople are moving) za Hinst=3,0m;
*indication field of illumination value: od 6 do 1.600 [lx];
* angle of sensor viewing around 120° (vertical); 360° (horizontal);
*protection level: IP20, dim. Oko 100x100x55 h mm.
router to convert a serial line EIB / KNX in the network ethernet TCP / IP to communicate with a computer for monitoring, which consists of di patch cord in cat. 6A;
bus network EIB/KNX implemented with certified cables;
bus network DALI implemented with certified cables;
INTERFACE DEVICES OF SPECIAL INSTALLATIONS OF LOW VOLTAGE
Consists of the following elements
BACNet over IP communication for fire detection, gas and against burglary, which enable translation of serial line that comes from the individual switchboards in network LAN Ethernet with protocole TCP / IP; will also be equipped with a driver that will enable translation within the central database with the data obtained by the computer supervisor;
_ interface switchboard of sound difusion using digital contacts at the entrance of the switchboard for fire detection;
_ interface control access system using a data bank from control computer system designed for access control system;
_ interface camera system CCTV using digital contacts at the entrance of burglar system.
CONTROL POINT FOR ELECTRICAL INSTALLATIONS OF HIGH VOLTAGE
Consists of:
a control units for the control with the schemes in the area of ​​the ports sufficient to manage controlled points , which are required for the control of a specific apparatus or an electrical frame;
bus line;
electric voltage of control apparatus;
part of the quota computer for supervision;
graphic station for review of controlled points;
licence.
CONTROL POINT FOR LIGHTING DEVICE
Consists of:
_ control units installed in electronic panels for BUS DALI i EIB/KNX;
_ control units at the terrain for supply of command keys and indicators of presence and lighting;
_ router;
_ bus DALI i EIB/KNX;
_ electric power supply of command devices;
_ licence.
CONTROL POINT FOR SPECIAL INSTALLATIONS
Consists of:
router interface switchboard and supervisor;
quota part of the computer for supervision;
graphic for mapping controlled devices and for status visualization of status/alarm;
licence.
Control points are specificially indicated in appropriate paragraph Address Points
BMS input/output address point for control lighting system
| UNDERGROUND LEVEL - BMS SYSTEM |  | 1
| Total amount |  | 1
Y100.A10.A3 | BUILDING MANAGEMENT SYSTEM (BMS) | n
CENTRALIZED SYSTEM OF INSTALLATION CONTROL (BMS SYSTEM)
Control system with an integrated command for automatic control of electrical installations, special and thermomechanical (described in Volume 3 (Book 3) of p thermomechanical installations project), Building Management System, which consists of the following elements:
N.1 Computer for monitoring with software SCADA (Supervisory Control And Data Acquisition), with the base for processing data from the electrical system, "high voltage", safety, security and thermomechanization that the graphical interface allows the user to visualize the following functions:
electrical installation of high voltage (high voltage):
* value and status that come directly from the bus line from the unit for a dialogue with the microprocessor installed in the electrical frames;
* status and alarms relay switches that control electronic frames;
* status and alarms UPS;
*status values ​​and alarms photovoltage system;
*status and alarm of main apparatus of electrical cabine.
*safety installations (fire and gas indicators)
* status and alarms of switchboards;
* status of the serial lines and indicator loops;
* status and alarms of indicators, with planimetric representation of their positions;
* status i planimetrijska pozicija pulsirajućih alarma;
* status of input and output modules
Installation of sound signalization for evacuation
* status of central unit;
* status of amplitude line;
safety installations (antiburglary, access control, CCTV)
* status and position of door control;
* status/alarm/planimetric position of indication elements;
* status of antiburglary switchboard.
Lighting system:
* status of individual control units;
* control and regulation of illuminotechnical status in different environments (ON/OFF/DIMM);
possibility of programming lighting scenario
night configuration
Display of alarms from all installations and keeping them in a database;
graphic display for the report:
*energy production from photovoltage (daily, hourly, monthly, annual);
* energy consumption of the building;
*alarms from external devices.
CONTROL UNIT OF ELECTRICAL HIGH VOLTAGE INSTALLATIONS consists of the following elements:
unit for receiving digital input, installed by the electrical frames (unit in the open), connected to the PLC via lines Bus, Modbus or Profibus, will have to serve as electrical isolation (galvanic separation) between the low-voltage of maintained apparatus and the lowest voltages within the control modules, which include optical signals, which refers to signals that are received, and the functions in progress.
unit for receiving digital input, installed with different electrical frames (external unit), connected to the PLC via Bus lines, Modbus or Profibus, will have to serve as electrical isolation (galvanic separation) between the low-voltage maintained apparatus and the lowest voltage within the control module, which contain optical signalization, which refers to signals that are received, and the functions in progress.
peripheral units for maintenance and automation of isolated functions (PLC) that are installed with various electrical boxes, consist of:
* power source 230 V AC 50 Hz with transformer on 24 VDC;
* scheme processor scheme with inputs of serial interface with a standard protocol Modbus or Profibus for connecting units in the open;
* scheme network with protocol serial port RS485 Modbus or Profibus for connection to a PC or supervision;
transmission mode with terminal setup and power supply modules interface and for connecting to the control modules, have the following features:
* plastic holder that allows easy installation on DIN supporter with base štamframeploče with lines for power and signal transmission, power plugs, fuses, broadband cables with connectors for connection to the control module, connect to the screw for connecting at precisely specified places;
* strength and frequence of power supply: 24V AC, +15/-10% - 50Hz;
* insulation level: class II;
* protection level: min. IP20.
Image bus lines with 4 conductors section 24 AWG, the serial connection of different elements that make up the system;
router for conversion of serial line to network TCP/IP for communication with supervisor computer, with patch cord in cat.6A;
dress package through conductors, accessories and special parts;
programming and system check;
LIGHTING CONTROL SYSTEM
Consists of the following parts:
POWER SUPPLY OF BUS LINES suitable for installation on DIN carriers 35mm (inside the electrical boxes) output voltage 640mA;
THE JOINTS BETWEEN MAIN AND SECONDARY BUS LINE with galvanic separation thereof, suitable for installation on DIN supporter 35mm (inside the electrical frames), suitable for data transmission through bus lines from one curcuit to another, and vice versa (potential short circuits on the secondary bus lines have been discovered and there is no transmission); ;
MODULE FOR MANAGEMENT OF ELECTRONIC REACTOR, SILENCERS AND STEERABLE (DALI) with the following characteristics:
* line management, each with 64 reactors/electrical transformes, in compliance with DALI, which can be split into 16 independent lighting;
* darkening 1÷100%;
* possibility of failure signalization in the system;
* command cables of changing polarities;
* connecting using clamps with screws;
* protection level min: IP20, dim: 40 x 30 x 270L mm.
* interface EIB/KNX;
MODULES INPUT MODELS WITH KEYS suitable for installation inside the box 503 with the following characteristics:
* 4 separate entrances with key;
*depending on the direction of the module, you can manage all the terminals of a system: Briefly pressing the appropriate button switches from one state to another (state "Missing" and state "Present"). A long press on the button increases or decreases shading of complete lighting or a group;
* cable long 5m prefabricated,for connecting module and key;
*protection level min: IP20, dim: 40 x 40 x 17 p mm.
DIGITAL OUTPUT MODULE WITH 4 POTENTIAL-FREE CONTACTS
has following characteristics:
*output relay with contacts for controlling and the independent directing for switching of electrical installations with voltage network up to 230/240V; komutaciju
* conductivity of contacts: 10A u AC1;
*connecting with clamps with screws;
* test key, LED for signalisation;
*installation into electrical box on DIN carrier 35 mm;
* protection level min: IP20, dim: 3 moduls.
PRESENCE OF LIGHT SENSOR (included in the BoQ Books (Book) 4 "high voltage") for inclusion of internal illumination system or control of the level of illumination as a function of contributions to natural light, with the following characteristics:
* installation in a prominent place on the ceiling or on the wooden beam by using particular carrier (the last one is included);
* auto power off function;
*the presence indicator is integrated with a time delay compared to the shutdown between 30 seconds and 20 minutes;
presence of indicator zone: dimensions around 4,0x4,0 m (when people are sitting) ili 6,0x6,0 m (people are moving) za Hinst=2,5m; dim. oko 4,5x4,5 m (people are sitting) ili 7,0x7,0 m (preople are moving)for Hinst=3,0m;
*indication field of illumination value: od 6 do 1.600 [lx];
* angle of sensor viewing around 120° (vertical); 360° (horizontal);
*protection level: IP20, dim. Oko 100x100x55 h mm.
router to convert a serial line EIB / KNX in the network ethernet TCP / IP to communicate with a computer for monitoring, which consists of di patch cord in cat. 6A;
bus network EIB/KNX implemented with certified cables;
bus network DALI implemented with certified cables;
INTERFACE DEVICES FOR LOW VOLTAGE INSTALLATIONS
Consists of:
BACNet over IP communication for fire detection, gas and against burglary, which enable translation of serial line that comes from the individual switchboards in network LAN Ethernet with protocole TCP / IP; will also be equipped with a driver that will enable translation within the central database with the data obtained by the computer supervisor;
interface switchboard sound system using digital contacts at the entrance to the switchboard for fire detection;
interface access control system using the database within the computer for control that is dedicated to access control system;
Interface CCTV camera system using a digital contacts on the door alarm system on the entrance of the antiburglar system.
CONTROL POINT FOR ELECTRICAL INSTALLATIONS OF HIGH VOLTAGE
Consists of:
a control units for the control with the schemes in the area of ​​the ports sufficient to manage controlled points , which are required for the control of a specific apparatus or an electrical frame;
bus line;
electric voltage of control apparatus;
part of the quota computer for supervision;
graphic station for review of controlled points;
licence.
CONTROL POINT OF LIGHTING DEVICES
Consists of:
_ control units installed in electronic panels for BUS DALI i EIB/KNX;
_ control units at the terrain for supply of command keys and indicators of presence and lighting;
_ router;
_ bus DALI i EIB/KNX;
_ electric power supply of command devices;
_ part of quota computer for supervision;
_ graphic for mapping system configured systems and systems for the control of lighting and technical configuration;
_ licence.
CONTROL POINT FOR SPECIAL INSTALLATIONS
Consists of:
router interface switchboard and supervisor;
quota part of the computer for supervision;
graphic for mapping controlled devices and for status visualization of status/alarm;
licence.
Control points are specificially indicated in appropriate paragraph Address Points
BMS input/output address point for safety systems
| UNDERGROUND LEVEL - BMS SYSTEM |  | 1
| LV SUBSTATION - BMS SYSTEM |  | 1
| UNDERGROUND LEVEL - BMS SYSTEM |  | 1
| Total amount |  | 1
TOTALDEVICES FOR SURVEILLANCE AND CENTRALIZED CONTTROL, BMS
TOTAL SPECIAL PLANTS - UNDERGROUND AND SUBSTATIONS
03 | SPECIAL PLANTS - GROUND FLOOR AND UPPER FLOOR LEVELS
01 - CONDUCTORS, CABLES AND ACCESSORIES
A230.A10.A22 | FTG10M1 0,6/1kV CEI 20-45 FIREPROOF CABLE | m
CABLE FTG10M1 0,6/1kV CEI 20-45, FTG10OM1 0,6/1kV CEI 20-45
Compliance with standards: CEI 20-22/3, 20-38, 20-45 and subsequent amendments and variations; EN50200.
Nominal voltage: 600/1000 V.
Insulator: a compound of ethylene-propylene rubber quality G10.
Coating: from a special thermoplastic polymer quality M1.
Filling: non-toxic rubber.
Conductor: flexible wire of coated copper coated with fireproof tape.
Behavior on the fire:
_does not spread fire;
_low emission of smoke, toxic and corrrosive gases;
_continuous work of minimum 180 minutes on the temperature 750°C in the presence of mechanical shock on every 5 min.
FTG10M1 0,6/1kV CEI 20-45 fire resistance cable 2x2.5 mmq
| GROUND FLOOR LEVEL - CONDUCTORS, CABLES AND ACCESSORIES |  | 140
| FIRST FLOOR LEVEL - CONDUCTORS, CABLES AND ACCESSORIES |  | 430
| SECOND FLOOR LEVEL CONDUCTORS, CABLES AND ACCESSORIES |  | 210
| GROUND FLOOR LEVEL - CONDUCTORS, CABLES AND ACCESSORIES |  | 70
| Total amount |  | 850
A230.A10.A23 | FTG10M1 0,6/1kV CEI 20-45 FIREPROOF CABLE | m
CABLE FTG10M1 0,6/1kV CEI 20-45, FTG10OM1 0,6/1kV CEI 20-45
Compliance with standards: CEI 20-22/3, 20-38, 20-45 i naknadnim dopunama i varijantama; EN50200.
Nominal voltage: 600/1000 V.
Insulator: a compound of ethylene-propylene rubber quality G10.
CABLE FTG10M1 0,6/1kV CEI 20-45, FTG10OM1 0,6/1kV CEI 20-45
Filling: non-toxic rubber.
Conductor: flexible wire of coated copper coated with fireproof tape.
Behavior on the fire:
_does not spread fire;
_low emission of smoke, toxic and corrrosive gases;
_continuous work of minimum 180 minutes on the temperature 750°C in the presence of mechanical shock on every 5 min.
FTG10M1 0,6/1kV CEI 20-45 fire resistance cable 2x4 mmq
| GROUND FLOOR LEVEL - CONDUCTORS, CABLES AND ACCESSORIES |  | 60
| FIRST FLOOR LEVEL - CONDUCTORS, CABLES AND ACCESSORIES |  | 50
| SECOND FLOOR LEVEL CONDUCTORS, CABLES AND ACCESSORIES |  | 20
| GROUND FLOOR LEVEL - CONDUCTORS, CABLES AND ACCESSORIES |  | 40
| Total amount |  | 170
A310.A22.A1 | CABLE FOR DATA TRANSIMISSION CAT.6a | m
CABLE FOR DATA TRANSIMISSION CAT.6A
Compliance with standards: ISO/IEC 11801- 2^ August edition 2002. and compliance with requests of Addendum 1 - February 2008. (New Standard Cat. 6A Class EA), CEI 20-35, IEC 60332.1, CEI 20-22, CEI 20-37, IEC 61034, NES 713, IEC 60754.
Copper LSZH cable coated in four pairs Cat. 6A SFTP with following characteristics:
_the external layer flame resistant and low content of halogen gases L.S.0.H.;
_nominal impedance of 100 Ohm, covered with intertwined pair (SFTP) with four intertwined pairs;
_diameter of copper conductor 23 AWG;
_Characteristics of maximum signal attenuation [dB] at different frequencies [MHz]:
* 1MHz: 4dB;
* 10 MHz: 6,4 dB;
* 100 MHz: 20,8dB;
* 200 MHz: 30 dB;
* 500 MHz: 49,3 dB.
_ Characteristics of paradiafiony NEXT [dB] on various frenquencies [MHz]:
* 1MHz: 674dB;
* 10 MHz: 58,6 dB;
* 100 MHz: 41,9dB;
* 200 MHz: 36,8 dB;
* 500 MHz: 29,9 dB.
Behavior on the fire:
_ does not spread fire;
_ low emission of smoke, toxic and corrrosive gases.
Cable FTP 4x2xAWG24 cat.6a
| GROUND FLOOR LEVEL - CONDUCTORS, CABLES AND ACCESSORIES |  | 695
| FIRST FLOOR LEVEL - CONDUCTORS, CABLES AND ACCESSORIES |  | 64
| SECOND FLOOR LEVEL CONDUCTORS, CABLES AND ACCESSORIES |  | 72
| Total amount |  | 831
A310.A31.A1 | SINGLE-MODE OPTICAL FIBRES OS1 LOOSE | m
Compliance with standards: ITU-T Rec G652 C; IEC 60793-2-50 tip B 1.3; CEI 20-38.
Conductor for outside, made ​​of fibers coated with protection 250micron loose type (loose).
External cover: polyethylene of high density.
Mechanical characteristics:
_ filling: gel which provides fibre protection on the entrance from moisture and other external impacts;
_ mechanical protection: glass yarn or other material deposited around the pipes that carries fiber against the effects of small rodents, the type for outside;
_ effort for maximum drive: 1000N;
_minimal resistance to crushing: 200N/cm.
Optical fibres: single-mode type OS1 od 9/125 micron for transmission support 1Gb/s up to 9000m.
Maximal attenuation per km:
- 1310nm; 0.4 dB;
- 1550nm: 0.4 dB.
Behavior on the fire:
_ does not spread fire;
_ low emission of smoke, toxic and corrrosive gases LSZH.
12 OS1 fiber optic cable
| GROUND FLOOR LEVEL - CONDUCTORS, CABLES AND ACCESSORIES |  | 100
| FIRST FLOOR LEVEL - CONDUCTORS, CABLES AND ACCESSORIES |  | 16
| SECOND FLOOR LEVEL CONDUCTORS, CABLES AND ACCESSORIES |  | 18
| Total amount |  | 134
A310.A31.A2 | SINGLE-MODE OPTICAL FIBRES OS1 LOOSE | m
Compliance with standards: ITU-T Rec G652 C; IEC 60793-2-50 tip B 1.3; CEI 20-38.
Conductor for outside, made ​​of fibers coated with protection 250micron loose type loose tube.
External cover: polyethylene of high density.
Mechanical characteristics:
_ filling: gel which provides fibre protection on the entrance from moisture and other external impacts;
_ mechanical protection: glass yarn or other material deposited around the pipes that carries fiber against the effects of small rodents, the type for outside;
_ effort for maximum drive: 1000N;
_minimal resistance to crushing: 200N/cm.
Optical fibres: single-mode type OS1 od 9/125 micron for transmission support 1Gb/s up to 9000m.
Maximal attenuation per km:
- 1310nm; 0.4 dB;
- 1550nm: 0.4 dB.
Behavior on the fire:
_ does not spread fire;
_ low emission of smoke, toxic and corrrosive gases LSZH.
6 OS1 fiber optic cable
| GROUND FLOOR LEVEL - CONDUCTORS, CABLES AND ACCESSORIES |  | 64
| Total amount |  | 64
TOTAL 01 - CONDUCTORS, CABLES AND ACCESSORIES
02 - CONDUITS FOR CABLES
B10.A10.A2 | METAL TRUNKING IN CLOSED VERSION, ZINC PLATED | m
SUPPORTING STRUCTURE FOR CABLES MADE OF HOT-DIP GALVANIZED STEEL FOR DROWNING AFTER TREATMENT
Compliance with standards: CEI 23-76, CEI 7-6 and subsequent variations.
Impact resistance: > 1J on room temperature (20°C ±5).
Mechanical resistance: minimum allowed load (values ​​measured for maximum arrow 1/200 medium capacity, the composition at 1/5 of the opening) measured in accordance with the appropriate performance standards:
_ closed channel with h. 75mm, light between two supporters 1,5m:
* 145 kg/m for channels wide 50-75 mm;
* 149 kg/m for channels wide 100 mm;
* 158 kg/m for channels wide 150 mm;
* 165 kg/m for channels wide 200 mm;
* 204 kg/m for channels wide 300 mm;
* 208 kg/m for channels wide 400 mm;
* 214 kg/m for channels wide 500-600 mm;
_ hollow channel with h. 75mm, light between two supporters 1,5m:
* 145 kg/m for channels wide 50-75 mm;
* 156 kg/m for channels wide 100 mm;
* 170 kg/m for channels wide 150 mm;
* 190 kg/m for channels wide 200-300 mm;
* 201 kg/m for channels wide 400 mm;
* 208 kg/m for channels wide 500 mm;
* 217 kg/m for channels wide 600 mm.
Electrical characteristics:
_ electric continuity guaranteed by the constructor with the electrical resistance (at 12V max ca 50Hz, 25A) = <0.005 ohm per meter <= 0.05 ohm nearby compound.
Structural characteristics:
_ body made ​​of one piece of sheet metal, hollow or closed, depending on the types, with rounded edges or reinforced edges against cut obtained by rolling and galvanized on fire after processing zinc quality Zn B132 A 99.90%;
_thickness of sheet metal: min.0,8 mm (up to 150x75) and 1 mm and over (for larger widths);
_ average thickness of zinc layer: 57 micron +/-10% for individual front side;
_ avearge mass of zink layer: 400 g/m2 +/-10% for individual front side;
_ cover (when required) of galvanized steel with the same treatment and structural characteristics of s.d., with the closure with the latch, i.e. by hook that can not be lost.
Protection level (in case of constructions with permanent full-bottom / closed and with a cover): min. IP30 for the entire system.
Zinc plated metal trunking, perforated base, size 100x75mm
| ROOF LEVEL - CONDUITS FOR CABLES |  | 46
| Total amount |  | 46
B10.A10.A22 | METAL TRUNKING IN CLOSED VERSION, ZINC PLATED | m
SUPPORTING STRUCTURE FOR CABLES MADE OF HOT-DIP GALVANIZED STEEL FOR DROWNING AFTER TREATMENT
Compliance with standards: CEI 23-76, CEI 7-6 and subsequent variations.
Impact resistance: > 1J on room temperature (20°C ±5).
Mechanical resistance: minimum allowed load (values ​​measured for maximum arrow 1/200 medium capacity, the composition at 1/5 of the opening) measured in accordance with the appropriate performance standards:
_ closed channel with h. 75mm, light between two supporters 1,5m:
* 145 kg/m for channels wide 50-75 mm;
* 149 kg/m for channels wide 100 mm;
* 158 kg/m for channels wide 150 mm;
* 165 kg/m for channels wide 200 mm;
* 204 kg/m for channels wide 300 mm;
* 208 kg/m for channels wide 400 mm;
* 214 kg/m for channels wide 500-600 mm;
_ hollow channel with h. 75mm, light between two supporters 1,5m:
* 145 kg/m for channels wide 50-75 mm;
* 156 kg/m for channels wide 100 mm;
* 170 kg/m for channels wide 150 mm;
* 190 kg/m for channels wide 200-300 mm;
* 201 kg/m for channels wide 400 mm;
* 208 kg/m for channels wide 500 mm;
* 217 kg/m for channels wide 600 mm.
Electrical characteristics:
_ electric continuity guaranteed by the constructor with the electrical resistance (at 12V max ca 50Hz, 25A) = <0.005 ohm per meter <= 0.05 ohm nearby compound.
Structural characteristics:
_ body made ​​of one piece of sheet metal, hollow or closed, depending on the types, with rounded edges and reinforced edges against cut obtained by rolling and galvanized on fire after processing zinc quality Zn B132 A 99.90%;
_thickness of sheet metal: min.0,8 mm (up to 150x75) and 1 mm and over (for larger widths);
_ average thickness of zinc layer: 57 micron +/-10% for individual front side;
_ average mass of zink layer: 400 g/m2 +/-10% for individual front side;
_ cover (when required) of galvanized steel with the same treatment and structural characteristics of s.d., with the closure with the latch, i.e. by hook that can not be lost.
Protection level (in case of constructions with permanent full-bottom / closed and with a cover): min. IP30 for the entire system.
Metal trunking cover 100 mm
| ROOF LEVEL - CONDUITS FOR CABLES |  | 46
| Total amount |  | 46
B10.A40.A14 | ZINC PLATED WIRE MESH | m
SUPPORTING STRUCTURE FOR CABLES MADE OF HOT-DIP GALVANIZED STEEL FOR DROWNING AFTER TREATMENT
Compliance with standards: CEI 23-76, CEI 7-6 and subsequent variations.
Impact resistance: > 1J on room temperature (20°C ±5).
Mechanical resistance: minimum allowed load (values ​​measured for maximum arrow 1/200 medium capacity, the composition at 1/5 of the opening) measured in accordance with the appropriate performance standards:
_constructions with h. 50 mm, light between two supporters 1,5m;
* 18 kg/m for channels wide 50-100 mm;
* 27 kg/m for channels wide 150 mm;
* 33 kg/m for channels wide 200 mm;
* 63 kg/m for channels wide 300 mm;
* 104 kg/m for channels wide 400 mm;
* 120 kg/m for channels wide 500-600 mm;
_ constructions with h. 100mm, light between two supporters 1,5m:
* 37 kg/m for channels wide 100 mm;
* 53 kg/m for channels wide 150 mm;
* 73 kg/m for channels wide 200 mm;
* 104 kg/m for channels wide 300-400 mm; * 125 kg/m for channels wide 500-600 mm.
Electrical characteristics:
_ electric continuity guaranteed by the constructor with the electrical resistance (at 12V max ca 50Hz, 25A) = <0.005 ohm per meter <= 0.05 ohm nearby compound.
Structural characteristics:
_structure is made of welded steel wire, hot-dipped galvanized for drowning after treatment with prior degreasing and pickling, and the final painting (for types that are required) epoxy resin or polyester;
_ safety edge without parts that contains sharp edges;
_ minimum mass of zink layer: 330 g/m2 +/-10%;
_ average thickness of zink layer: 50 micron +/- 10%.
_ cover (when required) of galvanized steel with the same treatment and structural characteristics of s.d., with the closure with the latch, i.e. by hook that can not be lost.
Behavior on the fire collor (upon request) auto extinguishing.
Zinc plated wire mesh, size 200x105mm
| ROOF LEVEL - CONDUITS FOR CABLES |  | 36
| Total amount |  | 36
B10.A40.A2 | ZINC PLATED WIRE MESH | m
CONSTRUCTION FOR CABLES MADEOF HOT-DIP GALVANIZED STEEL FOR DROWNING AFTER TREATMENT
Compliance with standards: CEI 23-76, CEI 7-6 and subsequent variations.
Impact resistance: > 1J on room temperature (20°C ±5).
Mechanical resistance: minimum allowed load (values ​​measured for maximum arrow 1/200 medium capacity, the composition at 1/5 of the opening) measured in accordance with the appropriate performance standards:
_ constructions with h. 50mm, light between two supporters 1,5m:
* 18 kg/m for channels wide 50-100 mm;
* 27 kg/m for channels wide 150 mm;
* 33 kg/m for channels wide 200 mm;
* 63 kg/m for channels wide 300 mm;
* 104 kg/m for channels wide 400 mm;
* 120 kg/m for channels wide 500-600 mm;
_ constructions with h. 100 mm, light between two supporters 1,5m:
* 37 kg/m for channels wide 100 mm;
* 53 kg/m for channels wide 150 mm;
* 73 kg/m for channels wide 200 mm;
* 104 kg/m for channels wide 300-400 mm; * 125 kg/m for channels wide 500-600 mm.
Electrical characteristics:
_ electric continuity guaranteed by the constructor with the electrical resistance (at 12V max ca 50Hz, 25A) = <0.005 ohm per meter <= 0.05 ohm nearby compound.
Structural characteristics:
_structure is made of welded steel wire, hot-dipped galvanized for drowning after treatment with prior degreasing and pickling, and the final painting (for types that are required) epoxy resin or polyester;
_ safety edge without parts that contains sharp edges;
_ minimum mass of zink layer: 330 g/m2 +/-10%;
_ average thickness of zink layer: 50 micron +/- 10%.
_ cover (when required) of galvanized steel with the same treatment and structural characteristics of s.d., with the closure with the latch, i.e. by hook that can not be lost.
Behavior on the fire collor (upon request) auto extinguishing.
Zinc plated wire mesh, size 100x55mm
| GROUND FLOOR LEVEL - CONDUITS FOR CABLES |  | 6
| FIRST FLOOR LEVEL - CONDUITS FOR CABLES |  | 8
| SECOND FLOOR LEVEL - CONDUITS FOR CABLES |  | 74
| GROUND FLOOR LEVEL - CONDUITS FOR CABLES |  | 21
| Total amount |  | 109
B10.A40.A3 | ZINC PLATED WIRE MESH | m
CONSTRUCTION FOR CABLES MADEOF HOT-DIP GALVANIZED STEEL FOR DROWNING AFTER TREATMENT
Compliance with standards: CEI 23-76, CEI 7-6 and subsequent variations.
Impact resistance: > 1J on room temperature (20°C ±5).
Mechanical resistance: minimum allowed load (values ​​measured for maximum arrow 1/200 medium capacity, the composition at 1/5 of the opening) measured in accordance with the appropriate performance standards:
_ constructions with h. 50mm, light between two brackets 1,5m:
* 18 kg/m for channels wide 50-100 mm;
* 27 kg/m for channels wide 150 mm;
* 33 kg/m for channels wide 200 mm;
* 63 kg/m for channels wide 300 mm;
* 104 kg/m for channels wide 400 mm;
* 120 kg/m for channels wide 500-600 mm;
_ constructions with h. 100 mm, light between two brackets 1,5m:
* 37 kg/m for channels wide 100 mm;
* 53 kg/m for channels wide 150 mm;
* 73 kg/m for channels wide 200 mm;
* 104 kg/m for channels wide 300-400 mm; * 125 kg/m for channels wide 500-600 mm.
Electrical characteristics:
_ electric continuity guaranteed by the constructor with the electrical resistance (at 12V max ca 50Hz, 25A) = <0.005 ohm per meter <= 0.05 ohm nearby compound.
Structural characteristics:
_structure is made of welded steel wire, hot-dipped galvanized for drowning after treatment with prior degreasing and pickling, and the final painting (for types that are required) epoxy resin or polyester;
_ safety edge without parts that contain sharp edges;
_ minimum mass of zink layer: 330 g/m2 +/-10%;
_ average thickness of zink layer: 50 micron +/- 10%.
_ cover (when required) of galvanized steel with the same treatment and structural characteristics of s.d., with the closure with the latch, i.e. by hook that can not be lost.
Behavior on the fire collored (upon request) autoestingueting.
Zinc plated wire mesh, size 150x55mm
| FIRST FLOOR LEVEL - CONDUITS FOR CABLES |  | 235
| SECOND FLOOR LEVEL - CONDUITS FOR CABLES |  | 83
| Total amount |  | 318
B10.A40.A4 | ZINC PLATED WIRE MESH | m
CONSTRUCTION FOR CABLES MADEOF HOT-DIP GALVANIZED STEEL FOR DROWNING AFTER TREATMENT
Compliance with standards: CEI 23-76, CEI 7-6 and subsequent variations.
Impact resistance: > 1J on room temperature (20°C ±5).
Mechanical resistance: minimum allowed load (values ​​measured for maximum arrow 1/200 medium capacity, the composition at 1/5 of the opening) measured in accordance with the appropriate performance standards:
_ constructions with h. 50mm, light between two brackets 1,5m:
* 18 kg/m for channels wide 50-100 mm;
* 27 kg/m for channels wide 150 mm;
* 33 kg/m for channels wide 200 mm;
* 63 kg/m for channels wide 300 mm;
* 104 kg/m for channels wide 400 mm;
* 120 kg/m for channels wide 500-600 mm;
_ constructions with h. 100 mm, light between two brackets 1,5m:
* 37 kg/m for channels wide 100 mm;
* 53 kg/m for channels wide 150 mm;
* 73 kg/m for channels wide 200 mm;
* 104 kg/m for channels wide 300-400 mm; * 125 kg/m for channels wide 500-600 mm.
Electrical characteristics:
_ electric continuity guaranteed by the constructor with the electrical resistance (at 12V max ca 50Hz, 25A) = <0.005 ohm per meter <= 0.05 ohm nearby compound.
Structural characteristics:
_structure is made of welded steel wire, hot-dipped galvanized for drowning after treatment with prior degreasing and pickling, and the final painting (for types that are required) epoxy resin or polyester;
_ safety edge without parts that contain sharp edges;
_ minimum mass of zink layer: 330 g/m2 +/-10%;
_ average thickness of zink layer: 50 micron +/- 10%.
_ cover (when required) of galvanized steel with the same treatment and structural characteristics of s.d., with the closure with the latch, i.e. by hook that can not be lost.
Behavior on the fire collored (upon request) autoestingueting.
Zinc plated wire mesh, size 200x55mm
| GROUND FLOOR LEVEL - CONDUITS FOR CABLES |  | 19
| SECOND FLOOR LEVEL - CONDUITS FOR CABLES |  | 70
| Total amount |  | 89
B10.A40.A5 | ZINC PLATED WIRE MESH | m
CONSTRUCTION FOR CABLES MADEOF HOT-DIP GALVANIZED STEEL FOR DROWNING AFTER TREATMENT
Compliance with standards: CEI 23-76, CEI 7-6 and subsequent variations.
Impact resistance: > 1J on room temperature (20°C ±5).
Mechanical resistance: minimum allowed load (values ​​measured for maximum arrow 1/200 medium capacity, the composition at 1/5 of the opening) measured in accordance with the appropriate performance standards:
_ constructions with h. 50mm, light between two brackets 1,5m:
* 18 kg/m for channels wide 50-100 mm;
* 27 kg/m for channels wide 150 mm;
* 33 kg/m for channels wide 200 mm;
* 63 kg/m for channels wide 300 mm;
* 104 kg/m for channels wide 400 mm;
* 120 kg/m for channels wide 500-600 mm;
_ constructions with h. 100 mm, light between two brackets 1,5m:
* 37 kg/m for channels wide 100 mm;
* 53 kg/m for channels wide 150 mm;
* 73 kg/m for channels wide 200 mm;
* 104 kg/m for channels wide 300-400 mm; * 125 kg/m for channels wide 500-600 mm.
Electrical characteristics:
_ electric continuity guaranteed by the constructor with the electrical resistance (at 12V max ca 50Hz, 25A) = <0.005 ohm per meter <= 0.05 ohm nearby compound.
Structural characteristics:
_structure is made of welded steel wire, hot-dipped galvanized for drowning after treatment with prior degreasing and pickling, and the final painting (for types that are required) epoxy resin or polyester;
_ safety edge without parts that contain sharp edges;
_ minimum mass of zink layer: 330 g/m2 +/-10%;
_ average thickness of zink layer: 50 micron +/- 10%.
_ cover (when required) of galvanized steel with the same treatment and structural characteristics of s.d., with the closure with the latch, i.e. by hook that can not be lost.
Behavior on the fire collored (upon request) autoestingueting.
Zinc plated wire mesh, size 300x55mm
| GROUND FLOOR LEVEL - CONDUITS FOR CABLES |  | 42
| GROUND FLOOR LEVEL - CONDUITS FOR CABLES |  | 27
| Total amount |  | 69
B10.A40.A51 | ZINC PLATED WIRE MESH | m
CONSTRUCTION FOR CABLES MADEOF HOT-DIP GALVANIZED STEEL FOR DROWNING AFTER TREATMENT
Compliance with standards: CEI 23-76, CEI 7-6 and subsequent variations.
Impact resistance: > 1J on room temperature (20°C ±5).
Mechanical resistance: minimum allowed load (values ​​measured for maximum arrow 1/200 medium capacity, the composition at 1/5 of the opening) measured in accordance with the appropriate performance standards:
_ constructions with h. 50mm, light between two brackets 1,5m:
* 18 kg/m for channels wide 50-100 mm;
* 27 kg/m for channels wide 150 mm;
* 33 kg/m for channels wide 200 mm;
* 63 kg/m for channels wide 300 mm;
* 104 kg/m for channels wide 400 mm;
* 120 kg/m for channels wide 500-600 mm;
_ constructions with h. 100 mm, light between two brackets 1,5m:
* 37 kg/m for channels wide 100 mm;
* 53 kg/m for channels wide 150 mm;
* 73 kg/m for channels wide 200 mm;
* 104 kg/m for channels wide 300-400 mm; * 125 kg/m for channels wide 500-600 mm.
Electrical characteristics:
_ electric continuity guaranteed by the constructor with the electrical resistance (at 12V max ca 50Hz, 25A) = <0.005 ohm per meter <= 0.05 ohm nearby compound.
Structural characteristics:
_structure is made of welded steel wire, hot-dipped galvanized for drowning after treatment with prior degreasing and pickling, and the final painting (for types that are required) epoxy resin or polyester;
_ safety edge without parts that contain sharp edges;
_ minimum mass of zink layer: 330 g/m2 +/-10%;
_ average thickness of zink layer: 50 micron +/- 10%.
_ cover (when required) of galvanized steel with the same treatment and structural characteristics of s.d., with the closure with the latch, i.e. by hook that can not be lost.
Behavior on the fire collored (upon request) autoestingieting.
Divider, H = 55 mm
| GROUND FLOOR LEVEL - CONDUITS FOR CABLES |  | 115
| FIRST FLOOR LEVEL - CONDUITS FOR CABLES |  | 235
| SECOND FLOOR LEVEL - CONDUITS FOR CABLES |  | 111
| GROUND FLOOR LEVEL - CONDUITS FOR CABLES |  | 10
| Total amount |  | 471
B10.A40.A6 | ZINC PLATED WIRE MESH | m
CONSTRUCTION FOR CABLES MADEOF HOT-DIP GALVANIZED STEEL FOR DROWNING AFTER TREATMENT
Compliance with standards: CEI 23-76, CEI 7-6 and subsequent variations.
Impact resistance: > 1J on room temperature (20°C ±5).
Mechanical resistance: minimum allowed load (values ​​measured for maximum arrow 1/200 medium capacity, the composition at 1/5 of the opening) measured in accordance with the appropriate performance standards:
_ constructions with h. 50mm, light between two brackets 1,5m:
* 18 kg/m for channels wide 50-100 mm;
* 27 kg/m for channels wide 150 mm;
* 33 kg/m for channels wide 200 mm;
* 63 kg/m for channels wide 300 mm;
* 104 kg/m for channels wide 400 mm;
* 120 kg/m for channels wide 500-600 mm;
_ constructions with h. 100 mm, light between two brackets 1,5m:
* 37 kg/m for channels wide 100 mm;
* 53 kg/m for channels wide 150 mm;
* 73 kg/m for channels wide 200 mm;
* 104 kg/m for channels wide 300-400 mm; * 125 kg/m for channels wide 500-600 mm.
Electrical characteristics:
_ electric continuity guaranteed by the constructor with the electrical resistance (at 12V max ca 50Hz, 25A) = <0.005 ohm per meter <= 0.05 ohm nearby compound.
Structural characteristics:
_structure is made of welded steel wire, hot-dipped galvanized for drowning after treatment with prior degreasing and pickling, and the final painting (for types that are required) epoxy resin or polyester;
_ safety edge without parts that contain sharp edges;
_ minimum mass of zink layer: 330 g/m2 +/-10%;
_ average thickness of zink layer: 50 micron +/- 10%.
_ cover (when required) of galvanized steel with the same treatment and structural characteristics of s.d., with the closure with the latch, i.e. by hook that can not be lost.
Behavior on the fire collored (upon request) autoestingueting.
Zinc plated wire mesh, size 400x55mm
| GROUND FLOOR LEVEL - CONDUITS FOR CABLES |  | 48
| FIRST FLOOR LEVEL - CONDUITS FOR CABLES |  | 363
| SECOND FLOOR LEVEL - CONDUITS FOR CABLES |  | 14
| GROUND FLOOR LEVEL - CONDUITS FOR CABLES |  | 10
| Total amount |  | 435
B30.A10.A3 | PVC FLEXIBLE PIPE | m
TUBO PROTETTIVO PIEGHEVOLE - CORRUGATO IN PVC PER POSA SOTTO TRACCIA
Compliance with standards: CEI 23-82, 23-39 and subsequent variations.
Classification: not less than 3321.
Tread resistance: >= 750N.
Impact resistance: >= 2J.
electric isolation resistance: >= 100Mohm a 500V per 1 min.
Dialectric rigidity: >= 2kV/mm a 50Hz per 15 min.
Fire reaction: non propagating fire.
System protection level: min. IP4X
PVC flexible pipe D=25mm
| GROUND FLOOR LEVEL - CONDUITS FOR CABLES |  | 385
| FIRST FLOOR LEVEL - CONDUITS FOR CABLES |  | 40
| GROUND FLOOR LEVEL - CONDUITS FOR CABLES |  | 30
| Total amount |  | 455
B30.A20.A25 | PVC RIGID PIPE | m
TUBO PROTETTIVO RIGIDO MEDIO IN PVC PER POSA IN VISTA O SOTTOTRACCIA
Compliance with standards: 23-51, 23-54 and subsequent variations.
In line with tables: CEI-UNEL 37118, 37119, 37120.
Classification: not less than 3321.
Tread resistance: >= 750N.
Impact resistance: >= 2J.
electric isolation resistance >= 100Mohm a 500V per 1 min.
Dialectric rigidity: >= 2kV/mm a 50Hz per 15 min.
Fire reaction:
non propagating fire;
low content of alogen gasses (as by CEI 20-37).
System protection level: defined by type.
PVC rigid pipe IP65 D=40mm
| GROUND FLOOR LEVEL - CONDUITS FOR CABLES |  | 509
| GROUND FLOOR LEVEL - CONDUITS FOR CABLES |  | 132
| Total amount |  | 641
B30.A20.A26 | PVC RIGID PIPE | m
TUBO PROTETTIVO RIGIDO MEDIO IN PVC PER POSA IN VISTA O SOTTOTRACCIA
Compliance with standards: 23-51, 23-54 and subsequent variations.
In line with tables: CEI-UNEL 37118, 37119, 37120.
Classification: not less than 3321.
Tread resistance: >= 750N.
Impact resistance: >= 2J.
electric isolation resistance >= 100Mohm a 500V per 1 min.
Dialectric rigidity: >= 2kV/mm a 50Hz per 15 min.
Fire reaction:
non propagating fire;
low content of alogen gasses (as by CEI 20-37).
System protection level: defined by type.
PVC rigid pipe IP65 D=50mm
| SECOND FLOOR LEVEL - CONDUITS FOR CABLES |  | 70
| Total amount |  | 70
B40.A10.A6 | ZINC PLATED METAL PIPE | m
TUBO PROTETTIVO RIGIDO FILETTABILE IN ACCIAIO ZINCATO ELETTROSALDATO
Compliance with standards: 23-39, 23-54 and subsequent variations; UL94 V-1.
Classification: not less than 5557.
Tread resistance: >= 4000N.
Impact resistance: >= 6,8J.
electric resistance < 5mohm/m.
Construction caracteristics:
rigid tube profiled by steal zinc sheets with Sendzimir method, welded with zinc on welding points, cold flexible;
- raccordi e giunzioni con altri elementi dell'impianto o fra i tubi stessi di tipo filettato con passo metrico ISO a garanzia di continuita' metallica oltreche' del grado di protezione richiesto.
junctions and connections with other elements with ISO metric thread as guarantee of metallic as well as required protection level. - color (if required by type) based on epossidic resine
System protection leve: min. IP4X.
Fire reaction: collor (if required), autoestingueting
Zinc plated metal pipe D=50mm
| ROOF LEVEL - CONDUITS FOR CABLES |  | 13,5
| Total amount |  | 13.5
B70.A21.A1 | FLAME-FRINGE BARRIER WITH REMOVABLE BAGS BARRIERA FRANGI-FIAMMA A SACCHETTI AMOVIBILI Flame-fringe barrier composed by tamponage bags longitudinal disposed on cables wall route or cement channel In line with Minsitry of interiors regulation | dm2
n.91 del 14.09.61. Construction caracteristics : - tamponage bags in glass fiber sacchetti di contenimento in tessuto di fibra di vetro fitted plot, filled with tissotropic mixture having tickeness and width capable to be easely positioned on order to guarantee tamponage of interstices
and having length appropriate to realize barrier rage which will guarantee required fire resistance ; Minimal tickeness of the barrier: appprox. 200 mm equal to bag width
Fire reaction: untill resistance class REI 180.
Flame-fringe barrier with removable bags REI 180
| GROUND FLOOR LEVEL - CONDUITS FOR CABLES |  | 6
| FIRST FLOOR LEVEL - CONDUITS FOR CABLES |  | 20
| SECOND FLOOR LEVEL - CONDUITS FOR CABLES |  | 7
| GROUND FLOOR LEVEL - CONDUITS FOR CABLES |  | 5
| Total amount |  | 38
TOTAL 02 - CABLE CONDUCTORS
08 - DISTRIBUTION TERMINAL AND LIGHT SUPPLY
M30.A10.A1 | POWER SUPPLY POINTS Power supply is composed by : - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks (quoted appart) | n
; - eventualy transit boxes and jack boxes. Type of cabbling should be prescribed by chapter and dimensioned on the basis of efective voltage
used by devices (motored door/tent, cabinets, etc.) . In the case of existing conduits just the price of cabbling shoud be indicated . In the case of supply and instalation
of only conduits and boxes price for preparaty works should be indicated. Used materials should be in line with specific chaapter of present study.
Wall embedded power with PVC flexible pipe and 2x1.5 cable
| GROUND FLOOR LEVEL - DISTRIBUTION TERMINAL AND LIGHT SUPPLY |  | 8
| FIRST FLOOR LEVEL - DISTRIBUTION TERMINAL AND LIGHT SUPPLY |  | 2
| SECOND FLOOR LEVEL - DISTRIBUTION TERMINAL AND LIGHT SUPPLY |  | 2
| GROUND FLOOR LEVEL - DISTRIBUTION TERMINAL AND LIGHT SUPPLY |  | 4
| Total amount |  | 16
TOTAL 08 - DISTRIBUTION TERMINAL AND LIGHT SUPPLY
12 - SOUND DIFUSOR DEVICE
Q100.A10.A1 | CONNECTION FOR SOUND SPEAKER | n
PUNTO DIFFUSIONE SONORA EQUIVALENTE
Equivalent point for the spread of sound, consists of:
_ part of quota of junction box installed in the riser; usponski vod;
_ installation pipes for cables that start from the junction box installed along the riser to the speakers (separately calculated);
_ the junction of the head terminal (unless otherwise indicated);
_ lines that start from the junction box installed along the riser to the speakers (types in which it is required);
_ final box (if necessary) with matching cover with a hole for the outlet and cable gland kablovska uvodnica
In the case of point for the spread of sound for an audible alarm in accordance with EN 60849 will have to provide the following changes / additions:
_ junction terminals (unless otherwise indicated) of the ceramics;
_lines that start from the junction box installed along the riser to the speakers (types in which it is required) from cable FTG10(O)M1 CEI 20-45 fireproof;
_ protective fuses and fuse box, both made of ceramics
Connection for wall sound speaker with PVC flexible pipe and cables
| GROUND FLOOR LEVEL - SOUND SYSTEM |  | 4
| FIRST FLOOR LEVEL - SOUND SYSTEM |  | 4
| SECOND FLOOR LEVEL - SOUND SYSTEM |  | 4
| Total amount |  | 12
Q100.A10.A3 | CONNECTION FOR SOUND SPEAKER | n
PUNTO DIFFUSIONE SONORA EQUIVALENTE
Equivalent point for the spread of sound, consists of:
_ part of quota of junction box installed in the riser; usponski vod;
_ installation pipes for cables that start from the junction box installed along the riser to the speakers (separately calculated);
_ the junction of the head terminal (unless otherwise indicated);
_ lines that start from the junction box installed along the riser to the speakers (types in which it is required);
_ final box (if necessary) with matching cover with a hole for the outlet and cable gland kablovska uvodnica
In the case of point for the spread of sound for an audible alarm in accordance with EN 60849 will have to provide the following changes / additions:
_ junction terminals (unless otherwise indicated) of the ceramics;
_lines that start from the junction box installed along the riser to the speakers (types in which it is required) from cable FTG10(O)M1 CEI 20-45 fireproof;
_ protective fuses and fuse box, both made of ceramics
Connection for false ceiling sound speaker with PVC flexible pipe and cables
| GROUND FLOOR LEVEL - SOUND SYSTEM |  | 19
| FIRST FLOOR LEVEL - SOUND SYSTEM |  | 44
| SECOND FLOOR LEVEL - SOUND SYSTEM |  | 18
| GROUND FLOOR LEVEL - SOUND SYSTEM |  | 16
| Total amount |  | 97
Q100.A20.A1 | CONNECTION FOR MICROPHONE OUTLET | n
PUNTO PRESA MICROFONICA EQUIVALENTE
Connection for microphone is composed by:
part of quota of junction box installed on voltage;
installation of cables from the junction box installed along the voltage point to the jack (separately calculated);
transition and derivation cassets d.80 and 100x100 mm (where required);
connection of cables on microphone base.
signal cables and electrical supply fire proof for 60 minutes to the unit and jack connection, central and mic laterals
Microphone outlet with connection flexible pipe and cables
| GROUND FLOOR LEVEL - SOUND SYSTEM |  | 2
| Total amount |  | 2
Q20.A30.A1 | LOUDSPEAKERS | n
6 W 5" ceiling loudspeaker EN 54 with fire dome, metal
Ceiling loudspeaker specifically designed for use in buildings where performance of systems for voice evacuation announcements is governed by regulations.
It is designed for flush mounting in suspended ceiling
Ideal for even sound distribution.
The fire dome increases protection of the cable termination.
The driver unit is impregnated against moisture.
Ceramic terminal block
Thermal fuse.
Compliant with EN 54-24 standard
_ rated voltage: 100/70V;
_ impedance: at least 8 ohm;
_ IP protection: min IP32.
Constructive characteristics:
_dual cone speakers with wide frequency response and diffusion.
Ambient temperature -25 °C ... 55 °C
Rated Power 6 W
Transformer power taps 6 / 3 / 1,5 / 0,75 W
Material: Metal
Loudspeakers for flush mounting into suspended ceilings, power 6W
Loudspeaker for false ceiling installation, power 6W
| GROUND FLOOR LEVEL - SOUND SYSTEM |  | 19
| FIRST FLOOR LEVEL - SOUND SYSTEM |  | 44
| SECOND FLOOR LEVEL - SOUND SYSTEM |  | 18
| GROUND FLOOR LEVEL - SOUND SYSTEM |  | 16
| Total amount |  | 97
Q20.A30.A2 | LOUDSPEAKERS | n
6 W 6.5" round wall or ceiling surface mount loudspeaker, metal
The loudspeaker for voice alarm made of powder-coated metal in white with high degree of efficiency and a high-quality 200 mm broadband loudspeaker chassis.
Can be installed on ceiling and walls, where recessed mounting is not possible.
Flat and elegant design for unobtrusive installations provided with a metal back plate.
The loudspeaker is equipped for highest security requirements with a ceramic terminal and a thermal fuse.
The Chassis is protected against moisture by impregnation. EN 54 luodspeaker offers a powerful sound besides the high safety standard.
Ambient temperature -20 °C ... 80 °C
Rated Power 10 W
Transformer power taps 10 / 6 / 3 / 1,5 W
| GROUND FLOOR LEVEL - SOUND SYSTEM |  | 4
| FIRST FLOOR LEVEL - SOUND SYSTEM |  | 4
| SECOND FLOOR LEVEL - SOUND SYSTEM |  | 4
| Total amount |  | 12
Q20.A70.A1 | PUBLIC ADDRESS AND EVAC CONTROL UNIT | n
Central control element of the Public address and Voice Alarm system
4 independent amplifier channels, through which it can operate a total of 24 loudspeaker zones or 4 loudspeaker rings
There is also a possibility to combine spur and loop technologies in a DOM.
The loudspeaker lines are continuously monitored for short circuit, fault to ground, interruptions, as well as impedance deviation.
In the event of a faulty output, an emergency amplifier can dynamically replace it. The switchover is done automatically. Defective loudspeaker zones are separated in a non-reactive manner.
A DOM contains storage capacities for prerecorded audio messages that can be used for alarm texts and signals (evacuation alarm, all-clear signal) and caution signals (gongs).
The volume of every source and every amplifier channel can be regulated.
Additional filters such as parametric equalizers, high-pass and low-pass filters and delays are also available.
For special applications like e.g. tunnel, a delay in all for channels can be programmed up to 9.9 sec.
Authorized in compliance with EN 54-16
Compliant with IEC 60849, EN 60849 and EN50849
Networkable via Ethernet
Permanent monitoring of all functionally relevant system components
Automatic and dynamic switching to redundant emergency amplifiers
Automatic volume control (AVC), also during announcements
Remote monitoring and configuration via the network
24 V DC emergency power supply
Connection to a NTP server via Ethernet is possible
Up to 4 DAL bus links
Speech or audio memory up to 1 h
Rated voltage 90 .. 264 V AC
Power consumption 50 / 80 W
Contact load relay 100 V DC/1 A
Ambient temperature -5 °C ... 55 °C
CENTRAL UNIT OF PUBLIC ADDRESS AND VOICE ALARM SYSTEM
| GROUND LEVEL - PUBLIC ADDRESS SYSTEM |  | 1
| Total ammount |  | 1
| UNIVERSAL INTERFACE MODULE | n
Universal Interface Module UIM
The interface module of the Public Address and Voice Alarm system for connecting:
two analog audio inputs,
two analog audio outputs,
48 control contacts.
For eight control contacts, short-circuit and interruption monitoring can be activated.
The UIM is connected to the DOM module via the DAL bus.
It digitizes two analog audio inputs, i.e. from a CD player or a hazard detection system, and transmits the digitized audio data to the DOM module via the DAL bus.
Control contacts allows for an external control of the system, and information about the status of the system is made available.
Approval: G 210122
EN 54-16 certified
Two analog audio inputs/outputs
48 contacts freely programmable as inputs and outputs
Digital Audio link (DAL) to DOM
Inputs max. 36 V DC
Outputs 36 V DC/50 mA
Ambient temperature -5 °C ... 55 °C
Universal Interface Module UIM
| GROUND LEVEL - PUBLIC ADDRESS SYSTEM |  | 1
| Total ammount |  | 1
CD?DVD PLAYER
Dual Integrated DVD / CD Player and MP3 Player and FM / AM tuner, as well as USB/SD interface
The device supports two modes of operation.
Mode of operation 1: DVD/USB/SD and FM/AM tuner can be operated simultaneously via two separate ports.
Mode of operation 2: DVD/USB/SD and FM/AM tuner can be switched.
DVD videos and JPEG are supported. The connection to the VARIODYN D1 system is done via a cinch audio link. Suitable for 24-hour operation.
Two independent audio outputs for DVD / USB / SD and FM / AM Tuner
Two independent volumes can be set
A combined audio output
Rated voltage 230 V AC
Output voltage 2 V DC ± 0,2 V
Power consumption 13 W
Inputs FM 75 Ω, USB-Port, SD-Port
Outputs 1 x Cinch for FM/AM-Tuner, 1 x Cinch for DVD/USB/SD, 1 x Cinch for mixed signals
Dual Integrated DVD / CD Player and MP3 Player and FM / AM tuner, as well as USB/SD interface
| GROUND LEVEL - PUBLIC ADDRESS SYSTEM |  | 1
| Total ammount |  | 1
in the case of amplificator malfunction appropriate LED will give indication untill malfunctioning is repristinated.
Amplificator management unit of type RCF DXT MT5708 or equivalent approved.
n.1 UPS unit (Uninterruptible Power Supply) with power 3kVA and 1 hour authonomy.
Supply include cabbling and control of lines on installation.
Software customizing with defining grafic maps where building planimetry should be visualized as well as terminal unuts and amplificators.
Activation and testing of the system should be performed by authorized manufacturer personnel. Supply should also include training for central personnel to be employed.
Public address and evac control unit
| GROUND FLOOR LEVEL - VIDEO SURVEILLANCE SYSTEM |  | 1
| Total amount |  | 1
Q20.A70.A2 |  | n
AMPLIFIERS
The power amplifier with two independent amplifier channels, each with 400 Watt, part of Honeywell Public Address and Voice Alarm system. The power amplifiers are controlled and monitored by DOM.
Compliant with EN 60849 and EN 50849
EN 54-16 certified
Class D two channel amplifier
Protected against overload, short- circuits and overheating
24 V DC emergency power supply input
General display element
System voltage (green LED)
CPU status (green LED)
Combined fault (yellow LED)
24 V emergency power supply (yellow LED)
Display element per amplifier channel
Operation (green LED)
Amplifier channel status (green LED)
Amplifier channel error (yellow LED)
Clip display (yellow LED)
Rated voltage 230 V AC
Rated current 4.5 A
Power output 2 x 400 W
Ambient temperature -5 °C ... 55 °C
The power amplifier with two independent amplifier channels, each with 400 Watt
GROUND LEVEL - PUBLIC ADDRESS SYSTEM
| Total amount |  | 3
3
Q20.A70.A6 |  | n
MICROPHONIC POSTATION
Digital Call microphone Station serves for the selection of loudspeaker circuits and for setting off speech announcements as well as various gong or alarm sounds, with audio input.
It features 12 freely configurable keys, 13 LED's and a gooseneck microphone.
Digital Calling station supports redundant cable connections to two separate DOMs
The function of the microphone of the digital paging microphone is permanently acoustically monitored.
Also provides an external audio input and output which can be used for connecting audio devices such as CD players.
Every DCS in the system can simultaneously generate and receive different voice transmissions and control signals.
A digital paging microphone can be offset up to 300 m by means of a copper cable. Extension to a greater distance is possible with fiber optic (FO) cables.
If more keys and/or LEDs are needed, it is possible to add up to six digital key modules, which allows the increase of the total number of available keys and LEDs to 120 per call station.
High failure safety due to redundant transmission route
Cost-effective copper cabling
Elektret gooseneck microphone with cardioid pattern
Permanent monitoring of the microphone and cable
Loudspeaker for monitoring and for intercom operation between other paging stations
24-bit AD/DA converter
Independent additional audio input/output e.g. for audioplayer
12 freely configurable keys with independent programmable LED
A separate LED, programmable in yellow or red
Can be used redundantly as well as non-redundantly
Current consumption < 70 mA
Ambient temperature -5 °C ... 55 °C
Digital Call microphone Station serves for the selection of loudspeaker circuits and for setting off speech announcements as well as various gong or alarm sounds, with audio input.
| GROUND LEVEL - PUBLIC ADDRESS SYSTEM |  | 2
| Total amount |  | 2
EMERGENCY POWER SUPPLY
Emergency manager for use as emergency power supply of an Voice Alarm application.
3 individually fused outputs for control devices (DOM)
6 individually fused high power outputs for power amplifiers
Approval according to EN 54-4 (A2)
LED indicators for power, battery, consumer
Potential free contacts for forwarding of error messages
Battery capacity up to 225 Ah
Rated voltage 230 V AC
Output voltage 24 V DC
Output current max.150 A
Ambient temperature -5 °C ... 45 °C (at 100 % load)
UPS power supply for Public Address and Voice Alarm
GROUND LEVEL - PUBLIC ADDRESS SYSTEM
| Total amount |  | 1
TOTAL 12 - SOUND DIFFUSOR DEVICE
13 - FIRE DETECTION DEVICE
R10.A11.A11 |  | n
EXPANSION UNIT FOR REMOTE TERMINALS
Card to be integrated in fire detection central as per position R10.A11.A2 for integration of remote terminal R10.A18.A1
Expansion unit for remote terminal
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 2
| Total amount |  | 2
R10.A11.A2 | MICROPROCESSOR FIRE DETECTION CONTROL UNIT FOR ANALOGIC ELEMENTS | n
Self contained addressable control panels capable of operating in a network of at least 32 panels and terminals or 16 panels if connected to a management station system. Panels shall have LPCB, VDS and FM approval to EN54 and meet the relevant requirements of country regulation.
Control panels must provide at least the following: Type FC2040 with housing, with four integrated detection loops, or eight with loop extension for the connection of up to 504 devices
Central fire detection unit is fully integrable to Building Management System, communication via BACNet over IP protocol using built-in RJ45 socket without need for hardware gateways, on panel site licence L2 is needed in order to enable communication.
In addition, the loop extension card allows doubling the number of loops keeping unchanged the number of addresses.
One monitored sounder circuit.
Designated monitored fire output for connection to remote ARC communication equipment. This circuit also provides operation in degrade mode according to EN54 requirements for systems with more than 512 detectors.
Designated fire output with clean contacts. Provides operation in degrade mode according to EN54 requirements for systems with more than 512 detectors.
Designated monitored fault output for connection to remote ARC communication equipment.
Designated fault output with dry contacts.
Eight free programmable input/outputs.
Integral 24Vdc monitored power supply to EN54-4 with integral battery backup for up to 72hrs + 30minutes full alarm.
The panel construction shall allow for:
Sufficient cable entries for all connectable detection loops, sounder circuits, network cables & mains supplies.
Attractive removable molded front cover with metal back box providing minimum ingress protection of IP30.
Surface or semi-flush mounting.
Manned / Unmanned operation:
Control panels shall have a dedicated monitored fire brigade communication output and shall be capable of operating in two distinct modes:
Mode Manned – Alarms from automatic detectors will activate the system sounders and initiate a timer (T1) programmable from 10s to 5 minutes. Providing a responsible person acknowledges the panel within this time period no signal will be sent to the fire brigade communication equipment. Upon acknowledgement a second timer (T2) programmable from 10s to 10 minutes will be initiated. Again providing the system can be reset within this time period no signal will be sent to the fire brigade communication equipment. Operation of any manual call point will immediately cancel the delay timers and a signal will be sent to the fire brigade communication equipment.
Mode unmanned – Alarms from any manual call point or automatic detector will immediately send a signal to the fire brigade communication equipment.
It shall be possible to select mode manned by any of the following:
Automatically selected during working hours using internal system clock with automatic switching of summer / winter time. It may be possible to extend working hours by up to 4 hours (programmable) by pressing a separate control. (Extend working hours control). This extension can be subsequently cancelled by pressing a (cancel working hour’s extension control). Or
Manually selected with premises manned control button. Or
Automatically selected when intrusion system unset. Or
Automatically selected with input from Access control system.
Delays to the fire brigade communication equipment can be cancelled by pressing the alarm delay off control on the control panel.
Fault attendance monitoring: Control panels shall have a dedicated monitored output to communicate with fault communication equipment this shall work in two distinct modes manned & unmanned.
Mode manned - A fault activates local alarming and starts the delay t1 for attendance monitoring. The operating personnel acknowledge the fault at the operating terminal prior to the expiry of t1, thus silencing the local alarming equipment. If the fault is not acknowledged, global alarming is activated before the expiry of t1. Simultaneously to the delay t1, the service intervention time ts starts in the 'intervention monitoring' part. If the fault is not eliminated prior to the expiry of ts, the maintenance personnel are called up.
Mode unmanned – Faults are reported directly.
Conditions: Fire alarm control panels shall be capable of receiving and handling all of the following conditions from field devices:
Alarm.
Pre-alarm.
Device fault.
Device impaired.
Device isolated.
Device isolator activated
Detector drift compensation limit exceeded.
CO pre-warning {01105}
CO warning {01105}
Programmable functions: Fire alarm control panels shall be capable of being configured to do all of the following:
Manned / unmanned mode:
Selectable by time of day.
Selectable on specific days.
Selectable by remote input.
Selectable manually.
Programmable times for presence & investigation times.
Selectable for sounders during first timer, off, on or pulsed.
Detector behavior:
It shall be possible to select the required parameter set for each detector at the panel.
It shall be possible to select an alternative parameter set for ASA technology detectors in mode manned.
It shall be possible to configure each individual device to work within the manned/unmanned concept or not.
Control cause & effect:
Fire alarm control panels shall have the possibility to create complex cause & effect controls including AND, OR & NOT functions or combinations thereof.
In addition, controls can be programmed with respect to panel functions and be time related.
It shall be possible to program separate cause & effect for CO pre-warning & warning signals. {01105}
Sounders:
It shall be possible to select sounder tones and volume from the control panel. Up to two different tones shall be selectable for each sounder and configured to operate with different cause & effect scenarios.
Alarm indicators:
It shall be possible to configure an individual extension LED to be activated from any of several detectors.
Disablement – Fire alarm control panels shall allow the isolation of any individual device, zone, section or area. Any isolation shall have the ability to be restored after a pre-defined time period.
Renovation mode – Fire alarm control panels shall include a renovation mode which can be set during periods of temporary building renovation. This mode sets all detectors in the selected area to a lower sensitivity “Renovation” parameter set.
Test Modes – Fire alarm control panels shall allow the following tests to be performed:
Lamp test – The control panel shall include a control button that will illuminate all panel indicators and highlight the complete display.
Detector test – The control panel can set zones into detector test mode. This increases the sensitivity of all detectors within that zone. On test the detector alarm indicator shall be illuminated but sounders & controls shall not be activated. Base sounders directly connected to the detector tested shall operate briefly.
Installation test - The control panel can set zones into detector test mode. This increases the sensitivity of all detectors within that zone. On test the detector alarm indicator shall be illuminated and all programmed sounders and controls shall operate as required.
Walk test – The operating panel can set groups in walk test mode. When a detector is triggered, the alarm sounders are activated for 10 seconds.
Floor repeater panels with control – The control panel shall allow connection of up to 4 repeater panels on each detection loop. These panels will repeat the indication of the main display and allow for silencing and reset of the system. In addition these repeaters will have 6 freely programmable buttons and associated indicators. Repeater panels may be powered from the detection loop or from a remote 24Vdc power supply. {01230 AND 01240}
Indicating only floor repeater panels – The control panel shall allow connection of up to 4 repeater panels on the detection loop. These panels will repeat the indication of the main display. Repeater panels may be powered from the detection loop or from a remote 24Vdc power supply. {01250}
Additional cards – Networkable fire alarm control panels shall allow the integration of the following additional cards: {01120 AND 01130 AND 01140 AND 01150 AND 01160 AND 01170 AND 01180}
Loop extension card
2 x 4 way sounder cards.
Network cards.
RS232 interface card
RS485 interface card.
Additional cards – Networkable fire alarm control panels (756 devices) shall allow the integration of the following additional cards: {01184}
Detection loop card (4 loops)
Loop extension card
Conventional card (8 stubs)
Detection loop card for MS9i addressable detector series (2 loops)
Detection loop card for Interactive addressable detector series (1 loop)
Detection loop card for Interactive Ex addressable detector series (1 stub)
Detection loop card for AnalogPLUS addressable detector series (4 loops)
I/O card (programmable)
2 x 4 way sounder cards.
Network cards.
RS232 interface card
RS485 interface card.
Additional cards – Networkable expandable fire alarm control panels (1512 devices) shall allow the integration of the following additional cards: {01190}
Detection loop card (4 loops)
Loop extension card
Conventional card (8 stubs)
Detection loop card for MS9i addressable detector series (2 loops)
Detection loop card for Interactive addressable detector series (1 loop)
Detection loop card for Interactive Ex addressable detector series (1 stub)
Detection loop card for AnalogPLUS addressable detector series (4 loops)
I/O card (programmable)
2 x 4 way sounder cards.
Network cards.
RS232 interface card
RS485 interface card.
Additional cards – Networkable expandable fire alarm control panels (5000 devices) shall allow the integration of the following additional cards: {01195}
Detection loop card (4 loops)
Loop extension card
Conventional card (8 stubs)
Detection loop card for MS9i addressable detector series (2 loops)
Detection loop card for Interactive addressable detector series (1 loop)
Detection loop card for Interactive Ex addressable detector series (1 stub)
Detection loop card for AnalogPLUS addressable detector series (4 loops)
I/O-Card (programmable)
I/O Card (remote transmission)
I/O Card (sounder / supervised)
2 x 4 way sounder cards.
Network cards.
RS232 interface card
RS485 interface card
The fire alarm panel shall allow the exchange of defect module and verify if the firmware of the new card has the correct version for the main software application
The fire alarm panel shall allow the exchange of defect module bus cards in a running system {01184 AND 01190 AND 01195}
The Control Panel shall allow to configure which event categories should be displayed
Up to 4 alarm concepts within a Fire alarm control panel shall be available {01120 AND 01130 AND 01140 AND 01150 AND 01160 AND 01170 AND 01180 AND 01184}
Up to 8 alarm concepts within a Fire alarm control panel shall be available {01190}
Up to 24 alarm concepts within a Fire alarm control panel shall be available {01195}
Programmable time for inputs before it is evaluated as active.
Alarm counter, which can be set with parameters for:
Alarms counter from one or more fire control panel
Test alarms will be counted as yes / no
Fiber optic cable network modules single mode 40 km, multi mode 4 km.
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 1
| Total amount |  | 1
R10.A12.A1 | GAS DETECTION CONTROL UNIT | n
CENTRALE RIVELAZIONE GAS
Technology Microprocessor 16 bits
Voltage From 9V to 15V DC
Maximum consumption 180 mA per module line
Maximum length C.U. /
dtrs 1,000 m
Cable Shield cable 4 wires for main power – 2 x 1.5mm2
&
2 x 0,25 mm2 twisted pair for communicationsMaximum
capacity per
line Up to 16 detectors
Reading modes Sequential or Maximum reading
Data presentation LCD display 16 x 2 lines of back-lit alphanumeric
characters
Reading speed 2 s per detector -sequential mode- & 2 s -maximum
readingVentilation
outputs 4 independent outputs per module line 3A 250V AC or
3A 30V DC dry contact fuse-protected with optical
status indicator and de-parasiting circuit and ground
branching
Alarm output 1 general. Dry contact relay 5A 250V AC or 8A 30V
DC dry contact and fuse-protected
Fault output 1 general. Dry contact C, NO
Battery output Up to 2 batteries 12V DC 7,5Ah
Power supply 13,8V 4,5A voltage stabilized and limited current
Gas detection control unit for 2 serial lines
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 1
| Total amount |  | 1
R10.A18.A1 | REMOTE TERMINAL FOR FIRE DETECTION SYSTEM | n
TERMINALE DI RIPETIZIONE ALLARMI REMOTO
Electromeccanical caracteristics:
Nominal functioning voltage : 24V c.c.;
Construction caracteristics:
microprocessor control;
retro lighting display with different collor depending on status, with clear text of at least n. 40 characters on n.2 lines for visualisation of allarm or malfunction events limited to specific zone trough software programmation ;
connection to central trough dedicated lineas on n. 2 conduits;
internal sonor allarm;
"sheet" keys with following caracteristics:
* stop of local sonor allarm;
* visualisation od events code.
Price of pannels is inclusive of: programmation and activation by specialized technician
Remote terminal for visualization alarm and control signal (fire detection system)
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 1
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 1
| Total amount |  | 2
R10.A200.A1 | WORK FOR ACTIVATION OF FIRE AND GAS DETECTION SYSTEM | n
ATTIVAZIONE E COLLAUDO DELL'IMPIANTO RIVELAZIONE FUMI E GAS
Activation of the system by specialized technician autorized by manufacturer of the system.
Work for activation of fire and gas detection system
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 1
| Total amount |  | 1
R10.A32.A1 | TERMIC ANALOG DETECTOR | n
Heat detectors shall be intelligent devices with integrated ASA algorithms for comparison with actual sensor signals ensuring reliable detection, FDNet communication
Detectors should fulfill and be approved to EN54-5.
In addition the detector shall include:
1. Selectable application specific ASA parameter sets.
2. Communication of 3 different danger levels for differentiated alarm activation.
3. Programmable time related switching of detector behavior.
4. The facility to detect if the detector is in an unsuitable environment and give a separate warning of such to the panel.
5. An internal self test facility to ensure correct operation of the thermal sensor & electronics. Faults shall be reported with separate signals to the control panel.
6. Redundant operation with twin thermal sensors.
7. An integral short circuit isolator.
8. A separately controllable remote indicator output for activation from this or other detectors.
9. An integral response indicator with 360° viewing angle.
10. Wireless communication device to facilitate testing; enable readout of current status and wiring diagnostics. In addition the detector shall give data on its length of time in service to aid scheduled maintenance routines.
11. Operation in the temperature ranges -25°C to + 65°C
12. EMC compatibility of 50V/m
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 2
| SECOND FLOOR LEVEL - FIRE DETECTION |  | 5
| Total amount |  | 7
R10.A36.A1 | ADDRESSABLE SMOKE DETECTOR FOR VENTILATION SYSTEM | n
ADDRESSABLE OPTICAL ANALOG DETECTOR
Optical smoke detectors shall incorporate Advanced Signal Analysis (ASA) whereby the signals from the detectors sensors are compared with a dynamic algorithm set thus enhancing detection speed and false alarm rejection. FDNet communication
Detectors should fulfill and be approved to EN54-7.
The detector shall have been designed to have high tolerance to dust, dirt, temperature fluctuations and air currents.
In addition the detector shall include:
1. Selectable application specific ASA parameter sets.
2. Programmable time related switching of detector behavior.
3. 3 different danger levels for differentiated alarm activation.
4. Compensation for the gradual build up of dust & dirt to ensure a consistent level of detection over time. When the detector reaches a point where it can no longer retain this consistent detection a separate warning signal shall be given to the control equipment.
5. The facility to detect if the detector is in an unsuitable environment and give a separate warning of such to the panel.
6. An internal self test facility to ensure correct operation of the optics & electronics. Faults will be reported with separate signals to the control panel.
7. An integral short circuit isolator.
8. A separately controllable remote indicator output for activation from this or other detectors.
9. An integral response indicator with 360° viewing angle.
10. Wireless communication device to facilitate testing; enable readout of current status and wiring diagnostics. In addition the detector shall give data on its length of time in service to aid scheduled maintenance routines.
11. Operation in the temperature ranges -10°C to + 60°C
12. EMC compatibility of 50V/m
| SECOND FLOOR LEVEL - FIRE DETECTION |  | 8
| Total amount |  | 8
R10.A40.A1 | ADDRESSABLE SMOKE DETECTOR | n
ADDRESSABLE OPTICAL ANALOG DETECTOR
Optical smoke detectors shall incorporate Advanced Signal Analysis (ASA) whereby the signals from the detectors sensors are compared with a dynamic algorithm set thus enhancing detection speed and false alarm rejection. FDNet communication
Detectors should fulfill and be approved to EN54-7.
The detector shall have been designed to have high tolerance to dust, dirt, temperature fluctuations and air currents.
In addition the detector shall include:
1. Selectable application specific ASA parameter sets.
2. Programmable time related switching of detector behavior.
3. 3 different danger levels for differentiated alarm activation.
4. Compensation for the gradual build up of dust & dirt to ensure a consistent level of detection over time. When the detector reaches a point where it can no longer retain this consistent detection a separate warning signal shall be given to the control equipment.
5. The facility to detect if the detector is in an unsuitable environment and give a separate warning of such to the panel.
6. An internal self test facility to ensure correct operation of the optics & electronics. Faults will be reported with separate signals to the control panel.
7. An integral short circuit isolator.
8. A separately controllable remote indicator output for activation from this or other detectors.
9. An integral response indicator with 360° viewing angle.
10. Wireless communication device to facilitate testing; enable readout of current status and wiring diagnostics. In addition the detector shall give data on its length of time in service to aid scheduled maintenance routines.
11. Operation in the temperature ranges -10°C to + 60°C
12. EMC compatibility of 50V/m
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 15
| FIRST FLOOR LEVEL - FIRE DETECTION |  | 82
| SECOND FLOOR LEVEL - FIRE DETECTION |  | 53
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 16
| Total amount |  | 166
R10.A50.A1 | RESPONSE INDICATOR | n
OPTICAL REPETITOR
Alarm indicators are connected to automatic fire detectors in order to indicate quickly the source of an alarm signal from detectors which are not easily accessible or visible.
Alarm indicators are connected to automatic fire detectors in order to indicate quickly the source of an alarm signal from detectors which are not easily accessible or visible
Alarm indicators are mounted with two screws either directly to a door frame
operating voltage:5-8 V c.c.;
protection level: min. IP55.
current ma 35mA
Connection terminals max 1.5mm2
Response led indicator
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 7
| FIRST FLOOR LEVEL - FIRE DETECTION |  | 15
| SECOND FLOOR LEVEL - FIRE DETECTION |  | 56
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 12
| Total amount |  | 90
R10.A52.A1 | OPTICAL ACOUSTIC WARNING TABLE | n
OPTICAL ACOUSTIC COMMAND TABLE FOR FIRE SIGNALIZATION
Compliance with standards: EN 54-3.
Electromechanical characteristics:
operating voltage: 20-30 V c.c.;
protection level: min. IP30 for indoor installations,IP65 for outdoor installation.
Structural characteristics:
body of self-extinguishing thermoplastic material with red front part with the inscription "FIREPROOF ALARM" or "ALARM FOR GAS";
optical and acoustic signals that can be adjusted (pulse or fixed);
acoustic signalization: min. 90db;
led for operating signalization;
rechargeable battery 24V.
Optical acoustic warning fire panel with self powering kit, indoor installation
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 4
| FIRST FLOOR LEVEL - FIRE DETECTION |  | 8
| SECOND FLOOR LEVEL - FIRE DETECTION |  | 4
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 2
| Total amount |  | 18
R10.A61.A1 | TELEPHONE DIALER | n
COMBINATORE TELEFONICO A SINTESI VOCALE E/O DIGITALE
Elettromeccanical caracteristics:
Nominal functioning voltage: 12V c.c.;
ate least n. 2 entrance channels devided in:
* n. 2 of allarm;
* n. 1 battery status;
* n. 1 missing of network;
registration of at least n.6 voice messages devide in:
* n. 4 of allarm of duration non superior of 10 seconds;
* n. 1 common of duration not over 9 seconds;
* n. 1 of waiting of at least 2 seconds.
at least n. 2 exits ( n.1 relè e n.1 open collector).
Construction caracteristics:
metal cassette with eventual antimanumission;
keyboard and visualisation display, programming, memorization and modification of phone numbers;
programmation on NVRAM memory;
possibility of programmation of at least n.8 telephone number as vocal or digital and free connections of numbers with allarm messages;
visualisation trough user code of at least n. 30 backup events;
internal 12Vcc battery with authonomy of at least 1h.
Supply and instalation with signal cables of connection to fire detecting central, energy supply, system programmation
Telephone dialer
| GROUND FLOOR LEVEL - EVAC SYSTEM |  | 1
| Total amount |  | 1
R10.A70.A1 | MANUAL WARNING PUSHBUTTONS | n
MANUAL SWITCH FOR WARNING -BREAK A GLASS
Manual call points will be break glass and press button type suitable for surface mounting and approved to EN54-11 and EN54-17.
It shall be suitable for use in Hazardous Area Zones 0, 1 and 2 and zones 20, 21 and, 22. The call point shall include a test key feature for the rapid testing of the device without removing the glass. The call point shall also incorporate the following:
1. Alarm response indicator.
2. Facility for adding additional protective flap.
3. Wireless communication device to facilitate testing; enable readout of current status and wiring diagnostics.
4. Operating temperature: -35°C to + 70°C
5. An EMC Compatibility of at least 50V/m
6. Ingress protection of at least IP44 (IP64 with protection seal)
Manual directed pushbutton
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 5
| FIRST FLOOR LEVEL - FIRE DETECTION |  | 5
| SECOND FLOOR LEVEL - FIRE DETECTION |  | 7
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 4
| Total amount |  | 21
R10.A76.B1 | AIR SAMPLING SMOKE DETECTION SYSTEM | n
Air duct smoke detector shall be provided to protect air handling ducts ans shall have the following features:
1. Usable in air speeds from 1 to 20m/s
2. Ambient temperature operation range -20 to +50°C
3. Ingress protection to IP54
4. Capable of detecting in ducts between 100mm – 2.8m
Air sampling smoke detection system with 1(one) analogical detector
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 1
| FIRST FLOOR LEVEL - FIRE DETECTION |  | 9
| SECOND FLOOR LEVEL - FIRE DETECTION |  | 7
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 1
| Total amount |  | 18
R10.A76.B2 | AIR SAMPLING SMOKE DETECTION SYSTEM | n
Air duct smoke detector shall be provided to protect air handling ducts ans shall have the following features:
1. Usable in air speeds from 1 to 20m/s
2. Ambient temperature operation range -20 to +50°C
3. Ingress protection to IP54
4. Capable of detecting in ducts between 100mm – 2.8m
Air sampling smoke detection system with 2 (two) analogical detectors
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 1
| FIRST FLOOR LEVEL - FIRE DETECTION |  | 3
| SECOND FLOOR LEVEL - FIRE DETECTION |  | 1
| Total amount |  | 5
R10.A76.B3 | AIR SAMPLING SMOKE DETECTION SYSTEM | m
UNITÀ DI RIVELAZIONE FUMO A CAMPIONAMENTO D'ARIA
Smoke detecting unit able to perform, trough detecting aspirator, sampling of air taken from aposit tube situated in calibrated holes.
Electromeccanic caracteristics:
Functioning voltage: 20-30 V c.c.;
number of channels/detecting tubes, coincident with impact zone, indicated by codes R10.A76.B..;
Protection level: min. 44;
Protection from electromagnetic interferences in line with IEC 801-3 for values untill 50 V/m and from 1MHz to 1 GHz.
Construction caracteristics:
Unit containing smoke detector of standard conventional type or individual adressed analog or interactive;
connection to detecting line without using interface;
aspirant internal unit for realisation of indipendent depression of the ambiental air flow complete by monitorinh circuit for signalisation of failure related to malfanction end appropriate air aspiration function;
sampling tubes of lenght non superior to 100m for each taking channel apropriate for straight taking , on U or H (double U), composed by PVC tube standard complete with calibrated holes with appropriate adhesive tape;
holes perfomrmed on the basis of calculation which defines number, position and diemater in order to compensate losses on the route in order to obtain optimal air flow;
quantity of holes not over n.12 fori for each air taking tube;
equivalent surface controlled for each hole non superior to 30mq in case one detector for channel or 60 mq in case di n. 2 rdetectors;
connection possibility of at least n. 2 cascade units in one tube in order to relize signalization on more levels or to discriminate different laterals in configuration on U or H (doubble U);
local remote damage signalisation dispositive indicating minimal level of allowed air flow and eventual activation of at least one sampling hole;
sampling filters for dusty locations where required;
silencer for noise reduction;
air return dispositive.
Price must be diversificated for following typologies:
sampling unit;
tubes comprensive of fixing accessories;
realisation of calibrated holes on tubes including calculations and dimensioning.
PVC pipe
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 212
| FIRST FLOOR LEVEL - FIRE DETECTION |  | 970
| SECOND FLOOR LEVEL - FIRE DETECTION |  | 470
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 190
| Total amount |  | 1842
R10.A76.B4 | AIR SAMPLING SMOKE DETECTION SYSTEM | n
Aspirating smoke detection shall be addressable and integrated directly onto the detection loop. The detector shall have the following functions:
1. FDA241 type with an area of coverage up to 800 m2
2. 4 alarm state indicators
3. Smoke level bar-graph indicator
4. Airflow level bar-graph indicator
5. Fault indication
6. Purge indicator
7. Dust indicator
8. Info alarm Pre alarm and Fire 1 selectable between 0.03 & 2%/m
9. Fire 2 alarm selectable between 1.0 & 20%/m
10. 7 relay contacts for Info alarm, pre-alarm, Fire 1, Fire2, fault purge and dust
11. Integral short circuit isolation
Work for 12 balanced holes
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 1
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 1
| Total amount |  | 2
R10.A76.B5 | AIR SAMPLING SMOKE DETECTION SYSTEM | n
Aspirating smoke detection shall be addressable and integrated directly onto the detection loop. The detector shall have the following functions:
1. FDA241 type with an area of coverage up to 800 m2
2. 4 alarm state indicators
3. Smoke level bar-graph indicator
4. Airflow level bar-graph indicator
5. Fault indication
6. Purge indicator
7. Dust indicator
8. Info alarm Pre alarm and Fire 1 selectable between 0.03 & 2%/m
9. Fire 2 alarm selectable between 1.0 & 20%/m
10. 7 relay contacts for Info alarm, pre-alarm, Fire 1, Fire2, fault purge and dust
11. Integral short circuit isolation
Work for 24 balanced holes
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 1
| FIRST FLOOR LEVEL - FIRE DETECTION |  | 6
| SECOND FLOOR LEVEL - FIRE DETECTION |  | 3
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 1
| Total amount |  | 11
R10.A80.A2 | INPUT/OUTPUT MODULE FOR CONTROL AND RECEPTION | n
INTERFACE ANALOGICAL MODULE FOR DEVICE MANAGEMENT AND SIGNAL RECEPTION
Input / output modules shall comply with the requirements of and be approved to EN54-17.
Input / output modules should connect directly to the loop and not require further power supply connections.
Each input / output module shall take one address.
Input / output modules shall additionally include:
1. Inputs monitored for short & open circuit.
2. Inputs can be configured for normally open or normally closed operation.
3. Outputs to be rated at 250VAC 4A resistive & 30VDC 4A clean contacts.
4. Output to be selectable as continuous or as pulsed operation. Pulse duration to be selectable between 1 & 20 seconds.
5. Integral short circuit isolator.
6. LED indication of normal, fault, test, & activation conditions.
7. Module can be configured as fail safe.
8. Modules to be mounted in an IP66 housing with clear lid for device status indication.
9. Modules should additionally be suitable for DIN rail mounting.
10. Operating temperature: -25°C to +60°C
11. EMC compatibility: 50V/m
Analogical input module
| FIRST FLOOR LEVEL - FIRE DETECTION |  | 2
| SECOND FLOOR LEVEL - FIRE DETECTION |  | 25
| Total amount |  | 27
R10.A80.A4 | INPUT/OUTPUT MODULE FOR CONTROL AND RECEPTION | n
INTERFACE ANALOGICAL MODULE FOR DEVICE MANAGEMENT AND SIGNAL RECEPTION
Input / output modules shall comply with the requirements of and be approved to EN54-17.
Input / output modules should connect directly to the loop and not require further power supply connections.
Each input / output module shall take one address.
Input / output modules shall additionally include:
1. Inputs monitored for short & open circuit.
2. Inputs can be configured for normally open or normally closed operation.
3. Outputs to be rated at 250VAC 4A resistive & 30VDC 4A clean contacts.
4. Output to be selectable as continuous or as pulsed operation. Pulse duration to be selectable between 1 & 20 seconds.
5. Integral short circuit isolator.
6. LED indication of normal, fault, test, & activation conditions.
7. Module can be configured as fail safe.
8. Modules to be mounted in an IP66 housing with clear lid for device status indication.
9. Modules should additionally be suitable for DIN rail mounting.
10. Operating temperature: -25°C to +60°C
11. EMC compatibility: 50V/m
Analogical output module
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 6
| FIRST FLOOR LEVEL - FIRE DETECTION |  | 10
| SECOND FLOOR LEVEL - FIRE DETECTION |  | 29
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 2
| Total amount |  | 47
R100.A10.A11 | GENERIC DETECTOR POINT CONNECTION | n
PUNTO RIVELATORE EQUIVALENTE
The average price per position detector (detection apparatus excluded) consists of:
_ lines for power supply and signal beginning of the zone switchboard to the detector made ​​of loop cable for detection resistant to fire for 30 minutes, 2 x 18AWG (diameter 1 mm);
_ junction boxes and transmission boxes installed on the channels of riser and inside the premises;
_ installation pipes for cable boxes from the riser to the device detection.
The place where the pipes go through the installation pipes for cables and the location of the detector are indicated in the graphics tables.
Equivalent point detection is estimated by the body via calculating of all apparatus (detectors, sensors keys, horns, synoptic tables and tables for signaling. etc..) and the subsequent attribution of some average value for each of them, and therefore the price should be used to connect any component.
Analogical detector point connection with PVC rigid pipe and cables
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 9
| FIRST FLOOR LEVEL - FIRE DETECTION |  | 23
| SECOND FLOOR LEVEL - FIRE DETECTION |  | 57
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 5
| Total amount |  | 94
R100.A10.A2 | GENERIC DETECTOR POINT CONNECTION | n
PUNTO RIVELATORE EQUIVALENTE
The average price per position detector (detection apparatus excluded) consists of:
_ lines for power supply and signal beginning of the zone switchboard to the detector made ​​of loop cable for detection resistant to fire for 30 minutes, 2 x 18AWG (diameter 1 mm);
_ junction boxes and transmission boxes installed on the channels of riser and inside the premises;
_ installation pipes for cable boxes from the riser to the device detection.
The place where the pipes go through the installation pipes for cables and the location of the detector are indicated in the graphics tables.
Equivalent point detection is estimated by the body via calculating of all apparatus (detectors, sensors keys, horns, synoptic tables and tables for signaling. etc..) and the subsequent attribution of some average value for each of them, and therefore the price should be used to connect any component.
Analogical detector point connection with PVC flexible pipe and cables
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 19
| FIRST FLOOR LEVEL - FIRE DETECTION |  | 86
| SECOND FLOOR LEVEL - FIRE DETECTION |  | 45
| GROUND FLOOR LEVEL - FIRE DETECTION |  | 19
| Total amount |  | 169
TOTAL 13 - FIRE DETECTION DEVICE
14 - ANTI INTRUSION, CONTROLL ACCESS AND TVCC DEVICES
R20.A100.A1 | DOOR CONTROL MODULE | n
A Dual Reader Interface Module (DRIM) shall be available for each controlled door and provide the ability to connect up to two card readers or entry devices. This DRIM shall:
q Monitor the door position (door contact)
q Allow the connection of a Request-to-Exit (REX) switch for exit
q Control an electric door lock or strike
q Provide the facility for up to 3 auxiliary input devices to be connected
q Allow the connection of an alarm buzzer that can be triggered in the case of an alarm event, or more specifically locally trigger a buzzer for a door held event before this alarm is registered at the host.
All events that occur at the door must be reported from the DRIM to the ISC.
To allow for situations where an entry and exit reader may be required at the one door a DRIM will allow two readers to be connected. However, in circumstances where a door shall only require one reader the DRIM can be configured to operate in a two door mode, whereby a reader, door lock and door monitoring device can be connected for each door.
In addition, the DRIM shall also provide connection for single advanced reader that connects via an RS-485 or Wiegand / Clock/Data connections.
Finally, the DRIM shall also provide the ability to work offline in cases where communications with ISC has have been lost and still continue to accept a set of specified cards as being valid to the door(s) which it controls.
The device must contain all necessary power cables, Cat6 patch cable for connecting with vicinal cable systems, vertical cables, and all the necessary equipment for the professional completion of works.
Door control module
| GROUND FLOOR LEVEL - INTRUSION, ACCESS CONTROL AND CCTV |  | 3
| FIRST FLOOR LEVEL - INTRUSION, ACCESS CONTROL AND CCTV |  | 1
| SECOND FLOOR LEVEL - INTRUSION, ACCESS CONTROL AND CCTV |  | 1
| GROUND FLOOR LEVEL - INTRUSION, ACCESS CONTROL AND CCTV |  | 2
| Total amount |  | 7
R20.A102.A1 | PROXIMITY READER | n
TERMINAL OF PROXIMITY READER WITH A CARD
The terminal of proximity reader, which sends data to the peripheral unit, which controls the door to enable the operation of recognizing, authorization and executing commands of authorization.
 Transmission frequency 13.56 MHz
 The following card technologies are supported:
ISO14443-A:
 Mifare 1k and 4k (UID, S/B, MAD)
 Mifare UltraLight (UID, B)
 Mifare DesFire (UID)
 my-D proximity (UID, B) ISO14443-A+B
 my-C (UID) ISO15693:
 my-D vincinity (UID)
 I-Code SLI (UID)
 Tag-IT HFI (UID)
 LRI512 (UID)
 Configuration using configuration card or software tool
 Up to 7 cm read range, depending on mounting environment, card technology and card type
 DIP switch for functionality selection
 Flash memory for firmware updates
 Three-colour LED for status display and buzzer for audible signals
 Reader power from the power supply of the door controller
 "Touch and Go" operation
Proximity reader with code keypad
| GROUND FLOOR LEVEL - INTRUSION, ACCESS CONTROL AND CCTV |  | 3
| FIRST FLOOR LEVEL - INTRUSION, ACCESS CONTROL AND CCTV |  | 1
| SECOND FLOOR LEVEL - INTRUSION, ACCESS CONTROL AND CCTV |  | 1
| GROUND FLOOR LEVEL - INTRUSION, ACCESS CONTROL AND CCTV |  | 2
| Total amount |  | 7
R20.A20.A1 | PC SERVER FOR ACCESS CONTROL SYSTEM | n
PC SERVER IMPIANTO DI CONTROLLO ACCESSI
Access control system central unit, capable ti visualise data comming from periferic units and to implement the system trough programming and insertion of data, essentialty composed by:
n.1 PC with type Intel i5 processor with WINDOWS XP operating system or superior , as grafic interface , configuration and data implementation;
ram 4 GB, DDRIII;
HD 500 GB SATA, with function RAID 1 integrated;
CD/DVD reader;
video LCD TFT at least 22";
video card with resolution 1280x1024;
ergonomic operation keyboard;
mouse a n.2 butons with scroll;
laser color printer;
network card 10/100/1000 base T.
The Integrated Access Control System’s (ACS) primary function shall be to regulate access through specific doors, gates or barriers to secured areas of the facility. It shall also have the provision of capturing cardholder images and producing access cards used to provide this access.
The system shall use a single seamlessly integrated SQL database for both its access control and badging functionality. This integration shall be provided under one operating environment.
Access control system is fully integrable to Building Management System, communicationprotocol is realized without need for hardware gateways, additional licence is needed in order to enable communication.
The system shall provide a multi-tasking environment that allows the user to run several applications simultaneously. The ACS software shall run on a Windows Vista 32 bit operating system and be licensed by Microsoft under the Windows Vista Logo program. Such licensing shall ensure that the application was specifically designed for the Windows Vista platform and follow Microsoft’s development guidelines for this operating system. The ACS shall be able to run in conjunction with other Windows Vista applications such as MS Word and Excel while concurrently annunciating on-line access and security alarms and monitoring information.
The system shall operate on a Windows Vista multi-tasking, multi-threading 32-bit operating system. The System software shall be a true native 32-bit application built `from the ground up' for Windows XP. The System shall NOT be ported over from another operating system (i.e. UNIX, DOS, or OS/2) and shall not be a Win-16, UNIX, QNX or OS/2 program using a Windows NT Server. In addition, the system shall not be a UNIX or QNX Server using a Windows client.
All system application modules, features, and functions shall be generated from a single source code set. In addition, the source code must be designed using object-oriented software development techniques and compiled into native 32-bit applications. There shall not be separate source code bases for access control and ID badging. All system features and functionality listed in the proceeding pages shall ship with each system. Features and functionality available to the “Owner” shall be determined through licensing and shall be controlled by a software license key. The “Security Contractor” shall work with the Owner to develop and configure the system.
The Intelligent System Controllers (ISC's) shall comply with following standards • CE • C-Tick • UL
As a minimum the ACS shall provide the ability to connect up to 140 workstations to the server. Each workstation shall have the capability of displaying an easy to use MMI, from which all system operation, including programming, control and operation can be accomplished. The MMI shall employ a standard Windows look and feel and provide both an intuitive menu and button driven navigation system.
The MMI shall use allow for the customisation of an operator specific toolbar. This shall provide the ability to create a custom toolbar that only includes those buttons (links to parts of the ACS) that are most commonly used or required for the operation of the system.
In addition, the operator shall be able to display the look and feel of the toolbar buttons that allow them to perform tasks quickly and efficiently including the text size and placement and size and position of icons displayed.
In addition, the MMI shall also provide the ability for custom toolbar buttons to be programmed. This customisation will permit the selection of a personalized icon and the ability to include a command to be performed when the button is clicked by an operator.
The system shall request an operator’s user name and password before entry to the MMI is granted. The password must be fully encrypted on-screen to prevent it from being easily copied. The MMI will not be displayed until the identification of the operator has been verified and access to the ACS is granted. Authentication may be based on a pre-defined time schedule for certain groups of operators.
The system shall allow partitioning to be assigned on the basis of the following conditions (as a minimum):
• Cardholders
• System Functions (minimum of 60 feature levels)
• Holidays
• ISCs
• Field Devices
• Custom Pages
• Time Schedules
• Site Plans
• Reports
The system shall prevent the currently logged in operator from viewing the details, regarding any alarms triggered by a system component to which they have not been assigned privileges, including:
· Audit trail alarm entries
· Audit trail reports, which include alarm details
· Audible and visual alarm annunciation
The alarm information associated with any system component to which an operator has been assigned privileges will be displayed.
When assigning a function to an operator, the system shall allow the level of assignment to be specified. These levels include:
· Read only. This type of privilege level does not allow the operator to create or modify components in the specified area of the system. However, they are allowed to view those records.
· Modify. This type of privilege level does not allow the operator to create components in the specified area of the system. However, they are allowed to view and make modifications to existing records.
· Full. This type of privilege level allows the operator to create, modify and view components in the specified area of the system.
The system shall include a cardholder management component that is integrated with the access control system. The system must support at least 500,000 cards – all of which are downloaded and retained in the memory of each ISC. This cardholder management functionality must allow the enrolment of cardholders into the database, capturing of images and import/export of employee data. This functionality shall also allow a system operator to assign or modify the access rights of any cardholder.
Searching
The system shall allow the search of all programmed cardholders, based on the criteria supplied by an operator. Operators shall only be able to search and retrieve cardholder records to which they have assigned privileges.
The search criteria shall include any information that can be recorded against the cardholder and as a minimum include:
· Card number
· Name (first and / or last)
· Work Group
· Title
· Address
· Contact Numbers (phone, mobile, and pager)
· Payroll Number
· Vehicle Details (registration, colour, model)
· Custom Cardholder Data
Searching shall not only be limited to entire word matches. An operator may also search for cardholders by entering data that appears in the beginning of a word or string.
If more than one cardholder in the system meets the specified criteria, the operator shall be displayed a list of all matching records, from which they can select a particular record
The system shall be compatible with all major card and access entry technologies, including (but not limited to):
· Proximity cards and readers
· Biometric readers
· Bar code cards and readers
· Magstripe cards and readers
· Wiegand cards and readers
· Smart cards and readers
· iClass cards and readers (HADP range)
· Optical cards and readers
· Transmitter and infra-red cards and readers
· Keypads and PIN pads
| GROUND FLOOR LEVEL - INTRUSION, ACCESS CONTROL AND CCTV |  | 1
| Total amount |  | 1
R20.A201.A1 | WORK FOR ACTIVATION OF CONTROL ACCESS SYSTEM | globally
ATTIVAZIONE E COLLAUDO DELL'IMPIANTO CONTROLLO ACCESSI
Activation and testing of control access system by the manufacturer specialized technician.
Work for activation of control access system
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 1
| Total amount |  | 1
R20.A22.A1 | PROGRAMMER FOR KEY CARD CODES | n
STAMPANTE TESSERE DI PROSSIMITA'
Termografic printer (quoted separately) for badge programmation and personalisation of passes, in colllors and complete of support software
Programmer for key card codes
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 1
| Total amount |  | 1
R20.A80.A1 | DOOR LOCKING PUSHBUTTON | n
PUNTO COMANDO APRIPORTA
Command point made of:
_ part of the quota distribution and junction box installed along the riser;
_ conductor starting from the junction box installed along the riser and mounting box;
_ prefabricated boxes,built in or on the wall, depending on the types, which they possess, if required, connections for installation pipes for cables;
_ modular command fuses that have the following characteristics:
* Compliance with standards: CEI 23-9 and subsequent variations;
* voltage and nominal frequency: 250V c.a., 50Hz;
* nominal power : 10A for buttons and 16A for switches;
* test voltage: 2000V on 50Hz for 1 min.;
*switching power: 200 performed opening and closing to 1.25 In, 275V CA, cosfi'0, 3;
* testing functioning: 50000 maneuvers In, 250V CA, cosfi'0, 6;
* resistance of insulation: >15Mohm for 500V.
The price should include the internal wiring between fuses.
Door locking pushbutton
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 4
| FIRST FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 1
| SECOND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 1
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 2
| Total amount |  | 8
R40.A10.A1 | INTRUDER ALARM CONTROL UNIT | n
Central intrusion detection unit is fully integrable to Building Management System, communicationprotocol is realized without need for hardware gateways, no additional licence is required on panel side.
The Controller shall be capable of storing 10000 Intruder Events in its internal log, these events shall be accessible via the web server.
The controller shall support 64 calendars with a minimum of 3 different week types; each week type has 4 different on & off periods per day. The calendar can be used to enable/disable users, keypads, outputs, doors.
It shall be possible to create specific function with Cause & Effects programming via triggers and mapping gates. Status changes of areas, users, outputs, doors, etc. can be used as trigger. Several triggers can be combined in a mapping gate to be activated when all trigger conditions become true.
The system shall cope with daylight saving times automatically.
All system field expanders can be automatically addressed by the controller to prevent double addresses occurring on the system or manually set. The system software must detect double addresses if they occur.
It shall be possible to locally or remotely upgrade the firmware of controller and expanders.
The intruder inputs on the controller and any field expanders connected to the controller shall have the ability to analyse the input for gross attack and pulse count. The system shall also be able to vary the pulse count and gross attack settings on an input-by-input basis.
A wide variety of input types shall be available and for each input type a number of attributes should be configurable. Such as Chime, 24HR, Log, Inhibit, Normally open etc.
A general input type will be provided which can be used to monitor external equipment without intrusion functionality. This general type will support reporting and audible indications. It shall be possible to assign reporting codes to report specific events representing the equipment being monitored, water alarms, pressure alarms etc….
Alarm Relay Outputs shall be rated at 30V DC and 1A (resistive switching current), electronic outputs shall be rated at 12V DC and 400mA (resistive switching current)
The Controller and external Power Supplies shall be able to self-test the batteries to ensure that they are healthy on a regular basis.
Self-test for the detection of faults on the system shall occur when an Engineer exits from configuration mode.
The Controller shall support multiple languages a minimum of 4 different languages should be supported. When a language is selected, it shall change the language of all system keypads and all engineering and user menus on the system keypads and associated engineering tools (Web Servers etc.) to the language selected.
Engineering tools shall have the ability to read/configure the panel in one language whilst the panel and its system keypads are in a different language.
The controller shall support pluggable modules that allow additional communication paths in addition to the on-board IP facility if required. The system shall be configurable so that the most appropriate communication path can be determined as the primary communication path and then additional communication options used as secondary and tertiary paths.
Additional Pluggable PSTN modem(s) shall support V23/V90, Central station protocols (Contact ID, SIA, and Fast Format). PSTN modem must be capable of taking control of the PSTN line in an alarm situation and monitor the line for faults in Set / Unset operation. The modem shall support a minimum 56K speeds.
Additional pluggable GSM modem(s) shall support SMS for Event notification, SMS control and Central station protocols (Contact ID, SIA, Fast Format) and IP transmission over GPRS.
The controller should be able to send all alarms to the ARC/CMS via IP, PSTN or GSM modems. It must also be possible for the controller to send its alarms to multiple monitoring stations.
It must also be possible for the controller to send its alarms to multiple End users via SMS for Text notification.
The system will offer the ability to change event codes to individual receivers. The system will support the selection of events to be sent to individual receivers.
Controller
The Controller shall have a minimum of 8 on board wired Inputs and 6 fully programmable outputs. The system shall be expandable up to 512 wired inputs and 512 outputs by the use field expansion devices, Combination of wired / wireless inputs shall be possible.
The controller shall employ a high-speed expansion bus (BUS) that can be configured as in Loop and Spur topology. When the expansion bus is configured as a Loop topology a single or dual cable fault between the same two-expansion devices (short or open of data bus) shall allow all the system to remain fully operational with no loss of functionality (with cable faults reported). If additional cable faults were to occur then only the field expansion devices that do not have a connection to the controller shall be lost.
The controller shall provide an integrated Ethernet port to allow more than 10 parallel IP communications with connected applications such as Programming Software, Alarm Receiving Centres (CMS / ARC), Web Browsers, Danger Management Systems (DMS), 3rd party products, etc.
The controller shall provide an integrated Web server for system programming and operation. The Web server shall be accessible from any remote computer system running a web browser that can gain access to the panel through a LAN or WAN, serial, USB or modem. To allow access remotely, the communication shall be using a Secure Socket Layer (SLL), providing the user with the ability to login in using the same credentials (or separate web authentication credentials) and user rights for operation as if they were standing at the panel.
Hybrid systems
The System shall be expandable with several wireless access points to become a true hybrid alarm system. Therefore a combination of wired / wireless inputs (120 wireless inputs maximum) shall be possible. The wireless devices shall be addressed in the controller to allow multi-path reception from several wireless access points. The wireless access points shall use the European standard wireless frequency 868MHz, to providing greater security from interference and jamming.
Grading
The system grade required is determined by the risk analysis of the site to be protected and all the equipment must meet the minimum grade for that risk. If the risk is determined to be a Grade 2 system then all components of the system must be Grade 2 or above.
The enclosures of panel and external power supplies shall have sufficient space to house the standby battery with sufficient capacity to support the controller, plug in modules and the connected field devices (system keypads / field expanders etc.) for the required hold-up time as defined by the standard.
Programmable areas 60
Number of user codes 2500
Event memory 10'000 intrusion events, 10'000 access events
Max. number of hardwired zones 512
Max. number of wireless zones 120 (take away wired zones)
EOL resistor Dual 4k7 (default), other resistor combinations configurable
Number of on-board relays 1 strobe (30 VDC / 1 A resistive switching current)
Number of on-board open coll. 2 internal / external bell, 3 freely programmable (each max. 400 mA resistive switching current, supplied via auxiliary output)
Door Capacity Max. 64 entry doors Reader in only or 32 entry/exit doors or a combination of doors Reader in Reader in/out not exceeding 64 readers.
Time function 64 calendars (53 weeks, multiple on/off switching patterns for users, areas, inputs, outputs, keypads, doors)
Macro language Cause & Effect programming (1024 triggers / 512 mapping gates)
Number of field devices Max. 128 (32 keypads, 32 door-expanders, 64 input/output expanders)
Interfaces 2 X-BUS (2 spurs or 1 loop),
2 RS232 (for X-10 or external communication),
1 USB (PC connection),
1 SPC Fast Programmer,
1 Ethernet (RJ45)
Field bus X-BUS on RS-485 (307 kb/s) High Speed
Tamper contact Front spring tamper, 2 auxiliary tamper contact inputs
Output voltage 11-14 VDC in normal conditions (mains powered and fully charged battery)
Auxiliary power (nominal) Max. 1500 mA at 12 VDC (750 mA per output)
Operating temperature 0 ~ +40 °C
Standards / approval compliance EN50131-1, Grade 3, class II
SE: SFF1014, Larmklass 2
NL: REQ, Grade 3, class 2
HU: MABISZ
CZ: TESTALARM, TREZORTEST,NBU
INCERT
NF: a2p
BUS Configurations (Installation)
Loop Configuration
The Loop (or ring), cabling method offers the highest security by providing fault tolerant communications on the BUS. All system Keypads and field expanders are supervised and in case of a cable fault or break, the system continues to operate and all input circuits are monitored.
Spur Configuration
The spur (or chain or open loop) cabling method offers a high level of fault tolerance and may be more convenient on certain installations. The controller shall support two spurs. In the case of a cable fault or break, all Expanders and detectors up to the fault will continue to be supervised
Cables, distances and shielding
For normal installations a range of different common industry cables shall be able to be used (standard 4/6 core alarm cable (non shielded) / cat 5 / Belden etc.). Shielded cables should be used for sites with high electric field interference, e.g. Belden 9829, IYSTY 2 x 2 x 0.6 (min).
The system shall be able to support a minimum of 200m between each field expander irrespective of the cable type used. The system shall be able to extend this distance up to 400m between field expanders when Cat 5 / Belden 9829 / IYSTY 2 x 2 x 0.6 (min) cable is used in Loop and Spur cabling configuration.
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 1
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 1
| Total amount |  | 2
R40.A10.A7 | INTRUDER ALARM CONTROL UNIT | n
The Controller shall be capable of storing 10000 Intruder Events in its internal log, these events shall be accessible via the web server.
The controller shall support 64 calendars with a minimum of 3 different week types; each week type has 4 different on & off periods per day. The calendar can be used to enable/disable users, keypads, outputs, doors.
It shall be possible to create specific function with Cause & Effects programming via triggers and mapping gates. Status changes of areas, users, outputs, doors, etc. can be used as trigger. Several triggers can be combined in a mapping gate to be activated when all trigger conditions become true.
The system shall cope with daylight saving times automatically.
All system field expanders can be automatically addressed by the controller to prevent double addresses occurring on the system or manually set. The system software must detect double addresses if they occur.
It shall be possible to locally or remotely upgrade the firmware of controller and expanders.
The intruder inputs on the controller and any field expanders connected to the controller shall have the ability to analyse the input for gross attack and pulse count. The system shall also be able to vary the pulse count and gross attack settings on an input-by-input basis.
A wide variety of input types shall be available and for each input type a number of attributes should be configurable. Such as Chime, 24HR, Log, Inhibit, Normally open etc.
A general input type will be provided which can be used to monitor external equipment without intrusion functionality. This general type will support reporting and audible indications. It shall be possible to assign reporting codes to report specific events representing the equipment being monitored, water alarms, pressure alarms etc….
Alarm Relay Outputs shall be rated at 30V DC and 1A (resistive switching current), electronic outputs shall be rated at 12V DC and 400mA (resistive switching current)
The Controller and external Power Supplies shall be able to self-test the batteries to ensure that they are healthy on a regular basis.
Self-test for the detection of faults on the system shall occur when an Engineer exits from configuration mode.
The Controller shall support multiple languages a minimum of 4 different languages should be supported. When a language is selected, it shall change the language of all system keypads and all engineering and user menus on the system keypads and associated engineering tools (Web Servers etc.) to the language selected.
Engineering tools shall have the ability to read/configure the panel in one language whilst the panel and its system keypads are in a different language.
The controller shall support pluggable modules that allow additional communication paths in addition to the on-board IP facility if required. The system shall be configurable so that the most appropriate communication path can be determined as the primary communication path and then additional communication options used as secondary and tertiary paths.
Additional Pluggable PSTN modem(s) shall support V23/V90, Central station protocols (Contact ID, SIA, and Fast Format). PSTN modem must be capable of taking control of the PSTN line in an alarm situation and monitor the line for faults in Set / Unset operation. The modem shall support a minimum 56K speeds.
Additional pluggable GSM modem(s) shall support SMS for Event notification, SMS control and Central station protocols (Contact ID, SIA, Fast Format) and IP transmission over GPRS.
The controller should be able to send all alarms to the ARC/CMS via IP, PSTN or GSM modems. It must also be possible for the controller to send its alarms to multiple monitoring stations.
It must also be possible for the controller to send its alarms to multiple End users via SMS for Text notification.
The system will offer the ability to change event codes to individual receivers. The system will support the selection of events to be sent to individual receivers.
Controller
The Controller shall have a minimum of 8 on board wired Inputs and 6 fully programmable outputs. The system shall be expandable up to 512 wired inputs and 512 outputs by the use field expansion devices, Combination of wired / wireless inputs shall be possible.
The controller shall employ a high-speed expansion bus (BUS) that can be configured as in Loop and Spur topology. When the expansion bus is configured as a Loop topology a single or dual cable fault between the same two-expansion devices (short or open of data bus) shall allow all the system to remain fully operational with no loss of functionality (with cable faults reported). If additional cable faults were to occur then only the field expansion devices that do not have a connection to the controller shall be lost.
The controller shall provide an integrated Ethernet port to allow more than 10 parallel IP communications with connected applications such as Programming Software, Alarm Receiving Centres (CMS / ARC), Web Browsers, Danger Management Systems (DMS), 3rd party products, etc.
The controller shall provide an integrated Web server for system programming and operation. The Web server shall be accessible from any remote computer system running a web browser that can gain access to the panel through a LAN or WAN, serial, USB or modem. To allow access remotely, the communication shall be using a Secure Socket Layer (SLL), providing the user with the ability to login in using the same credentials (or separate web authentication credentials) and user rights for operation as if they were standing at the panel.
Hybrid systems
The System shall be expandable with several wireless access points to become a true hybrid alarm system. Therefore a combination of wired / wireless inputs (120 wireless inputs maximum) shall be possible. The wireless devices shall be addressed in the controller to allow multi-path reception from several wireless access points. The wireless access points shall use the European standard wireless frequency 868MHz, to providing greater security from interference and jamming.
Grading
The system grade required is determined by the risk analysis of the site to be protected and all the equipment must meet the minimum grade for that risk. If the risk is determined to be a Grade 2 system then all components of the system must be Grade 2 or above.
The enclosures of panel and external power supplies shall have sufficient space to house the standby battery with sufficient capacity to support the controller, plug in modules and the connected field devices (system keypads / field expanders etc.) for the required hold-up time as defined by the standard.
Programmable areas 60
Number of user codes 2500
Event memory 10'000 intrusion events, 10'000 access events
Max. number of hardwired zones 512
Max. number of wireless zones 120 (take away wired zones)
EOL resistor Dual 4k7 (default), other resistor combinations configurable
Number of on-board relays 1 strobe (30 VDC / 1 A resistive switching current)
Number of on-board open coll. 2 internal / external bell, 3 freely programmable (each max. 400 mA resistive switching current, supplied via auxiliary output)
Door Capacity Max. 64 entry doors Reader in only or 32 entry/exit doors or a combination of doors Reader in Reader in/out not exceeding 64 readers.
Time function 64 calendars (53 weeks, multiple on/off switching patterns for users, areas, inputs, outputs, keypads, doors)
Macro language Cause & Effect programming (1024 triggers / 512 mapping gates)
Number of field devices Max. 128 (32 keypads, 32 door-expanders, 64 input/output expanders)
Interfaces 2 X-BUS (2 spurs or 1 loop),
2 RS232 (for X-10 or external communication),
1 USB (PC connection),
1 SPC Fast Programmer,
1 Ethernet (RJ45)
Field bus X-BUS on RS-485 (307 kb/s) High Speed
Tamper contact Front spring tamper, 2 auxiliary tamper contact inputs
Output voltage 11-14 VDC in normal conditions (mains powered and fully charged battery)
Auxiliary power (nominal) Max. 1500 mA at 12 VDC (750 mA per output)
Operating temperature 0 ~ +40 °C
Standards / approval compliance EN50131-1, Grade 3, class II
SE: SFF1014, Larmklass 2
NL: REQ, Grade 3, class 2
HU: MABISZ
CZ: TESTALARM, TREZORTEST,NBU
INCERT
NF: a2p
BUS Configurations (Installation)
Loop Configuration
The Loop (or ring), cabling method offers the highest security by providing fault tolerant communications on the BUS. All system Keypads and field expanders are supervised and in case of a cable fault or break, the system continues to operate and all input circuits are monitored.
Spur Configuration
The spur (or chain or open loop) cabling method offers a high level of fault tolerance and may be more convenient on certain installations. The controller shall support two spurs. In the case of a cable fault or break, all Expanders and detectors up to the fault will continue to be supervised
Cables, distances and shielding
For normal installations a range of different common industry cables shall be able to be used (standard 4/6 core alarm cable (non shielded) / cat 5 / Belden etc.). Shielded cables should be used for sites with high electric field interference, e.g. Belden 9829, IYSTY 2 x 2 x 0.6 (min).
The system shall be able to support a minimum of 200m between each field expander irrespective of the cable type used. The system shall be able to extend this distance up to 400m between field expanders when Cat 5 / Belden 9829 / IYSTY 2 x 2 x 0.6 (min) cable is used in Loop and Spur cabling configuration.
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 1
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 1
| Total amount |  | 2
R40.A201.A1 | WORK FOR ACTIVATION OF INTRUDER ALARM SYSTEM | globally
ATTIVAZIONE E COLLAUDO DELL'IMPIANTO ANTINTRUSIONE
Activation and testing of intruder allarm system by the manufacturer specialized technician.
Work for activation of intruder alarm system (ministry building)
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 1
| Total amount |  | 1
R40.A201.A10 | WORK FOR ACTIVATION OF INTRUDER ALARM SYSTEM | globally
ATTIVAZIONE E COLLAUDO DELL'IMPIANTO ANTINTRUSIONE
Activation and testing of intruder allarm system by the manufacturer specialized technician.
Work for activation of intruder alarm system (university building)
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 1
| Total amount |  | 1
R40.A31.A1 | PASSIVE INFRARED DETECTOR | n
PASSIVE INFRARED DETECTOR
Supply voltage (12 V nom.)
– Max. ripple (0 … 100 Hz)
– Voltage monitoring
8.0 … 16.0 VDC
2.0 VPP
Alarm at < 5.5 … 7.5 V
Current consumption (at 8 …16 VDC)
– Quiescent / when alarm occurs (with LED)
2.8 mA / <10 mA
Alarm output, semiconductor relay 30 VDC / 100 mA / Ri <45 Ohm
Alarm holding time 2 … 3 s
Walktest indicator LED
Tamper contact 30 VDC / 100 mA
Control inputs LOW ≤1.5 V / HIGH ≥3.5 V
Walking speeds
– Wide angle / Curtain
0.1 … 4.0 m/s / 0.1 … 4.0 m/s
Ambient conditions
Operation temperature -20 … +55 °C
Storage temperature -20 … +60 °C
Humidity (EN60721) <95 % r.h., non condensing
EMI rejection up to 1 GHz / up to 2 GHz >30 V/m / >10 V/m
Housing protection EN60529, EN50102 IP41
Approvals VdS class B, wide angle: G 103506,
curtain: G 103507
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 11
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 8
| Total amount |  | 19
R40.A41.A1 | MAGNET CONTACT FOR DOOR CONTROL | n
CONTATTO MAGNETICO PER CONTROLLO PORTE AD INCASSO
Approval: IMQ I Level
Electromechanical characteristics:
_ operating distance: min. 20 mm.
_ dimensions min: 34x diameter 20 mm.
Structural characteristics:
_ "cigarette" body made ​​of brass, for flush mounting on a metal door, including armored, equipped with mounts;"cigaret" tijelo od mesinga, za uzidno postavljanje na metalnim vratima, uključujući i blindirana, opremljeno i odbojnikom;
_ connection via 4 wires (n.1 pair for sensor and n.1 pair forsabotage).
Magnet contact for door control
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 18
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 9
| Total amount |  | 27
R40.A52.A1 | OPTICAL ACOUSTIC WARNING INTRUDER ALARM PANEL | n
PANNELLO OTTICO ACUSTICO DI ALLARME
In line with: EN 54-3.
Electromeccanical caracteristics:
Functioning voltage: 20-30 V c.c.;
Protection level: min. IP30 for inside IP65 for external isolation.
Construction caracteristics:
chase in termoplastic autoestingueting material;
optical and acustic signalisation both settable (impulsive or fixed);
acustic signalisation: min. 90db;
function signal led;
autosupply battery 24V.
Acoustic warning intruder alarm panel with self powering kit, indoor installation
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 1
| Total amount |  | 1
R40.A52.A2 | OPTICAL ACOUSTIC WARNING INTRUDER ALARM PANEL | n
PANNELLO OTTICO ACUSTICO DI ALLARME
In line with: EN 54-3.
Electromeccanical caracteristics:
Functioning voltage: 20-30 V c.c.;
Protection level: min. IP30 for inside IP65 for external isolation.
Construction caracteristics:
chase in termoplastic autoestingueting material;
optical and acustic signalisation both settable (impulsive or fixed);
acustic signalisation: min. 90db;
function signal led;
autosupply battery 24V.
Acoustic warning intruder alarm panel with self powering kit, outdoor installation
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 1
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 1
| Total amount |  | 2
R40.A80.A1 | ADDRESSING ELEMENTS DEVICE | n
The I/O Expander shall enable 8 additional Alarm Inputs and 2 relay outputs (30V / 1A) to be added onto the BUS. The input types and the outputs shall be fully programmable. The PCB shall have an on-board buzzer, status LED; tamper switch and thermal fuse to protect auxiliary devices. Power to the I/O Expander shall be provided via the BUS cable from the controller or by locally based intelligent power supply units. The PCB shall be housed in a robust plastic enclosure.
The Alarm Inputs shall be capable of supporting a range of EOL resistor values to be able to take into account 3rd party legacy systems.
The Expanders may also be installed in the controller enclosure. This enclosure shall accommodate the standby battery, controller and I/O Expander(s).
Number of on-board zones 8
EOL resistor Dual 4k7 (default), other resistor combinations configurable
Number of on-board relays 2 (single-pole changeover, 30 VDC / max. 1 A resistive switching current)
Field bus X-BUS on RS-485 (307 kb/s)
Tamper contact Front spring tamper
Operating voltage 9.5 ~ 14 VDC
Operating temperature -10 ~ +50 °C
Standards / approval EN50131-1, Grade 3, class II
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 10
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 5
| Total amount |  | 15
R50.A117.A1 | CCTV CLIENT | n
PC UTENTE IMPIANTO TVCC
PC clientshould visualise live straming video from at least 16 cameras contemporary and site geografic on two different monitors.
Tecnichal caracteristics:
metal colored chase type Tower;
suppy 230V c.a. Of at least 400W;
mother card;
n.1 processor Intel i5;
hard disk of at least 7200 rpm for the total of at least 500 Gbyte;
memory RAM at least 4 Gbyte ECC DDRIII;
network card Gigabit Ethernet 10/100/1000 BaseT;
video card with n.2 exits DVI;
interior DVD reader;
internal DVD recorder with software;
multimedial keyboard and mouse cordless;
interior audio card retail or similar;
operative system Microsoft XP professional, or similar;
n.2 monitor LCD TFT 19";
suite software coordinate with video digital recorder for:
* integrated control of both digital videorecorders;
* grafic map control with camera position indication;
* motion detection allarm;
* virtual matrix;
* multiplexer virtual;
* rotation and control of dome cameras with virtual joystick or PC connected joystick;
* simultaneous access to recorded immagines in real time.
all installed components should not have hardware and software conflict.
supply should include accessories and acbbling and programming required for professional functioning.
PC client for CCTV system
| GROUND FLOOR LEVEL -CCTV SYSTEM |  | 1
| Total amount |  | 1
R50.A16.A1 | IP FIXED CAMERA MINIDOME PoE | n
TELECAMERA IP MINIDOME FISSA A COLORI
Fixed telecamera minidome for installation on the ceiling or on the wall, following characteristics:
case suitable for installation, with maximum cross-section ring 140 mm and height 128 mm;
power supply PoE according to standard IEEE 802.3 af;
communication with LAN Ethernet network, compatible to central video recording system as well as to central management station (BMS - Desigo CC)
with changing focus 3 - 9 mm;
sensor CMOS with progressive scanning.
Multiple stream which can be indvidually configured H.264 i Motion JPEG;
maximum resolution of at least SXGA 1,3MPixel, speed 12 fps. Possibility of sending at least two streaming videos, one for monitoring, and other for recording.
possibility of picture rotation;
resolution control of the picture: color, brightness, contrast, white level, etc.
motion detection function and anti-tamper alarm;
perfect integration with switchboard TVCC.
Camera must be equipped and installed with:
patch cord on the side of the camera and on the side of rack;
programming;
softwer licence.
IP fixed camera minidome PoE for indoor/outdoor installation
| GROUND FLOOR LEVEL -CCTV SYSTEM |  | 1
| GROUND FLOOR LEVEL -CCTV SYSTEM |  | 2
| Total amount |  | 3
R50.A17.A1 | IP DOME PTZ CAMERA | n
TELECAMERA IP DOME A COLORI BRANDEGGIABILE
camera IP Dome with following caracteristics:
metal custody (alluminium) class IP66, transparent dome in acril, sun protection;
supply 24 V c.a.;
communication with LAN Ethernet network, compatible to central video recording system as well as to central management station (BMS - Desigo CC)
ethernet network port RJ45;
sensor: CCD Progressive Scan of 1/4" risolution D1;
objective: f=3.4 - 122.4 mm, F1.4, automatic zoom, automatic function day/night shot;
minimal lighting: Color: 0,7 lux, B/N: 0,03 lux;
PTZ: pan speed max. 400 °/s ,
video compression: H.264; MPEG-4; Motion JPEG;
risolution: D1, VGA, QVGA a 25 fps;
Immagine settings: manual closing time, compression, color, lighting, sharpness, calibration of white, esposition control, esposition area, retrolighting illumination, week light precise setting, rotation, text and picture ovepositioning, privacy mask, immagine freez in PTZ;
perfect integration with TVCC central.
Cmera should be complete of:
supporters;
accessories;
patch cord.
electrical supply point;
software license for integration with control and supervision systems.
Cabbling and energy supply are included in the price.
IP dome PTZ camera, 35x, D/N
| GROUND FLOOR LEVEL -CCTV SYSTEM |  | 1
| Total amount |  | 1
R50.A30.A1 | DIGITAL VIDEO SERVER | n
SERVER DI VIDEOREGISTRAZIONE IMPIANTO TVCC
Supply, instalation and programmation of videorecorder server in real time for videosurveilance devices having following caracteristics:
metal chases complete by accessories fo instalation in cabinet rack 19";
supplier ridondato Hot Swap, 230V c.a. for at least 600W;
cache L2, 2 Mbyte;
processor: CPU tipo Intel Xeon 4C, 2.40GHz, 12M Cache, 5.86GT/s, 80W TDP,
Turbo, HT, DDR3-1066MHz;
ram: 4 GByte DDRIII with free slots for expansion of at least 12GByte;
hard disk hot swap: n.5 x 500 Gbyte in configuration RAID5;
n.2 network cards with port Gigabit Ethernet, 64bit, 1000baseT;
interface: serial RS232, VGA, USB, keyboard, mouse;
grafic with n.8MByte SDRAM;
master DVD internal;
reader DVD;
monitor LCD TFT 15" for instalation in 19";
keyboard with mouse instalable in cassette in rack 19";
coordinated operative system coordinato with videosurveilance software.
Server should be supplied and installed with electrical and signal cabbling in rack 19".
It should be configurated for functioning inside of the videosurveilance system as by professional standards.
Digital video server for rack installation (without CCTV software)
| GROUND FLOOR LEVEL -CCTV SYSTEM |  | 1
| Total amount |  | 1
R50.A45.A1 | VIDEOSURVEILLANCE SOFTWARE | n
SOFTWARE DI VIDEOSORVEGLIANZA
software controlling videosurveilance system installed in PC having following caracteristics:
compatible to BMS (SCADA). BMS consists also the same CCTV module as it is used for video management
Full protocol communication and interoperabiity is to be done
simultaneous access to all digital video recorders and all encoders connected in LAN Ethernet;
video virtuale matrix;
grafic map with camera apposit indication con;
video indipendent windows for visualisation of live or in playback of different cameras;
immagine recording adaptation to available width;
video reserch function trough data mask via date, hour, camera etc.;
picture printing and processsed picture printing function;
picture and video clip export appropriate for police use ;
motion detection controll function;
videorecorder visualisation and cobtrol with remote location via Web page;
control function via pocket PC
picture control in full duplex with posssibilty for visualisation of "live" and contemporary archive pictures review (simultaneus streaming function);
visualisation of at least 16 pictures live and/or simultaneous maps on 25 Fps;
visualisation in cycle (single or multi picture) and time setting possibility;
just recordered picture live review with conteporary screen visualisation of the same sequence;
visualisation and controll of video sequnze (group of cameras) during live visualisation;
PTZ control with mouse and external keyboard a, with drag-and-drop commands and possibility of setting preset and patterns of telecamere dome;
external butonsfor the periferic dome units control;
direct internal menu entrance from the single dome without use of other applications;
zoom digitale function, contemporary with visualisation and other functions;
real-time events and allarms history viewi;
dayly and weekly programmer for each single camera;
play back of video recorded sequences trough hour and date;
video sequenze research trough events, allarms, bookmarks, motion;
video sequenze research trough activation of motion detector in specific area (after event choice);
play back on analog monitor;
play back speed setting and in continous mode;
creating of HTML interactive map for all locations.
Price is inclusive of:
use licences;
instalation and programming;
realisation of grafic and visualisation elements.
Videosurveillance software with license for all CCTV system devices
| GROUND FLOOR LEVEL -CCTV SYSTEM |  | 1
| Total amount |  | 1
R60.A70.A1 | KEYBOARD FOR DISCONNECTION INTRUDER ALARM | n
ELECTRONIC KEY - KEYBOARD
The system Keypad(s) shall be remote from the controller and the system shall be capable of allowing up to 32 Keypads on each controller. The Keypad shall be configurable per User & per Area/Multiple Areas, allowing each User to see only the menu options or events that apply to that User/Area.
A range of systems keypads shall be available with options for optional display and control features.
The standard keypad range shall support the following features;
LCD display with 2 x lines of 16 characters to show all alert and warning messages with alphanumeric Keys to allow for both text and numeric data entry.
Soft function keys that can change function depending upon the menu selected.
The user shall be able to (Depending on user rights) System Set – Unset, Part A/B Set –Unset, Area Set –Unset.
The illumination shall be programmable to allow one of three states (Always on, always off or by Key press).
When multiple Keypads are used, the option to be able to silence the on board buzzer for quiet environments shall be capable of being deployed.
Integral EM proximity reader for keypad logon resp. setting / unsetting (PACE)
Local Wireless Access Point to support local wireless devices.
The enhanced keypad range shall have the following features;
Graphical LCD display with 128 x 64 dots providing space for alert and warning messages with alphanumeric Keys to allow for both text and numeric data entry.
Soft function keys (minimum of four) that can change function depending upon the mode of the system.
The user shall be able to (Depending on user rights) System Set – Unset, Part A/B Set –Unset, Area Set –Unset.
The illumination shall be programmable to allow one of three states (Always on, always off or by Keypress).
When multiple Keypads are used, the option to be able to silence the on board buzzer for quiet environments shall be capable of being deployed.
Integral EM proximity reader for keypad logon resp. setting / unsetting
Integral speaker to provide voice annunciation
Capable of displaying the installers logo
Capable of showing the status of four Areas / Partitions at any one time.
Support for locally attached key-switch and indication modules
The status of each Keypad on the system shall be viewable and this shall include;
Tamper status
Firmware Version
Input Voltage
Address ID
Capability to disable keypads based on various conditions
LCD-display 2 x 16 characters
Special keys 2 soft keys, 1 multi-dimensional navigation key
LED indicators 3 status LEDs
Card reader Integrated (125kHz, EM 4102)
Field bus X-BUS on RS-485 (307 kb/s)
Tamper contact Front / back spring tamper
Operating voltage 9.5 ~ 14 VDC
Operating temperature 5 ~ +40 °C
Standards / approval compliance EN50131-1, Grade 3, class II, SE: SFF1014, Larmklass 2, HU: MABISZ, CZ: TESTALARM, TREZORTEST,NBU
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 1
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 2
| Total amount |  | 3
S60.A40.A1 | VIDEO ENTRY PHONE SYSTEM | n
IMPIANTO VIDEOCITOFONICO
Electrical digital video-entry porter wizh two wires able to perform call from inside locations (entrance building doors) with camera, trough selection of apposit inside button.
Compliance with standards: CEI 12-13(88), 14-6(90)and subsequent variations; HD 195 S4.
The system will be composed of the following devices:
ELECTRONIC GROUP FOR POWER SUPPLY
_ nominal voltage and frequency: 230V c.a. +/-10%, 50Hz;
_ secondary outputs: 22V AC / 0,9 a continuous power supply of light on the panel with switches and resistance to overheating; 22V c.a. / 0,5 intermittent performance for power supply for sound,calls, the brightness of the recording place, the camera; monitor; 22V c.a./3A impulses for electric locks; 25V c.c. / 0.8 A intermittent performance for the interior premises,derivatives, etc..;
_ transformer power: 60VA;
_ group for decoding digitized calls for enabling dialed numbers;
_Structural characteristics :
*body of thermoplastic material of a modular structure suitable for installation on DIN or OMEGA guide inside the box frame or local plan (calculated separately) or on a wall
* round protective cover of input terminals;
*Self-protection inputs and outputs through a fuse;
*transformer core is made of small sheet metals with low loss;
EXTERNAL DIGITAL VIDEO-INTERCOM SPACE
External space with modular elements (tile with indicated names, audio tile, tile with table with switches, tile for recording, boxes, frames, module carrier construction, etc.) suitable for creating various configurations, consisting of:
_ tiles of anodized aluminum in color selected by the company, or of light alloys obtained by casting under press, thickness min. 15mm, which are subjected to anti corrosion treatment, with a small glass which contains the name of the polycarbonate, notched burglar bolts with the head of a flat plate, anti-vandal version;
_bricked in case made of thermoplastic material;
_ voice group:
* power supply: at least 6V c.c. +/-5%;
* level of noise in the background: < 30mV;
* body of thermoplastic material placed in the outer panel with switches;
* amplified microphone and speaker, with separate tone control in communications inward and outward;
_ recording group:
* camera made in technology CCD 1 / 4" color;
* power supply: 16-20V c.c.;
* working apsorpcija: 400mA , 70mA on stand by;
* video exit: bight moduled;
* starting time: < 6 sec.;
* screw for mechanical control of focus;
* screw for turning off the mechanical element in the event of failure;
* installation (in the version included in an external site) vertical installation; (in separate version) on the wall or on the ceiling, with adjustable cramps and power supply point; where required, thermostat waterproof housing, with protection from penetration of rain;
INNER SPACE
* power supply 18-23 V c.c.;
* screen: LCD 3,5";
* activation time: < 6 sec.;
* range of video signals at the entrance: 0,5-1,5 V pp;
* vertical frequency: 50Hz synchronized with the network;
* activation time: at least 60 sec.;
* white body of thermoplastic material;
* microphone with spiral cable;
* unit for confidential conversations;
*ability of differential calls from the floor or from the outside;
* keys for the command of opening the door, turn on lights on the stairs, turn on the monitor from the inside, calling the switchboard (if required);
* differential regulation of the brightness and contrast;
* additional equipment for installation;
* appropriate measures in order to implement a simplified installation of the cable system;
* installation on the table or on the wall;
DERIVATOR OF VIDEO SIGNALS
Derivator of video signal, voice and data with low attenuation coefficient,for two-wire devices to separate the video signals, taken from a column of supporter, towards inside spaces.
ELECTRICAL LOCK
_ power supply: 12V c.a.
Power supply box video entry phone system
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 1
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 1
| Total amount |  | 2
S60.A40.A2 | VIDEO ENTRY PHONE SYSTEM | n
IMPIANTO VIDEOCITOFONICO
Electrical digital video-entry porter wizh two wires able to perform call from inside locations (entrance building doors) with camera, trough selection of apposit inside button.
Compliance with standards: CEI 12-13(88), 14-6(90)and subsequent variations; HD 195 S4.
The system will be composed of the following devices:
ELECTRONIC GROUP FOR POWER SUPPLY
_ nominal voltage and frequency: 230V c.a. +/-10%, 50Hz;
_ secondary outputs: 22V AC / 0,9 a continuous power supply of light on the panel with switches and resistance to overheating; 22V c.a. / 0,5 intermittent performance for power supply for sound,calls, the brightness of the recording place, the camera; monitor; 22V c.a./3A impulses for electric locks; 25V c.c. / 0.8 A intermittent performance for the interior premises,derivatives, etc..;
_ transformer power: 60VA;
_ group for decoding digitized calls for enabling dialed numbers;
_Structural characteristics :
*body of thermoplastic material of a modular structure suitable for installation on DIN or OMEGA guide inside the box frame or local plan (calculated separately) or on a wall
* round protective cover of input terminals;
*Self-protection inputs and outputs through a fuse;
*transformer core is made of small sheet metals with low loss;
EXTERNAL DIGITAL VIDEO-INTERCOM SPACE
External space with modular elements (tile with indicated names, audio tile, tile with table with switches, tile for recording, boxes, frames, module carrier construction, etc.) suitable for creating various configurations, consisting of:
_ tiles of anodized aluminum in color selected by the company, or of light alloys obtained by casting under press, thickness min. 15mm, which are subjected to anti corrosion treatment, with a small glass which contains the name of the polycarbonate, notched burglar bolts with the head of a flat plate, anti-vandal version;
_bricked in case made of thermoplastic material;
_ voice group:
* power supply: at least 6V c.c. +/-5%;
* level of noise in the background: < 30mV;
* body of thermoplastic material placed in the outer panel with switches;
* amplified microphone and speaker, with separate tone control in communications inward and outward;
_ recording group:
* camera made in technology CCD 1 / 4" color;
* power supply: 16-20V c.c.;
* working apsorpcija: 400mA , 70mA on stand by;
* video exit: bight moduled;
* starting time: < 6 sec.;
* screw for mechanical control of focus;
* screw for turning off the mechanical element in the event of failure;
* installation (in the version included in an external site) vertical installation; (in separate version) on the wall or on the ceiling, with adjustable cramps and power supply point; where required, thermostat waterproof housing, with protection from penetration of rain;
INNER SPACE
* power supply 18-23 V c.c.;
* screen: LCD 3,5";
* activation time: < 6 sec.;
* range of video signals at the entrance: 0,5-1,5 V pp;
* vertical frequency: 50Hz synchronized with the network;
* activation time: at least 60 sec.;
* white body of thermoplastic material;
* microphone with spiral cable;
* unit for confidential conversations;
*ability of differential calls from the floor or from the outside;
* keys for the command of opening the door, turn on lights on the stairs, turn on the monitor from the inside, calling the switchboard (if required);
* differential regulation of the brightness and contrast;
* additional equipment for installation;
* appropriate measures in order to implement a simplified installation of the cable system;
* installation on the table or on the wall;
DERIVATOR OF VIDEO SIGNALS
Derivator of video signal, voice and data with low attenuation coefficient,for two-wire devices to separate the video signals, taken from a column of supporter, towards inside spaces.
ELECTRICAL LOCK
_ power supply: 12V c.a.
Indoor video entry phone
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 2
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 1
| Total amount |  | 3
S60.A40.A3 | VIDEO ENTRY PHONE SYSTEM | n
IMPIANTO VIDEOCITOFONICO
Electrical digital video-entry porter wizh two wires able to perform call from inside locations (entrance building doors) with camera, trough selection of apposit inside button.
Compliance with standards: CEI 12-13(88), 14-6(90)and subsequent variations; HD 195 S4.
The system will be composed of the following devices:
ELECTRONIC GROUP FOR POWER SUPPLY
_ nominal voltage and frequency: 230V c.a. +/-10%, 50Hz;
_ secondary outputs: 22V AC / 0,9 a continuous power supply of light on the panel with switches and resistance to overheating; 22V c.a. / 0,5 intermittent performance for power supply for sound,calls, the brightness of the recording place, the camera; monitor; 22V c.a./3A impulses for electric locks; 25V c.c. / 0.8 A intermittent performance for the interior premises,derivatives, etc..;
_ transformer power: 60VA;
_ group for decoding digitized calls for enabling dialed numbers;
_Structural characteristics :
*body of thermoplastic material of a modular structure suitable for installation on DIN or OMEGA guide inside the box frame or local plan (calculated separately) or on a wall
* round protective cover of input terminals;
*Self-protection inputs and outputs through a fuse;
*transformer core is made of small sheet metals with low loss;
EXTERNAL DIGITAL VIDEO-INTERCOM SPACE
External space with modular elements (tile with indicated names, audio tile, tile with table with switches, tile for recording, boxes, frames, module carrier construction, etc.) suitable for creating various configurations, consisting of:
_ tiles of anodized aluminum in color selected by the company, or of light alloys obtained by casting under press, thickness min. 15mm, which are subjected to anti corrosion treatment, with a small glass which contains the name of the polycarbonate, notched burglar bolts with the head of a flat plate, anti-vandal version;
_bricked in case made of thermoplastic material;
_ voice group:
* power supply: at least 6V c.c. +/-5%;
* level of noise in the background: < 30mV;
* body of thermoplastic material placed in the outer panel with switches;
* amplified microphone and speaker, with separate tone control in communications inward and outward;
_ recording group:
* camera made in technology CCD 1 / 4" color;
* power supply: 16-20V c.c.;
* working apsorpcija: 400mA , 70mA on stand by;
* video exit: bight moduled;
* starting time: < 6 sec.;
* screw for mechanical control of focus;
* screw for turning off the mechanical element in the event of failure;
* installation (in the version included in an external site) vertical installation; (in separate version) on the wall or on the ceiling, with adjustable cramps and power supply point; where required, thermostat waterproof housing, with protection from penetration of rain;
INNER SPACE
* power supply 18-23 V c.c.;
* screen: LCD 3,5";
* activation time: < 6 sec.;
* range of video signals at the entrance: 0,5-1,5 V pp;
* vertical frequency: 50Hz synchronized with the network;
* activation time: at least 60 sec.;
* white body of thermoplastic material;
* microphone with spiral cable;
* unit for confidential conversations;
*ability of differential calls from the floor or from the outside;
* keys for the command of opening the door, turn on lights on the stairs, turn on the monitor from the inside, calling the switchboard (if required);
* differential regulation of the brightness and contrast;
* additional equipment for installation;
* appropriate measures in order to implement a simplified installation of the cable system;
* installation on the table or on the wall;
DERIVATOR OF VIDEO SIGNALS
Derivator of video signal, voice and data with low attenuation coefficient,for two-wire devices to separate the video signals, taken from a column of supporter, towards inside spaces.
ELECTRICAL LOCK
_ power supply: 12V c.a.
Outdoor video entry phone
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 3
| GROUND FLOOR LEVEL - INTRUDER ALARM SYSTEM |  | 1
| Total amount |  | 4
TOTAL 14 - ANTI INTRUSION, CONTROLL ACCESS AND TVCC DEVICES
15 - CALL SYSTEM
S10.A10.A12 | CALL SYSTEM FOR DISABLED TOILETS | n
SISTEMA DI SEGNALAZIONE CHIAMATA
Call system for at least n.60 calls, extendible to n.240 chiamanti,able to perform following functions:
alfanumeric personalizable identification of at least n. 18 characters from the call point;
semplified cabbling non over n.5 conductors in maximal expansion;
call signal with visible message permanent and with sound notice contemporary;
continious monitoring fof the correct functioning of the device with coded signalisation of failures on diplay ;
memorisation of contemporary calls and cyclic visualisation of calls on display ;
signalisation permanent memory even in case of lack of supply .
cancelation of single calls from the central position or via butons in proximity of the call buton;
call repetition on other display boards;
visualisation of actual hour in absence of active calls;
priority calls programmable control;
guided informations for programming and personalisation trough remote controller.
CALL POINTS, CANCELATION AND SIGNALISATION
Call points, cancellation and signalisation are composed by:
quote of supply and signalisation composed of in wall or on wall conductor ;
quota parte delle cassette di transito e di derivazione installate lungo la dorsale;
conduits from derivation cassette installed on voltage line to socket;
cables type FM9 of section non under 1,5 mmq;
in wall socket;
appropriate identification elements/call point code;
frutti di comando e di segnalazione modulari aventi le seguenti caratteristiche:
BUTONS:
* in line with: CEI 23-9 and subsequent variations;
* nominal voltage: 230V c.a. +/-10%, 50Hz;
* isolation resistance: >5Mohm a 250V;
* eventual serigrafy and logotype selected by DL.;
* pulling cord of at least 2mt;
RINGTONE AND BUZZERS:
* nominal voltage: 230V c.a. +/-10%, 50Hz;
* nominal power: 8VA almeno;
socket chase in autoestingueting policarbonat (UL94-V0) for click fixing and tool removal , having perforations for screw fixing for adjustable in wall box instalation ;
cover plaque of type selected by DL fixed by pressure or with tools removable screws ;
eventualy transit cassette.
Price should be inclusive of inside cabbling between sockets.
Each quotation should include evantual quote of cabbling between different elements
Optic-acoustic signal point
| GROUND FLOOR LEVEL - SOS SYSTEM |  | 2
| FIRST FLOOR LEVEL - SOS SYSTEM |  | 3
| SECOND FLOOR LEVEL - SOS SYSTEM |  | 1
| GROUND FLOOR LEVEL - SOS SYSTEM |  | 1
| Total amount |  | 7
S10.A10.A14 | CALL SYSTEM FOR DISABLED TOILETS | n
SISTEMA DI SEGNALAZIONE CHIAMATA
Call system for at least n.60 calls, extendible to n.240 chiamanti,able to perform following functions:
alfanumeric personalizable identification of at least n. 18 characters from the call point;
semplified cabbling non over n.5 conductors in maximal expansion;
call signal with visible message permanent and with sound notice contemporary;
continious monitoring fof the correct functioning of the device with coded signalisation of failures on diplay ;
memorisation of contemporary calls and cyclic visualisation of calls on display ;
signalisation permanent memory even in case of lack of supply .
cancelation of single calls from the central position or via butons in proximity of the call buton;
call repetition on other display boards;
visualisation of actual hour in absence of active calls;
priority calls programmable control;
guided informations for programming and personalisation trough remote controller.
CALL POINTS, CANCELATION AND SIGNALISATION
Call points, cancellation and signalisation are composed by:
quote of supply and signalisation composed of in wall or on wall conductor ;
quota parte delle cassette di transito e di derivazione installate lungo la dorsale;
conduits from derivation cassette installed on voltage line to socket;
cables type FM9 of section non under 1,5 mmq;
in wall socket;
appropriate identification elements/call point code;
frutti di comando e di segnalazione modulari aventi le seguenti caratteristiche:
BUTONS:
* in line with: CEI 23-9 and subsequent variations;
* nominal voltage: 230V c.a. +/-10%, 50Hz;
* isolation resistance: >5Mohm a 250V;
* eventual serigrafy and logotype selected by DL.;
* pulling cord of at least 2mt;
RINGTONE AND BUZZERS:
* nominal voltage: 230V c.a. +/-10%, 50Hz;
* nominal power: 8VA almeno;
socket chase in autoestingueting policarbonat (UL94-V0) for click fixing and tool removal , having perforations for screw fixing for adjustable in wall box instalation ;
cover plaque of type selected by DL fixed by pressure or with tools removable screws ;
eventualy transit cassette.
Price should be inclusive of inside cabbling between sockets.
Each quotation should include evantual quote of cabbling between different elements
Reset call push button
| GROUND FLOOR LEVEL - SOS SYSTEM |  | 2
| FIRST FLOOR LEVEL - SOS SYSTEM |  | 3
| SECOND FLOOR LEVEL - SOS SYSTEM |  | 1
| GROUND FLOOR LEVEL - SOS SYSTEM |  | 1
| Total amount |  | 7
S10.A10.A15 | CALL SYSTEM FOR DISABLED TOILETS | n
SISTEMA DI SEGNALAZIONE CHIAMATA
Call system for at least n.60 calls, extendible to n.240 chiamanti,able to perform following functions:
alfanumeric personalizable identification of at least n. 18 characters from the call point;
semplified cabbling non over n.5 conductors in maximal expansion;
call signal with visible message permanent and with sound notice contemporary;
continious monitoring fof the correct functioning of the device with coded signalisation of failures on diplay ;
memorisation of contemporary calls and cyclic visualisation of calls on display ;
signalisation permanent memory even in case of lack of supply .
cancelation of single calls from the central position or via butons in proximity of the call buton;
call repetition on other display boards;
visualisation of actual hour in absence of active calls;
priority calls programmable control;
guided informations for programming and personalisation trough remote controller.
CALL POINTS, CANCELATION AND SIGNALISATION
Call points, cancellation and signalisation are composed by:
quote of supply and signalisation composed of in wall or on wall conductor ;
quota parte delle cassette di transito e di derivazione installate lungo la dorsale;
conduits from derivation cassette installed on voltage line to socket;
cables type FM9 of section non under 1,5 mmq;
in wall socket;
appropriate identification elements/call point code;
frutti di comando e di segnalazione modulari aventi le seguenti caratteristiche:
BUTONS:
* in line with: CEI 23-9 and subsequent variations;
* nominal voltage: 230V c.a. +/-10%, 50Hz;
* isolation resistance: >5Mohm a 250V;
* eventual serigrafy and logotype selected by DL.;
* pulling cord of at least 2mt;
RINGTONE AND BUZZERS:
* nominal voltage: 230V c.a. +/-10%, 50Hz;
* nominal power: 8VA almeno;
socket chase in autoestingueting policarbonat (UL94-V0) for click fixing and tool removal , having perforations for screw fixing for adjustable in wall box instalation ;
cover plaque of type selected by DL fixed by pressure or with tools removable screws ;
eventualy transit cassette.
Price should be inclusive of inside cabbling between sockets.
Each quotation should include evantual quote of cabbling between different elements
Call push button
| GROUND FLOOR LEVEL - SOS SYSTEM |  | 2
| FIRST FLOOR LEVEL - SOS SYSTEM |  | 3
| SECOND FLOOR LEVEL - SOS SYSTEM |  | 1
| GROUND FLOOR LEVEL - SOS SYSTEM |  | 1
| Total amount |  | 7
TOTAL 15 - CALL DEVICES
18 - TV DEVICES
T10.A10.A1 | CENTRAL UNIT FOR TV-SAT SYSTEM WITH ANTENNAS | globally
COMPLESSO DI RICEZIONE TV E TV SATELLITE VIA CAVO
TV receiption system distributing ground tv and satelite signal from the unique antenna system and unique distributionhaving following devices:
GROUND ANTENNA SEGNAL SYSTEM
Caracteristics:
n.1 commbined antenna UHF-VHF having following caracteristics:
* VHF: channels from E5 to E12;
* UHF: channels from E21 to E69;
* gain (dBi):
+ VHF: 9
+ UHF: 16
* front back ratio: 20dB
* imped 75 Ohm;
Serie of suporters in zinked steal of lenght able to guarantee minimal distance between anntenas and between antennas and roof, complete with brackets, closing taps and wind eventual wind protection dimensioned in order tobear wind with velocity of at least 50m/s.
SATELITE ANTENNA TV SYSTEM
Caracteristics:
n. 1 parabolic antenna type having following caracteristics:
* satellite di ricezione: ASTRA, EUTELSAT;
* diameter: >= 90cm;
* entrance frequency: 10.7-12.75 GHz;
* gain: 10,95 GHz min. 41,5dB;
* junction with direction device;
* double convertor system LNB for n.8 polarised exits;
* convertitore exit frequence: 950-2150 MHz;
* convertor gain: > 50dB;
Serie of suporters in zinked steal of lenght able to guarantee minimal distance between anntenas and between antennas and roof, complete with brackets, closing taps and wind eventual wind protection dimensioned in order tobear wind with velocity of at least 50m/s.
TV-SAT AMPLIFICATORS SYSTEM
n.9 entrances (8 SAT, 1 TV);
regolable gain15 dB;
supply unit
CONNECTION CABLES
coaxial cable, with sheath PE type PAS4136104 manufactured by Fracarro or equivalent.
Usable exits from different modules should be connected between tham with bridges permitting signal transmission and supply.
Price should be inclusive of brackets and support eccessories in order to obtain complete and functional instalation.
Central unit for TV-SAT system with antennas
| SECOND FLOOR LEVEL - TV SYSTEM |  | 1
| Total amount |  | 1
T10.A10.A2 | MULTISWITCH | globally
containing metal cabinet, for instalation on wall, complete by blind door zipper opening, dimension 400x750x100 mm (bxhxp);
supply devices;
active regolable multiswitchi, low consume with following principal caracteristics :
* entrances: n.8 SAT + n.1 TV;
* modulated exits: n.16;
* gain regulation SAT: 15dB;
* gain regulation TV: 20dB;
* insertion loss: less than 2,5dB
internal signal and supply cabbling
CONNECTION CABBLING
coaxial, type Fracarro PAS4136104 or equivalent.
Multiswitch for TV-SAT system
| GROUND FLOOR LEVEL - TV SYSTEM |  | 1
| FIRST FLOOR LEVEL - TV SYSTEM |  | 1
| SECOND FLOOR LEVEL - TV SYSTEM |  | 1
| Total amount |  | 3
T20.A10.A1 | TV/SAT OUTLET | n
PUNTO PRESA TV/SAT
TV/SAT outlet for centralized devices composed by:
(eventualy) inductive cassette installed in the containment cassette quote;
conduit from derivation inductive cassette to outlet, rigid or flexible and coaxial cable.
socket complete of demodulated outlet TV+SAT and covering plaque.
coaxial cable LSZH type Fracarro PAS4206200, or equivalent, from multiswitch to field outlet.
TV/SAT outlet with flexible PVC pipe, cables and connection devices
| GROUND FLOOR LEVEL - TV SYSTEM |  | 5
| FIRST FLOOR LEVEL - TV SYSTEM |  | 7
| SECOND FLOOR LEVEL - TV SYSTEM |  | 7
| Total amount |  | 19
TOTAL 18 - TV DEVICES
11 - TRANSMISSION DATA AND TELEPHONE DEVICES
X10.A10.A2 | COMMUNICATION DATA RACK 19" | n
RACK 19" DI PERMUTAZIONE
Compliance with standards: DIN 41488, 41494/1.
Structural characteristics:
_modular supporting structure is made of extruded profiles aluminum and angular elements that can be composed of living under the aluminum strainer;
_ roof, lateral, back and floor panel to cover the steel minimum thickness of 1.5 mm;
_ basic processing of sheet metal and structures obtained by electrophoresis color RAL 7044; finish painting with epoxy powder RAL 7035;
_ execution on the floor (equipped with screw-in part for the support of painted sheet metal) or on a wall, depending on how it is provided in graphic tables;
_ lateral and rear panels of blind type;
_ front panel blind type of painted steel or anodized aluminum, for the completion and closure of premises that are not used by setting;
_ front door of a transparent type with a frame whose edges on all sides are coated colored sheet; safety glass thickness min. 3mm; joints that are able to provide a door opening angle of at least 105 °, in the number 2 on the panel up to 1200mm, no. 3 h. from 1400 to 1600mm, no.4 by h. 1800 to 2000; point of closure on the side of hitting the same number of joints;
_ handle for closing with a unique key (if there is no lock that is controlled by access control system);
_ flexible grounding or earthing systems on all movable panels for sealing and sliding surfaces as well as in all the metallic elements that serve as support to active devices in the network;
_ shelves for placement of network devices from galvanized, perforated, painted steel, fixed or type to pull using groove for sliding made ​​of galvanized plated steel, which has a handle to pull the chrome galvanized steel;
_ box for placing a keyboard that has the same characteristics as pulling shelves , equipped with a folding vertical part of the step;
_ legs for control at the bottom with a lock-nut for blocking;
_ grids for ventilation with filter with fine grid against dust (if inside the panel there is no air conditioning system);
_ forced ventilation system with a load capacity of air 150mc / h installed on the roof (if inside the panel there is no air conditioning system) with power supply 230V + / -10% c.a. 50Hz, connected to the panel for power and managrd by the internal thermostat;
_ panel for power supply made of:
* no. 2 overall switches (input line UPS and output line UPS) automatic modular type 2x16 curve C, Pi 6kA, Id 30mA type A;
* no. .. 7 sockets of universal type (bipolar conflict with a hole in the earth at the center) to the axis of polarity leaned compared to to the axis of panels to be m + allow the use of all sockets without obstacles or interference on the cables that come out from within the plugs;
_ pocket for placing documents from hard plastic (excluding flexible transparent bags made ​​of nylon or similar) installed in panels or in a place defined by the company;
_ blind panels in at least 15% of available frontal surface (excluding ventilation panels and panels for power supply);
_ additional elements for setting cables such as:
* constructions for setting PVC cbales, which have spare space in the amount of at least 50% of the space they occupy;
* vertical cable management rings for every 25 cm height of the panels installed on both sides;
* round covers for covering strip, surge protectors, protective screens, etc.., for all of the devices and power supply parts in order to still guarantee a degree of protection not less than IP20 on open panels;
_ external level protection : IP40 or as indicated in graphic tables, including the bottom;
_ dimensions as described in the types with the indicated base in mm (width x depth) and height in units of standard 19 "(each unit corresponds to the size of 44.45 mm).
Communication data rack 19" 800x800mm 42U
| FIRST FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 4
| SECOND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 1
| Total amount |  | 5
X10.A10.A3 | COMMUNICATION DATA RACK 19" | n
RACK 19" DI PERMUTAZIONE
Compliance with standards: DIN 41488, 41494/1.
Structural characteristics:
_modular supporting structure is made of extruded profiles aluminum and angular elements that can be composed of living under the aluminum strainer;
_ roof, lateral, back and floor panel to cover the steel minimum thickness of 1.5 mm;
_ basic processing of sheet metal and structures obtained by electrophoresis color RAL 7044; finish painting with epoxy powder RAL 7035;
_ execution on the floor (equipped with screw-in part for the support of painted sheet metal) or on a wall, depending on how it is provided in graphic tables;
_ lateral and rear panels of blind type;
_ front panel blind type of painted steel or anodized aluminum, for the completion and closure of premises that are not used by setting;
_ front door of a transparent type with a frame whose edges on all sides are coated colored sheet; safety glass thickness min. 3mm; joints that are able to provide a door opening angle of at least 105 °, in the number 2 on the panel up to 1200mm, no. 3 h. from 1400 to 1600mm, no.4 by h. 1800 to 2000; point of closure on the side of hitting the same number of joints;
_ handle for closing with a unique key (if there is no lock that is controlled by access control system);
_ flexible grounding or earthing systems on all movable panels for sealing and sliding surfaces as well as in all the metallic elements that serve as support to active devices in the network;
_ shelves for placement of network devices from galvanized, perforated, painted steel, fixed or type to pull using groove for sliding made ​​of galvanized plated steel, which has a handle to pull the chrome galvanized steel;
_ box for placing a keyboard that has the same characteristics as pulling shelves , equipped with a folding vertical part of the step;
_ legs for control at the bottom with a lock-nut for blocking;
_ grids for ventilation with filter with fine grid against dust (if inside the panel there is no air conditioning system);
_ forced ventilation system with a load capacity of air 150mc / h installed on the roof (if inside the panel there is no air conditioning system) with power supply 230V + / -10% c.a. 50Hz, connected to the panel for power and managrd by the internal thermostat;
_ panel for power supply made of:
* no. 2 overall switches (input line UPS and output line UPS) automatic modular type 2x16 curve C, Pi 6kA, Id 30mA type A;
* no. .. 7 sockets of universal type (bipolar conflict with a hole in the earth at the center) to the axis of polarity leaned compared to to the axis of panels to be m + allow the use of all sockets without obstacles or interference on the cables that come out from within the plugs;
_ pocket for placing documents from hard plastic (excluding flexible transparent bags made ​​of nylon or similar) installed in panels or in a place defined by the company;
_ blind panels in at least 15% of available frontal surface (excluding ventilation panels and panels for power supply);
_ additional elements for setting cables such as:
* constructions for setting PVC cbales, which have spare space in the amount of at least 50% of the space they occupy;
* vertical cable management rings for every 25 cm height of the panels installed on both sides;
* round covers for covering strip, surge protectors, protective screens, etc.., for all of the devices and power supply parts in order to still guarantee a degree of protection not less than IP20 on open panels;
_ external level protection : IP40 or as indicated in graphic tables, including the bottom;
_ dimensions as described in the types with the indicated base in mm (width x depth) and height in units of standard 19 "(each unit corresponds to the size of 44.45 mm).
Communication data rack 19" 800x1000mm 42U
| GROUND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 3
| Total amount |  | 3
X10.A23.A4 | JACK PANEL FOR RJ45 OUTLETS | n
PANNELLO DI PERMUTAZIONE IN RAME CAT.6
Compliance with standards: TIA/EIA 568-B-2.1 e ISO/IEC11801/2
Structural characteristics:
_ structure of painted sheet metal thickness of 10mm, equipped with support for rack 19 "1U;
_ holes for confirmation at least br.24 sockets RJ45;
_ horizontal panel for conducting cables, size 1U;
_ sockets RJ45 with following characteristics:
* contact for confirmation of conductors with a diameter of 0.4 to 0.65 mm;
* display on the monitor cat.6A;
* marks and label brackets for identification initialed outlet.
The price includes:
_ testing of connectors.
RJ45 jack panel, empty, rack mountable
| GROUND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 4
| FIRST FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 32
| SECOND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 9
| Total amount |  | 45
X10.A23.A6 | JACK PANEL FOR RJ45 OUTLETS | n
PANNELLO DI PERMUTAZIONE IN RAME CAT.6
Compliance with standards: TIA/EIA 568-B-2.1 e ISO/IEC11801/2
Structural characteristics:
_ structure of painted sheet metal thickness of 10mm, equipped with support for rack 19 "1U;
_ holes for confirmation at least br.24 sockets RJ45;
_ horizontal panel for cable management, size 1U;
_ sockets RJ45 with following characteristics:
* contact for confirmation of conductors with a diameter of 0.4 to 0.65 mm;
* display on the monitor cat.6A;
* marks and label brackets for identification initialed sockets for comutation.
The price includes:
_ testing of connectors.
RJ45 category outlet for jack panel and connection
| GROUND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 82
| FIRST FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 729
| SECOND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 152
| Total amount |  | 963
X10.A26.A13 | JACK PANEL FOR FIBER OPTIC CABLES | n
PANNELLO DI PERMUTAZIONE PER FIBRE OTTICHE
Compliance with standards: EIA/TIA 568-A I B, IEC 874/14, ISO 11801, DIN41488.
Structural characteristics:
_ modular metal box in version rack 19 "1U of at least two entries for fiber optical cables;
_ No.24 holes for installation of single mode optocoupler type LC; optokapleri
_ upper transparent sliding cover;
_ module capsule cable for optical suspenders;
_ rails for fibers and internal fixation system for fixing individual fibers;tračnica
_ blind plugs for closing unused hole;
_ panel for cable management, size 1U;
* marks and label brackets for identifying sockets for comutation. komutaciju.
The price includes:
_ single mode LC-type connectors;
_ testing of connectors;
_ testing with OTDR technique.
12 singlemode fiber optic cable jack panel and connection
| GROUND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 4
| FIRST FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 2
| SECOND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 1
| Total amount |  | 7
X100.A20.A11 | N.3 TELECOM OUTLET RJ45 CAT. 6A INSTALLED ON THE FLOOR BOX | n
transmission data otlet point equivalent composed by:
n.3 outlets RJ45 cat.6A,
cables SFTP cat 6A from rack of FD to outlet (medium distance70m);
socket plaque covering chase for at least n.3 outlets to be installed on tower frutti;
identification of each outlet;
covering taps on each outlet to avoid dust entrance;
flexible tube in PVC from channel to tower by floor.
Price is inclusive of certificate of "permanent link" in line with CEI EN 50173 e 50174 and closure of outlet with appropriate tap after certification.
n.3 telecom outlet RJ45 cat.6a installed on the floor box
| GROUND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 10
| FIRST FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 213
| SECOND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 24
| GROUND FLOOR LEVEL - VIDEO ENTRY PHONE SYSTEM |  | 16
| Total amount |  | 263
X100.A21.A1 | TELECOM OUTLET RJ45 CAT. 6A | n
transmission data otlet point equivalent composed by:
containing box in wall or on wall (indicated in short descriptions);
outlets RJ45 cat.6A, (number indicated in short descriptions)
cables SFTP cat 6A from rack of FD to outlet (medium distance 70m);
socket plaque covering chase for the number of sockets to be installed in the box;
(eventual) transit cassette;
identification of each outlet;
covering taps on each outlet to avoid dust entrance;
flexsible tube in PVC (for in wall instalation) diameter 32 mm, rigid tube in PVC (for instalation on wall) diameter 32 mm, from channel to containing box.
Price is inclusive of certificate of "permanent link" in line with CEI EN 50173 e 50174 and closure of outlet with appropriate tap after certification.
n.2 telecom outlet RJ45 cat.6a in wall with tube in PVC flexsible
| GROUND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 4
| FIRST FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 8
| SECOND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 1
| Total amount |  | 13
X100.A21.A2 | TELECOM OUTLET RJ45 CAT. 6A | n
transmission data otlet point equivalent composed by:
containing box in wall or on wall (indicated in short descriptions);
outlets RJ45 cat.6A, (number indicated in short descriptions)
cables SFTP cat 6A from rack of FD to outlet (medium distance 70m);
socket plaque covering chase for the number of sockets to be installed in the box;
(eventual) transit cassette;
identification of each outlet;
covering taps on each outlet to avoid dust entrance;
flexsible tube in PVC (for in wall instalation) diameter 32 mm, rigid tube in PVC (for instalation on wall) diameter 32 mm, from channel to containing box.
Price is inclusive of certificate of "permanent link" in line with CEI EN 50173 e 50174 and closure of outlet with appropriate tap after certification.
n.2 telecom outlet RJ45 cat.6a on wall WiFi with tube in PVC rigido
| GROUND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 3
| FIRST FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 7
| SECOND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 4
| GROUND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 3
| Total amount |  | 17
X100.A21.A3 | TELECOM OUTLET RJ45 CAT. 6A | n
transmission data otlet point equivalent composed by:
containing box in wall or on wall (indicated in short descriptions);
outlets RJ45 cat.6A, (number indicated in short descriptions)
cables SFTP cat 6A from rack of FD to outlet (medium distance 70m);
socket plaque covering chase for the number of sockets to be installed in the box;
(eventual) transit cassette;
identification of each outlet;
covering taps on each outlet to avoid dust entrance;
flexsible tube in PVC (for in wall instalation) diameter 32 mm, rigid tube in PVC (for instalation on wall) diameter 32 mm, from channel to containing box.
Price is inclusive of certificate of "permanent link" in line with CEI EN 50173 e 50174 and closure of outlet with appropriate tap after certification.
n.2 telecom outlet RJ45 cat.6a on wall for multimedial with tube in PVC rigido
| FIRST FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 3
| SECOND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 6
| GROUND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 5
| Total amount |  | 14
X100.A21.A4 | TELECOM OUTLET RJ45 CAT. 6A | n
transmission data otlet point equivalent composed by:
containing box in wall or on wall (indicated in short descriptions);
outlets RJ45 cat.6A, (number indicated in short descriptions)
cables SFTP cat 6A from rack of FD to outlet (medium distance 70m);
socket plaque covering chase for the number of sockets to be installed in the box;
(eventual) transit cassette;
identification of each outlet;
covering taps on each outlet to avoid dust entrance;
flexsible tube in PVC (for in wall instalation) diameter 32 mm, rigid tube in PVC (for instalation on wall) diameter 32 mm, from channel to containing box.
Price is inclusive of certificate of "permanent link" in line with CEI EN 50173 e 50174 and closure of outlet with appropriate tap after certification.
n.2 telecom outlet RJ45 cat.6a on wall for access control with tube in PVC rigido
| GROUND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 3
| FIRST FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 1
| SECOND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 1
| GROUND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 2
| Total amount |  | 7
X100.A21.A5 | TELECOM OUTLET RJ45 CAT. 6A | n
transmission data otlet point equivalent composed by:
containing box in wall or on wall (indicated in short descriptions);
outlets RJ45 cat.6A, (number indicated in short descriptions)
cables SFTP cat 6A from rack of FD to outlet (medium distance 70m);
socket plaque covering chase for the number of sockets to be installed in the box;
(eventual) transit cassette;
identification of each outlet;
covering taps on each outlet to avoid dust entrance;
flexsible tube in PVC (for in wall instalation) diameter 32 mm, rigid tube in PVC (for instalation on wall) diameter 32 mm, from channel to containing box.
Price is inclusive of certificate of "permanent link" in line with CEI EN 50173 e 50174 and closure of outlet with appropriate tap after certification.
n.2 telecom outlet RJ45 cat.6a on wall for camera with tube in PVC rigido
| GROUND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 1
| GROUND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 2
| Total amount |  | 3
X100.A21.A7 | TELECOM OUTLET RJ45 CAT. 6A | n
transmission data otlet point equivalent composed by:
containing box in wall or on wall (indicated in short descriptions);
outlets RJ45 cat.6A, (number indicated in short descriptions)
cables SFTP cat 6A from rack of FD to outlet (medium distance 70m);
socket plaque covering chase for the number of sockets to be installed in the box;
(eventual) transit cassette;
identification of each outlet;
covering taps on each outlet to avoid dust entrance;
flexsible tube in PVC (for in wall instalation) diameter 32 mm, rigid tube in PVC (for instalation on wall) diameter 32 mm, from channel to containing box.
Price is inclusive of certificate of "permanent link" in line with CEI EN 50173 e 50174 and closure of outlet with appropriate tap after certification.
n.2 telecom outlet RJ45 cat.6a on wall for camera with tube in PVC rigido
| GROUND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 4
| FIRST FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 1
| SECOND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 4
| GROUND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 1
| Total amount |  | 10
X100.A21.A8 | TELECOM OUTLET RJ45 CAT. 6A | n
transmission data otlet point equivalent composed by:
containing box in wall or on wall (indicated in short descriptions);
outlets RJ45 cat.6A, (number indicated in short descriptions)
cables SFTP cat 6A from rack of FD to outlet (medium distance 70m);
socket plaque covering chase for the number of sockets to be installed in the box;
(eventual) transit cassette;
identification of each outlet;
covering taps on each outlet to avoid dust entrance;
flexsible tube in PVC (for in wall instalation) diameter 32 mm, rigid tube in PVC (for instalation on wall) diameter 32 mm, from channel to containing box.
Price is inclusive of certificate of "permanent link" in line with CEI EN 50173 e 50174 and closure of outlet with appropriate tap after certification.
n.3 telecom outlet RJ45 cat.6a in wall with tube in PVC flexsible
| SECOND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 4
| Total amount |  | 4
X100.A22.A1 | CONNECTION RACK 19" FOR MULTIMEDIA EQUIPMENTS TO FLOOR DISTRIBUTOR | n
Composed by:
n.4 cables SFTP cat 6A from rack FD to multimedial cabinet (medium 70m for single connection);
patch panel with four positions installed in multimedial cabinet type rack 19";
n.4 connectors RJ45 cat.6A attesting cables SFTP to be installed on rack;
attests;
each outlet marked;
closing taps for each outlot to prevent dust entrance ;
n.2 tubi flexible tubes PVC diameter 32 mm from channel to cabinet.
Price is inclusive of certificate of "permanent link" in line with CEI EN 50173 e 50174 and closure of outlet with appropriate tap after certification.
Connection rack 19" for multimedia equipments to floor distributor
| FIRST FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 3
| SECOND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 6
| Total amount |  | 9
X100.A23.A1 | N.3 TELECOM OUTLET RJ45 CAT. 6A INSTALLED ON THE FLOOR BOX PREDISPOSED FOR MULTIMEDIA | n
Transmission point outlet equivalent composed by:
n.3 outlets RJ45 cat.6A,
cables SFTP cat 6A from rack FD to outlet (medium distance 70m);
socket plaque covering chase for at least n.3 sockets to be installed on tower;
each outlet marked;
closing taps for each outlot to prevent dust entrance ;
n.2 tubi flexible tubes PVC diameter 32 mm from channel to floor tower.
Price is inclusive of certificate of "permanent link" in line with CEI EN 50173 e 50174 and closure of outlet with appropriate tap after certification.
n.3 telecom outlet RJ45 cat.6a installed on the floor box predisposed for multimedia
| FIRST FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 3
| SECOND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 6
| GROUND FLOOR LEVEL - TRANSMISSION DATA AND TELEPHONE |  | 5
| Total amount |  | 14
TOTAL 11 - TRANSMISSION DATA AND TELEPHONE DEVICES
16 - SUPERVISION, ACCESS CONTROLL AND TVCC
Y100.A10.A1 | BUILDING MANAGEMENT SYSTEM (BMS) | n
SISTEMA DI CONTROLLO CENTRALIZZATO IMPIANTI (BMS SYSTEM)
Control system with an integrated command for automatic control of electrical installations, single software platform for fire and security systems, thermotechnical systems (described in Volume 3 (Book 3) of thermomechanical installations project) by using BACNet over IP protocol for fire and thermotechnics. Fully integrated with light control system using protocol communication (KNX/EIB) Building Management System, which consists of the following elements:
N.1 Computer for monitoring with software SCADA (Supervisory Control And Data Acquisition) WinCC, with the base for processing data from the electrical system, "high voltage", safety, security and thermomechanization that the graphical interface allows the user to visualize the following functions:
_electrical installation of high voltage (high voltage):
* value and status that come directly from the buses, from connected units to the microprocessor installed in the electrical command panels;
* status and alarm of clicking relay which is emitted by switches managed by the control panels;
* status and alarms UPS;
*status values ​​and alarms photovoltage system;
*status and alarm of main apparatus on substation.
_safety installations (fire and gas indicators)
* status and alarms of switchboards;
* status of the serial lines and indicator curcuits;
* status and alarms of indicators, with planimetric representation of their positions;
* state and planimetric position of buttons for alarm;
* status of input and output modules
_installation of sound signalization for evacuation
* status of central unit;
* status of amplitude line;
_safety installations (burglary, access control, CCTV)
* status and position of module for transition management;
* status/alarm/planimetric position of indication elements;
* status of burglary switchboard.
_Lighting system:
* status of individual control units;
* control and regulation of illuminotechnical status in different environments (ON/OFF/DIMM);
*possibility of programming lighting scenario
*night configuration
_Part with alarms for display of alarms from all installations and keeping them in a database;
_Part with trend graphic for transition:
*energy production from photovoltage (daily, hourly, monthly, annual);
* energy consumption of the building;
*alarms from external devices.
CONTROL UNIT OF ELECTRICAL HIGH VOLTAGE INSTALLATIONS consists of the following elements:
_unit for receiving digital input, installed in electric command panels (unit at the terrain), connected to the PLC via lines Bus, Modbus or Profibus; will have to serve as electrical isolation (galvanic separation) between the low-voltage device which needs to be managed and very low voltage within the control modules, which include optical signals, which refers to signals that are received, and the functions in progress.
_unit for receiving digital input, installed in electric panels (unit at the terrain), connected to the PLC via Bus lines, Modbus or Profibus, will have to serve as electrical isolation (galvanic separation) between the low-voltage maintained apparatus and the lowest voltage within the control module, which contain optical signalization, which refers to signals that are received, and the functions in progress.
_peripheral units for management and automation of operating island (PLC) that are installed with various electric command panles, consist of:
* power supply units 230 V AC 50 Hz with transformer on 24 VDC;
* scheme processors with inputs of serial interface with a standard protocol Modbus or Profibus for connecting units at the terrain;
* network cards with protocol serial port RS485 Modbus or Profibus for connection to a PC for supervision;
terminal module with terminal setup and power supply modules interface and for connecting to the control modules, have the following features:
* plastic holder for snap installation on guide DIN with a mesh insulating plates (stripboard) with the runway for the power supply and data transmission terminals for power supply, fuses, broadband cable connector for connection to the control module, connector screw for connection of interfaces is not the spaces provided
* voltage and frequence of power supply: 24V AC, +15/-10% - 50Hz;
* insulation level: class II;
* protection level: min. IP20.
_bus line protected with 4 conductors section 24 AWG, the serial connection of different elements that make up the system;
_router for conversion of serial line to network TCP/IP for communication with supervisor computer, with patch cord in cat.6A;
_dress package through conductors, accessories and smallparts;
_programming and techical system check;
LIGHTING CONTROL SYSTEM
Consists of the following parts:
_POWER SUPPLY OF BUS LINES suitable for installation on supporter DIN 35mm (inside the electrical panels) output voltage 640mA;
_THE JOINTS BETWEEN MAIN AND SECONDARY BUS LINE with galvanic separation thereof, suitable for installation on DIN 35mm (inside the electrical panels), suitable for data transmission of bus telegrams from one curcuit to another, and vice versa (potential short circuits on the secondary bus lines have been discovered and there is no transmission); ;
_MODULE FOR MANAGEMENT OF ELECTRONIC REACTOR, SILENCERS AND STEERABLE (DALI) with the following characteristics:
* line management, each with 64 reactors/electrical transformes DALI, which can be split into 16 independent illuminotechnical conditions;
* darkening 1÷100%;
* possibility of failure signalization in the system;
* command cables of changing polarities;
* connecting using clamps with screws;
* protection level min: IP20, dim: 40 x 30 x 270L mm.
* interface EIB/KNX;
MODULES INPUT MODELS WITH KEYS suitable for installation inside the box 503 with the following characteristics:
* 4 entrances separated from keys ;
*depending on the direction of the module, you can manage all the terminals of a system: Briefly pressing the appropriate button switches from one state to another (state "Missing" and state "Present"). A long press on the button increases or decreases shading of complete lighting or a group;
* cable long 5m prefabricated,for connecting module and key;
*protection level min: IP20, dim: 40 x 40 x 17 p mm.
DIGITAL OUTPUT MODULE WITH 4 POTENTIAL-FREE CONTACTS
has following characteristics:
*output relay with contacts for controlling and the independent directing for switching of electrical installations with voltage network up to 230/240V;
* conductivity of contacts: 10A u AC1;
*connecting with clamps with screws;
* test key, LED for signalisation;
*installation into electrical box on DIN carrier 35 mm;
* protection level min: IP20, dim: 3 moduls.
PRESENCE OF LIGHT SENSOR (included in the BoQ Books (Book) 4 "high voltage") for inclusion of internal illumination system or control of the level of illumination as a function of contributions to natural light, with the following characteristics:
* installation in a prominent place on the ceiling or on the wooden beam by using particular carrier (the last one is included);
* auto power off function;
*the presence indicator is integrated with a time delay compared to the shutdown between 30 seconds and 20 minutes;
presence of indicator zone: dimensions around 4,0x4,0 m (when people are sitting) ili 6,0x6,0 m (people are moving) za Hinst=2,5m; dim. oko 4,5x4,5 m (people are sitting) ili 7,0x7,0 m (preople are moving)for Hinst=3,0m;
*indication field of illumination value: od 6 do 1.600 [lx];
* angle of sensor viewing around 120° (vertical); 360° (horizontal);
*protection level: IP20, dim. Oko 100x100x55 h mm.
router to convert a serial line EIB / KNX in the network ethernet TCP / IP to communicate with a computer for monitoring, which consists of di patch cord in cat. 6A;
bus network EIB/KNX implemented with certified cables;
bus network DALI implemented with certified cables;
INTERFACE DEVICES FOR LOW VOLTAGE INSTALLATIONS
Consists of:
BACNet over IP communication for fire detection, router for gas, embedded protocols for systems against burglary, which enable monitoring and full control for ALL data points by network LAN Ethernet with protocole TCP / IP; will also be equipped with a driver that will enable translation within the central database with the data obtained by the computer supervisor;
interface switchboard sound system using digital contacts at the entrance to the switchboard for fire detection;
interface access control system using the database within the computer for control that is dedicated to access control system;
Interface CCTV camera system using a digital contacts on the door alarm system on the entrance of the antiburglar system.
CONTROL POINT FOR ELECTRICAL INSTALLATIONS OF HIGH VOLTAGE
Consists of:
a control units for the control with the schemes in the area of ​​the ports sufficient to manage controlled points , which are required for the control of a specific apparatus or an electrical frame;
bus line;
electric voltage of control apparatus;
part of the quota computer for supervision;
graphic station for review of controlled points;
licence.
CONTROL POINT OF LIGHTING DEVICES
Consists of:
_ regulation units installed in electric panels for BUS DALI and EIB/KNX;
_ units for management at the terrain for procurement of keys and presence and lighting indicators;
_ router;
_ bus DALI i EIB/KNX;
_ electric power supply of command devices;
_ part of the quota computer for supervision;;
_ graphic for mapping of configured system and systems for control of lighting and technical configurations;
_ licence.
CONTROL POINT OF SPECIAL DEVICES
Consists of:
_ interface router switchboard with supervisor;
_ part of the quota computer for supervision;
_ graphic for mapping controlled devices and for status visualization of status/alarm;
_ licence.
Control points are specificially indicated in appropriate paragraph Address Points
BMS input/output address point for electrical plants
| GROUND FLOOR LEVEL - BMS SYSTEM |  | 1
| FIRST FLOOR LEVEL - BMS SYSTEM |  | 1
| SECOND FLOOR LEVEL - BMS SYSTEM |  | 1
| GROUND FLOOR LEVEL - BMS SYSTEM |  | 1
| Total amount |  | 1
Y100.A10.A2 | BUILDING MANAGEMENT SYSTEM (BMS) | n
SISTEMA DI CONTROLLO CENTRALIZZATO IMPIANTI (BMS SYSTEM)
Control system with an integrated command for automatic control of electrical installations, single software platform for fire and security systems, thermotechnical systems (described in Volume 3 (Book 3) of thermomechanical installations project) by using BACNet over IP protocol for fire and thermotechnics. Fully integrated with light control system using protocol communication (KNX/EIB) Building Management System, which consists of the following elements:
N.1 Computer for monitoring with software SCADA (Supervisory Control And Data Acquisition) WinCC, with the base for processing data from the electrical system, "high voltage", safety, security and thermomechanization that the graphical interface allows the user to visualize the following functions:
_electrical installation of high voltage (high voltage):
* value and status that come directly from the buses, from connected units to the microprocessor installed in the electrical command panels;
* status and alarm of clicking relay which is emitted by switches managed by the control panels;
* status and alarms UPS;
*status values ​​and alarms photovoltage system;
*status and alarm of main apparatus on substation.
_safety installations (fire and gas indicators)
* status and alarms of switchboards;
* status of the serial lines and indicator curcuits;
* status and alarms of indicators, with planimetric representation of their positions;
* state and planimetric position of buttons for alarm;
* status of input and output modules
_installation of sound signalization for evacuation
* status of central unit;
* status of amplitude line;
_safety installations (burglary, access control, CCTV)
* status and position of module for transition management;
* status/alarm/planimetric position of indication elements;
* status of burglary switchboard.
_Lighting system:
* status of individual control units;
* control and regulation of illuminotechnical status in different environments (ON/OFF/DIMM);
*possibility of programming lighting scenario
*night configuration
_Part with alarms for display of alarms from all installations and keeping them in a database;
_Part with trend graphic for transition:
*energy production from photovoltage (daily, hourly, monthly, annual);
* energy consumption of the building;
*alarms from external devices.
CONTROL UNIT OF ELECTRICAL HIGH VOLTAGE INSTALLATIONS consists of the following elements:
unit for receiving digital input, installed by the electrical boxes (unit in the open), connected to the PLC via lines Bus, Modbus or Profibus, will have to serve as electrical isolation (galvanic separation) between the low-voltage of maintained apparatus and the lowest voltages within the control modules, which include optical signals, which refers to signals that are received, and the functions in progress.
_unit for receiving digital input, installed in electric panels (unit at the terrain), connected to the PLC via Bus lines, Modbus or Profibus, will have to serve as electrical isolation (galvanic separation) between the low-voltage maintained apparatus and the lowest voltage within the control module, which contain optical signalization, which refers to signals that are received, and the functions in progress.
_peripheral units for management and automation of operating island (PLC) that are installed with various electric command panles, consist of:
* power supply units 230 V AC 50 Hz with transformer on 24 VDC;
* scheme processors with inputs of serial interface with a standard protocol Modbus or Profibus for connecting units at the terrain;
* network cards with protocol serial port RS485 Modbus or Profibus for connection to a PC for supervision;
terminal module with terminal setup and power supply modules interface and for connecting to the control modules, have the following features:
* plastic holder for snap installation on guide DIN with a mesh insulating plates (stripboard) with the runway for the power supply and data transmission terminals for power supply, fuses, broadband cable connector for connection to the control module, connector screw for connection of interfaces is not the spaces provided
* voltage and frequence of power supply: 24V AC, +15/-10% - 50Hz;
* insulation level: class II;
* protection level: min. IP20.
_bus line protected with 4 conductors section 24 AWG, the serial connection of different elements that make up the system;
_router for conversion of serial line to network TCP/IP for communication with supervisor computer, with patch cord in cat.6A;
_dress package through conductors, accessories and smallparts;
_programming and techical system check;
LIGHTING CONTROL SYSTEM
Consists of the following parts:
_POWER SUPPLY OF BUS LINES suitable for installation on supporter DIN 35mm (inside the electrical panels) output voltage 640mA;
_THE JOINTS BETWEEN MAIN AND SECONDARY BUS LINE with galvanic separation thereof, suitable for installation on DIN 35mm (inside the electrical panels), suitable for data transmission of bus telegrams from one curcuit to another, and vice versa (potential short circuits on the secondary bus lines have been discovered and there is no transmission); ;
_MODULE FOR MANAGEMENT OF ELECTRONIC REACTOR, SILENCERS AND STEERABLE (DALI) with the following characteristics:
* line management, each with 64 reactors/electrical transformes DALI, which can be split into 16 independent illuminotechnical conditions;
* darkening 1÷100%;
* possibility of failure signalization in the system;
* command cables of changing polarities;
* connecting using clamps with screws;
* protection level min: IP20, dim: 40 x 30 x 270L mm.
* interface EIB/KNX;
MODULES INPUT MODELS WITH KEYS suitable for installation inside the box 503 with the following characteristics:
* 4 entrances separated from keys ;
*depending on the direction of the module, you can manage all the terminals of a system: Briefly pressing the appropriate button switches from one state to another (state "Missing" and state "Present"). A long press on the button increases or decreases shading of complete lighting or a group;
* cable long 5m prefabricated,for connecting module and key;
*protection level min: IP20, dim: 40 x 40 x 17 p mm.
DIGITAL OUTPUT MODULE WITH 4 POTENTIAL-FREE CONTACTS
has following characteristics:
*output relay with contacts for controlling and the independent directing for switching of electrical installations with voltage network up to 230/240V;
* conductivity of contacts: 10A u AC1;
*connecting with clamps with screws;
* test key, LED for signalisation;
*installation into electrical box on DIN carrier 35 mm;
* protection level min: IP20, dim: 3 moduls.
PRESENCE OF LIGHT SENSOR (included in the BoQ Books (Book) 4 "high voltage") for inclusion of internal illumination system or control of the level of illumination as a function of contributions to natural light, with the following characteristics:
* installation in a prominent place on the ceiling or on the wooden beam by using particular carrier (the last one is included);
* auto power off function;
*the presence indicator is integrated with a time delay compared to the shutdown between 30 seconds and 20 minutes;
presence of indicator zone: dimensions around 4,0x4,0 m (when people are sitting) ili 6,0x6,0 m (people are moving) za Hinst=2,5m; dim. oko 4,5x4,5 m (people are sitting) ili 7,0x7,0 m (preople are moving)for Hinst=3,0m;
*indication field of illumination value: od 6 do 1.600 [lx];
* angle of sensor viewing around 120° (vertical); 360° (horizontal);
*protection level: IP20, dim. Oko 100x100x55 h mm.
router to convert a serial line EIB / KNX in the network ethernet TCP / IP to communicate with a computer for monitoring, which consists of di patch cord in cat. 6A;
bus network EIB/KNX implemented with certified cables;
bus network DALI implemented with certified cables;
INTERFACE DEVICES FOR LOW VOLTAGE INSTALLATIONS
Consists of:
BACNet over IP communication for fire detection, gas and against burglary, which enable translation of serial line that comes from the individual switchboards in network LAN Ethernet with protocole TCP / IP; will also be equipped with a driver that will enable translation within the central database with the data obtained by the computer supervisor;
interface switchboard sound system using digital contacts at the entrance to the switchboard for fire detection;
interface access control system using the database within the computer for control that is dedicated to access control system;
Interface CCTV camera system using a digital contacts on the door alarm system on the entrance of the antiburglar system.
CONTROL POINT FOR ELECTRICAL INSTALLATIONS OF HIGH VOLTAGE
Consists of:
a control units for the control with the schemes in the area of ​​the ports sufficient to manage controlled points , which are required for the control of a specific apparatus or an electrical frame;
bus line;
electric voltage of control apparatus;
part of the quota computer for supervision;
graphic station for review of controlled points;
licence.
CONTROL POINT OF LIGHTING DEVICES
Consists of:
_ regulation units installed in electric panels for BUS DALI and EIB/KNX;
_ units for management at the terrain for procurement of keys and presence and lighting indicators;
_ router;
_ bus DALI i EIB/KNX;
_ electric power supply of command devices;
_ part of the quota computer for supervision;;
_ graphic for mapping of configured system and systems for control of lighting and technical configurations;
_ licence.
CONTROL POINT OF SPECIAL DEVICES
Consists of:
_ interface router switchboard with supervisor;
_ part of the quota computer for supervision;
_ graphic for mapping controlled devices and for status visualization of status/alarm;
_ licence.
Control points are specificially indicated in appropriate paragraph Address Points
BMS input/output address point for control lighting system
| GROUND FLOOR LEVEL - BMS SYSTEM |  | 1
| FIRST FLOOR LEVEL - BMS SYSTEM |  | 1
| SECOND FLOOR LEVEL - BMS SYSTEM |  | 1
| GROUND FLOOR LEVEL - BMS SYSTEM |  | 1
| Total amount |  | 1
Y100.A10.A3 | BUILDING MANAGEMENT SYSTEM (BMS) | n
SISTEMA DI CONTROLLO CENTRALIZZATO IMPIANTI (BMS SYSTEM)
Control system with an integrated command for automatic control of electrical installations, single software platform for fire and security systems, thermotechnical systems (described in Volume 3 (Book 3) of thermomechanical installations project) by using BACNet over IP protocol for fire and thermotechnics. Fully integrated with light control system using protocol communication (KNX/EIB) Building Management System, which consists of the following elements:
N.1 Computer for monitoring with software SCADA (Supervisory Control And Data Acquisition) WinCC, with the base for processing data from the electrical system, "high voltage", safety, security and thermomechanization that the graphical interface allows the user to visualize the following functions:
_electrical installation of high voltage (high voltage):
* value and status that come directly from the buses, from connected units to the microprocessor installed in the electrical command panels;
* status and alarm of clicking relay which is emitted by switches managed by the control panels;
* status and alarms UPS;
*status values ​​and alarms photovoltage system;
*status and alarm of main apparatus on substation.
_safety installations (fire and gas indicators)
* status and alarms of switchboards;
* status of the serial lines and indicator curcuits;
* status and alarms of indicators, with planimetric representation of their positions;
* state and planimetric position of buttons for alarm;
* status of input and output modules
_installation of sound signalization for evacuation
* status of central unit;
* status of amplitude line;
_safety installations (burglary, access control, CCTV)
* status and position of module for transition management;
* status/alarm/planimetric position of indication elements;
* status of burglary switchboard.
_Lighting system:
* status of individual control units;
* control and regulation of illuminotechnical status in different environments (ON/OFF/DIMM);
*possibility of programming lighting scenario
*night configuration
_Part with alarms for display of alarms from all installations and keeping them in a database;
_Part with trend graphic for transition:
*energy production from photovoltage (daily, hourly, monthly, annual);
* energy consumption of the building;
*alarms from external devices.
CONTROL UNIT OF ELECTRICAL HIGH VOLTAGE INSTALLATIONS consists of the following elements:
_unit for receiving digital input, installed in electric command panels (unit at the terrain), connected to the PLC via lines Bus, Modbus or Profibus; will have to serve as electrical isolation (galvanic separation) between the low-voltage device which needs to be managed and very low voltage within the control modules, which include optical signals, which refers to signals that are received, and the functions in progress.
_unit for receiving digital input, installed in electric panels (unit at the terrain), connected to the PLC via Bus lines, Modbus or Profibus, will have to serve as electrical isolation (galvanic separation) between the low-voltage maintained apparatus and the lowest voltage within the control module, which contain optical signalization, which refers to signals that are received, and the functions in progress.
_peripheral units for management and automation of operating island (PLC) that are installed with various electric command panles, consist of:
* power supply units 230 V AC 50 Hz with transformer on 24 VDC;
* scheme processors with inputs of serial interface with a standard protocol Modbus or Profibus for connecting units at the terrain;
* network cards with protocol serial port RS485 Modbus or Profibus for connection to a PC for supervision;
terminal module with terminal setup and power supply modules interface and for connecting to the control modules, have the following features:
* plastic holder for snap installation on guide DIN with a mesh insulating plates (stripboard) with the runway for the power supply and data transmission terminals for power supply, fuses, broadband cable connector for connection to the control module, connector screw for connection of interfaces is not the spaces provided
* voltage and frequence of power supply: 24V AC, +15/-10% - 50Hz;
* insulation level: class II;
* protection level: min. IP20.
_bus line protected with 4 conductors section 24 AWG, the serial connection of different elements that make up the system;
_router for conversion of serial line to network TCP/IP for communication with supervisor computer, with patch cord in cat.6A;
_dress package through conductors, accessories and smallparts;
_programming and techical system check;
LIGHTING CONTROL SYSTEM
Consists of the following parts:
_POWER SUPPLY OF BUS LINES suitable for installation on supporter DIN 35mm (inside the electrical panels) output voltage 640mA;
_THE JOINTS BETWEEN MAIN AND SECONDARY BUS LINE with galvanic separation thereof, suitable for installation on DIN 35mm (inside the electrical panels), suitable for data transmission of bus telegrams from one curcuit to another, and vice versa (potential short circuits on the secondary bus lines have been discovered and there is no transmission); ;
_MODULE FOR MANAGEMENT OF ELECTRONIC REACTOR, SILENCERS AND STEERABLE (DALI) with the following characteristics:
* line management, each with 64 reactors/electrical transformes DALI, which can be split into 16 independent illuminotechnical conditions;
* darkening 1÷100%;
* possibility of failure signalization in the system;
* command cables of changing polarities;
* connecting using clamps with screws;
* protection level min: IP20, dim: 40 x 30 x 270L mm.
* interface EIB/KNX;
MODULES INPUT MODELS WITH KEYS suitable for installation inside the box 503 with the following characteristics:
* 4 entrances separated from keys ;
*depending on the direction of the module, you can manage all the terminals of a system: Briefly pressing the appropriate button switches from one state to another (state "Missing" and state "Present"). A long press on the button increases or decreases shading of complete lighting or a group;
* cable long 5m prefabricated,for connecting module and key;
*protection level min: IP20, dim: 40 x 40 x 17 p mm.
DIGITAL OUTPUT MODULE WITH 4 POTENTIAL-FREE CONTACTS
has following characteristics:
*output relay with contacts for controlling and the independent directing for switching of electrical installations with voltage network up to 230/240V;
* conductivity of contacts: 10A u AC1;
*connecting with clamps with screws;
* test key, LED for signalisation;
*installation into electrical box on DIN carrier 35 mm;
* protection level min: IP20, dim: 3 moduls.
PRESENCE OF LIGHT SENSOR (included in the BoQ Books (Book) 4 "high voltage") for inclusion of internal illumination system or control of the level of illumination as a function of contributions to natural light, with the following characteristics:
* installation in a prominent place on the ceiling or on the wooden beam by using particular carrier (the last one is included);
* auto power off function;
*the presence indicator is integrated with a time delay compared to the shutdown between 30 seconds and 20 minutes;
presence of indicator zone: dimensions around 4,0x4,0 m (when people are sitting) ili 6,0x6,0 m (people are moving) za Hinst=2,5m; dim. oko 4,5x4,5 m (people are sitting) ili 7,0x7,0 m (preople are moving)for Hinst=3,0m;
*indication field of illumination value: od 6 do 1.600 [lx];
* angle of sensor viewing around 120° (vertical); 360° (horizontal);
*protection level: IP20, dim. Oko 100x100x55 h mm.
router to convert a serial line EIB / KNX in the network ethernet TCP / IP to communicate with a computer for monitoring, which consists of di patch cord in cat. 6A;
bus network EIB/KNX implemented with certified cables;
bus network DALI implemented with certified cables;
INTERFACE DEVICES FOR LOW VOLTAGE INSTALLATIONS
Consists of:
BACNet over IP communication for fire detection, gas and against burglary, which enable translation of serial line that comes from the individual switchboards in network LAN Ethernet with protocole TCP / IP; will also be equipped with a driver that will enable translation within the central database with the data obtained by the computer supervisor;
interface switchboard sound system using digital contacts at the entrance to the switchboard for fire detection;
interface access control system using the database within the computer for control that is dedicated to access control system;
Interface CCTV camera system using a digital contacts on the door alarm system on the entrance of the antiburglar system.
CONTROL POINT FOR ELECTRICAL INSTALLATIONS OF HIGH VOLTAGE
Consists of:
a control units for the control with the schemes in the area of ​​the ports sufficient to manage controlled points , which are required for the control of a specific apparatus or an electrical frame;
bus line;
electric voltage of control apparatus;
part of the quota computer for supervision;
graphic station for review of controlled points;
licence.
CONTROL POINT OF LIGHTING DEVICES
Consists of:
_ regulation units installed in electric panels for BUS DALI and EIB/KNX;
_ units for management at the terrain for procurement of keys and presence and lighting indicators;
_ router;
_ bus DALI i EIB/KNX;
_ electric power supply of command devices;
_ part of the quota computer for supervision;;
_ graphic for mapping of configured system and systems for control of lighting and technical configurations;
_ licence.
CONTROL POINT OF SPECIAL DEVICES
Consists of:
_ interface router switchboard with supervisor;
_ part of the quota computer for supervision;
_ graphic for mapping controlled devices and for status visualization of status/alarm;
_ licence.
Control points are specificially indicated in appropriate paragraph Address Points
BMS input/output address point for safety systems
| GROUND FLOOR LEVEL - BMS SYSTEM |  | 1
| FIRST FLOOR LEVEL - BMS SYSTEM |  | 1
| SECOND FLOOR LEVEL - BMS SYSTEM |  | 1
| GROUND FLOOR LEVEL - BMS SYSTEM |  | 1
| Total amount |  | 1
TOTAL 16 - SUPERVISION, ACCESS CONTROLL AND TVCC
TOTAL SPECIAL PLANTS - GROUND FLOOR AND UPPER FLOOR LEVELS
TOTAL SPECIAL PLANTS