## THERMOTECH
NOTE | PRICES TO BE INSERTED MUST BE WITHOUT V.A.T.
B.1. | THERMOTECHNICAL INSTALLATIONS
Notes:
If on some position material or equipment manufacturer is indicated, teneder can instal other materials or equiment if with same or equivalent caracteristics in line with project documentation. All materials and equipment to be used in construction must be authorised by the Investor.
All related preparaory works, finishings, cleanings, correction, testing of materials, instalations, equipment, providing of atests or similar would not be quoted or payed separately. All pricess are to be incorporated in positions of the BoQ of this Volume. For execution of all positions all relevant materials, tools, movements, connections, organisations, worksman, insurance and other related, are suposed to be included in order to execute works in defined conditions, finalisation with indicated guarantee periods - everything ready for technical taking over.
Code | Description | Unit | Quantity | Unit price | Total
01 | THERMAL TECHNOLOGY - CENTRAL PLANT
TB | PIPES
TB.110.A3 | PIPES FROM THE BLACK DRAGGED STEEL | kg
PIPES FROM THE BLACK DRAGGED STEEL compliance with standards : UNI EN 10255 average series for diameter in inch or in DN; UNI EN 10216-1/TR1 diameter in mm or DN (thickness at least from table 5 according to rules). Construction and installation characteristics: - pipeline from the black steel, type of dragged metal without welding (for pipes UNI EN 10255 average series assumed, at the same price, use of welding pipes Fretz-Moon) welds ; - conventional weight for the different diameters and typology for installed pipes which are in use for different installations, installed according to rule, specified with specifications and/or designed technical conditions; - for calculation will be used values of the linear density, depending of the pipeline type and diameter which is in use, specified in the respective tables UNI EN.
The price includes : - painting of the two coats with anti-rust paint in different colors, however, at the same price, overpainting of fabric color with epoxy resin, in both cases are included over painting on each joints- where is necessary, for underground pipes, as a replacement for the coating to prevent rust : coating of insulating polyethylene, with repetition at all joints. – waste and scrap; - Special chipping, accessories and all the fixed points; - Substrates, supports, anchor; - Various supplies.
Black steel pipes in the central plant
| Central plant – air conditioning |  | 2050
| Total amount |  | 2050
TB.130.A1 | COMPACT STAINLESS STEEL PIPES | kg
COMPACT STAINLESS STEEL PIPES : compliance with standard UNI EN ISO 1127 Construction and installation characteristics: - steel pipes from austenitic stainless steel type AISI 304 (ASTMTP304) and/or AISI 316 (ASTMTP316), compact and calibrated (outer crimp), spherical and empty. Connections with welding in the electric arc with austenitic steel; are assumed when they are necessary and/or predicted, connection parts with flanged ends - conventional weight for the different diameters and typology for installed pipes which are in use for different installations, specified in the C.S.A. and/or other design technical works. Price include : waste and scrap; - Equipment, special pieces; - Bonds and strongholds; - Various consumables
Pipes from the stainless steel according to AISI 304
| Central plant – air conditioning |  | 490
| Total amount |  | 490
TB.222.B10 | PIPES FROM THE HIGH DENSITY POLYETHYLENE (PEAD) FOR THE FLUID UNDER THE PRESSURE | m
PIPES FROM THE HIGH DENSITY POLYETHYLENE (PEAD) FOR THE FLUID UNDER THE PRESSURE compliance with standards: UNI EN 12201-5:2004; UNI EN 1555:2004 (flammable fluid). Construction and installation characteristics: - pipes PEVG (polyethylene high density), with high resistance on the impact, on freezing ,on chemical reaction, etc. and suitable for the distribution of fluids under pressure, even in the type of power supply. Pipe fittings for fitting to DN100; weld (polyfusion) for the above DN. In the case that the request and / or set, the pipe will be of the type: - PE80 or PE100, PN6, 3 (SDR26), PN10 (SDR17) or PN 16 (SDR11); - PE80 (series S5 to de 75 mm and S8 series of de up to 75 mm) according to the standard UNI EN 1555:2004 distribution of flammable fuels. Typology of used equipment is specified with Specification. Price include: waste and scrap; - Equipment, special pieces; - Bonds and strongholds; - Various consumables
Polyethylene pipes PN16, PeHD, diameter 125mm
| Central plant – air conditioning |  | 15
| Total amount |  | 15
TOTAL PIPELINES
TC | VALVES AND PIPES COMPONENTS
TC.110.A5 | BALL VALVE FROM BRASS , WITH THREAD,PN16 | piece
BALL VALVE FROM BRASS , WITH THREAD,PN16 in accordance with : UNIT EN 1074; UNI 8858 Construction and installation characteristics: Two-way or three-way valve (according to what is required or as needed) with brass body POT 58Pb nickel or chrome and stainless steel ball- AISI 304; with total open, which have control spring mounted on the inner side of the body with double sealing (2 o-ring Viton and joints from PTFE), handle in the lever maneuver or butterfly, plastic coated metal (with connection on extension, included in the price when it comes to insulated pipes) and connection with thread ; for use in the round of cold or chilled water, potable water, fire alarm installation and gas / air network; - Supply the version with hose, connectors male / female species or open thread, where appropriate; The operating parameters: - Maximum temperature: 110 ° C - nominal working pressure: PN16. Price includes: - pipe fittings, connectors, accessories; - Various supplies.
ball valves, diameter 1"
| Central plant – air conditioning |  | 9
| Total amount |  | 9
TC.110.A8 | BALL VALVE FROM BRASS ,WITH THREAD PN16 | piece
BALL VALVE FROM BRASS, WITH THREAD PN16 in accordance with: UNI EN 1074; UNI 8858 Construction and installation characteristics: Two-way or three-way valve (according to what is required or what is needed) with brass body POT 58Pb nickel or chrome and stainless steel ball- AISI 304; with total open, which have control spring mounted on the inner side of the body with double sealing (2 o-ring Viton and joints from PTFE), handle in the lever maneuver or butterfly, plastic coated metal (with connection on extension, included in the price when it comes to insulated pipes) and connection with thread ; for use in the round of cold or chilled water, potable water, fire alarm installation and gas / air network; - Supply the version with hose, connectors male / female species or open thread, where appropriate; The operating parameters: - Maximum temperature: 110 ° C - nominal working pressure: PN16. Price includes: - pipe fittings, connectors, accessories; - Various supplies.
ball valves, diameter 2"
| Central plant – air conditioning |  | 4
| Total amount |  | 4
TC.130.A10 | BUTTERFLY VALVE FROM THE CAST IRON FLANGE PN 16 | piece
BUTTERFLY VALVE FROM THE CAST IRON FLANGE PN 16 Construction and installation characteristics: butterfly valve with body from cast iron spherical shape GG40, inside lined with EPDM rubber and preformed resilient rings with: round holes with threaded screws fixed to the middle, in the same number as a number of open holes in the flange joints in pipes, or round central hole (type wafer) fixing the clamp and screws ; installed to provide , when the valve is closed, disassembling the pipe and/or intercept components either forward or backward; axle and disc-type lens cap stainless steel or cast iron GG40 spheroidal shape, coated materials unpulsing ; -leverage solid-resistant material and perforated appropriately for the application lock on the key with the seal covered the price when it comes to butterfly valve for fire protection installations; - Locking device and / or pre-positioning (for diameters larger than DN200 lighted wheel with gear)
In the case of drinking water usage , the valve shall be supplied with epoxy with appropriate internal processing in accordance with the regulations. In the case of the fire installations usage, all locks must have the same key. In the case of flammable gases usage, butterfly valve shall be of the type described above, except that sealing has to be the seal of the nitrile. The operating parameters: - Maximum operating temperature: 120 ° C - nominal working pressure: 16 bar. Price includes: - fittings, flanges and screws opposite; - Various supplies.
Butterfly valve DN80
| Central plant – air conditioning |  | 18
| Total amount |  | 18
TC.130.A11 | BUTTERFLY VALVE FROM THE CAST IRON FLANGE PN 16 | piece
BUTTERFLY VALVE FROM THE CAST IRON FLANGE PN 16 Construction and installation characteristics: butterfly valve with body from cast iron spherical shape GG40, inside lined with EPDM rubber and preformed resilient rings with: round holes with threaded screws fixed to the middle, in the same number as a number of open holes in the flange joints in pipes, or round central hole (type wafer) fixing the clamp and screws ; installed to provide , when the valve is closed, disassembling the pipe and/or intercept components either forward or backward; axle and disc-type lens cap stainless steel or cast iron GG40 spheroidal shape, coated materials unpulsing ; -leverage solid-resistant material and perforated appropriately for the application lock on the key with the seal covered the price when it comes to butterfly valve for fire protection installations; - Locking device and / or pre-positioning (for diameters larger than DN200 lighted wheel with gear). In the case of drinking water usage , the valve shall be supplied with epoxy with appropriate internal processing in accordance with the regulations. In the case of the fire installations usage, all locks must have the same key. In the case of flammable gases usage, butterfly valve shall be of the type described above, except that sealing has to be the seal of the nitrile. The operating parameters: - Maximum operating temperature: 120 ° C - nominal working pressure: 16 bar. Price includes: - fittings, flanges and screws opposite; - Various supplies.
Butterfly valve DN100
| Central plant – air conditioning |  | 7
| Total amount |  | 7
TC.130.A12 | BUTTERFLY VALVE FROM THE CAST IRON FLANGE PN 16 | piece
BUTTERFLY VALVE FROM THE CAST IRON FLANGE PN 16Construction and installation characteristics: butterfly valve with body from cast iron spherical shape GG40, inside lined with EPDM rubber and preformed resilient rings with: round holes with threaded screws fixed to the middle, in the same number as a number of open holes in the flange joints in pipes, or round central hole (type wafer) fixing the clamp and screws ; installed to provide , when the valve is closed, disassembling the pipe and/or intercept components either forward or backward; axle and disc-type lens cap stainless steel or cast iron GG40 spherical shape, coated materials unpulsing ; -leverage solid-resistant material and perforated appropriately for the application lock on the key with the seal covered the price when it comes to butterfly valve for fire protection installations; - Locking device and / or pre-positioning (for diameters larger than DN200 lighted wheel with gear)
In the case of drinking water usage , the valve shall be supplied with epoxy with appropriate internal processing in accordance with the regulations. In the case of the fire installations usage, all locks must have the same key. In the case of flammable gases usage, butterfly valve shall be of the type described above, except that sealing has to be the seal of the nitrile. The operating parameters: - Maximum operating temperature: 120 ° C - nominal working pressure: 16 bar. Price includes: - fittings, flanges and screws opposite; - Various supplies.
Butterfly valve DN125
| Central plant – air conditioning |  | 37
| Total amount |  | 37
TC.130.A13 | BUTTERFLY VALVE FROM THE CAST IRON FLANGE PN 16 | piece
BUTTERFLY VALVE FROM THE CAST IRON FLANGE PN 16Construction and installation characteristics: butterfly valve with body from cast iron spherical shape GG40, inside lined with EPDM rubber and preformed resilient rings with: round holes with threaded screws fixed to the middle, in the same number as a number of open holes in the flange joints in pipes, or round central hole (type wafer) fixing the clamp and screws ; installed to provide , when the valve is closed, disassembling the pipe and/or intercept components either forward or backward; axle and disc-type lens cap stainless steel or cast iron GG40 spherical shape, coated materials unpulsing ; -leverage solid-resistant material and perforated appropriately for the application lock on the key with the seal covered the price when it comes to butterfly valve for fire protection installations; - Locking device and / or pre-positioning (for diameters larger than DN200 lighted wheel with gear)
In the case of drinking water usage , the valve shall be supplied with epoxy with appropriate internal processing in accordance with the regulations. In the case of the fire installations usage, all locks must have the same key. In the case of flammable gases usage, butterfly valve shall be of the type described above, except that sealing has to be the seal of the nitrile. The operating parameters: - Maximum operating temperature: 120 ° C - nominal working pressure: 16 bar. Price includes: - fittings, flanges and screws opposite; - Various supplies.
Butterfly valve DN150
| Central plant – air conditioning |  | 5
| Total amount |  | 5
TC.130.A9 | BUTTERFLY VALVE FROM THE CAST IRON FLANGE PN 16 | piece
BUTTERFLY VALVE FROM THE CAST IRON FLANGE PN 16Construction and installation characteristics: butterfly valve with body from cast iron spherical shape GG40, inside lined with EPDM rubber and preformed resilient rings with: round holes with threaded screws fixed to the middle, in the same number as a number of open holes in the flange joints in pipes, or round central hole (type wafer) fixing the clamp and screws ; installed to provide , when the valve is closed, disassembling the pipe and/or intercept components either forward or backward; axle and disc-type lens cap stainless steel or cast iron GG40 spherical shape, coated materials unpulsing ; -leverage solid-resistant material and perforated appropriately for the application lock on the key with the seal covered the price when it comes to butterfly valve for fire protection installations; - Locking device and / or pre-positioning (for diameters larger than DN200 lighted wheel with gear)
In the case of drinking water usage , the valve shall be supplied with epoxy with appropriate internal processing in accordance with the regulations. In the case of the fire installations usage, all locks must have the same key. In the case of flammable gases usage, butterfly valve shall be of the type described above, except that sealing has to be the seal of the nitrile. The operating parameters: - Maximum operating temperature: 120 ° C - nominal working pressure: 16 bar. Price includes: - fittings, flanges and screws opposite; - Various supplies.
Butterfly valve DN65
| Central plant – air conditioning |  | 12
| Total amount |  | 12
TC.140.A12 | FLAT INTERRUPTED VALVE FROM THE CAST IRON WITH FLANGES PN 16 | piece
FLAT INTERRUPTED VALVE FROM THE CAST IRON WITH FLANGES PN 16 Regulatory compliance:UNI 1284 Construction and installation characteristics: Valve with flow-running "liberated maintenance", body and lid from the gray cast iron GG25; performance rights or under the angle at the same price; rod and cap made of stainless steel (acceptance and closure of carbon steel with sealing surfaces of stainless steel); - seat in stainless steel sealing rings; - gaskets made of pure graphite without asbestos; - device with a seal in the outside direction with bellows from the stainless steel with more protective seals; - hand wheel from the cast iron with an indicator of openness . It is used for the installation for heating, cooling, steam. If it is required or needed: work under the angle without increasing prices. The operating parameters: - Maximum temperature: 300 ° C - nominal operating pressure: 16 bar. Price includes accessories, opposing flanges and screws; - Various supplies.
Flat interrupted valve , DN125
| Central plant – air conditioning |  | 3
| Total amount |  | 3
TC.143.A12 | FLAT INTERRUPTED VALVE FROM THE STAINLESS STEEL WITH FLANGES PN 16 | piece
FLAT INTERRUPTED VALVE FROM THE CAST IRON WITH FLANGES PN 16 Regulatory compliance:UNI 1284 Construction and installation characteristics: Valve with flow-running "liberated maintenance", body and lid from the stainless steel AISI 316; performance rights or under the angle at the same price; - rod and cap made of stainless steel AISI 316; - seat in stainless steel sealing rings; - gaskets made of pure graphite without asbestos; - device with a seal in the outside direction with bellows from the stainless steel with more protective seals; - hand wheel form the cast iron with an indicator of openness. It is used for steam plant, chilled water, thermal oil, corrosive liquids, demineralized water, and so on. It is used for the installation of heating, cooling, steam. If it is required or needed: work under the angle without increasing prices. The operating parameters: - Maximum temperature: 400 ° C - nominal operating pressure: 16 bar. Price includes accessories, opposing flanges and screws from the cast iron AISI 316; - Various supplies.
Flat interrupted valve , DN125
| Central plant – air conditioning |  | 3
| Total amount |  | 3
TC.143.A13 | FLAT INTERRUPTED VALVE FROM THE STAINLESS STEEL 316 FLANGED PN 16 | piece
FLAT INTERRUPTED VALVE FROM THE CAST IRON WITH FLANGES PN 16 Regulatory compliance:UNI 1284 Construction and installation characteristics: Valve with flow-running "liberated maintenance", body and lid from the stainless steel AISI 316; performance rights or under the angle at the same price; - rod and cap made of stainless steel AISI 316; - seat in stainless steel sealing rings; - gaskets made of pure graphite without asbestos; - device with a seal in the outside direction with bellows from the stainless steel with more protective seals; - hand wheel form the cast iron with an indicator of openness. It is used for steam plant, chilled water, thermal oil, corrosive liquids, demineralized water, and so on. It is used for the installation of heating, cooling, steam. If it is required or needed: work under the angle without increasing prices. The operating parameters: - Maximum temperature: 400 ° C - nominal operating pressure: 16 bar. Price includes accessories, opposing flanges and screws from the cast iron AISI 316; - Various supplies.
Flat interrupted valve , DN150
| Central plant – air conditioning |  | 3
| Total amount |  | 3
TC.320.A5 | IRREVERSIBLE VALVE WITH DISC MADE OF BRASS, WITH THREAD PN 16 | piece
IRREVERSIBLE VALVE WITH DISC MADE OF BRASS, WITH THREAD PN 16 Construction and installation characteristics: The body of the irreversible valve is from the brass, disc zipper is from the austenitic steel or stainless with stainless steel spring fittings threaded to standard; generally used for each types of the hydraulic installation, of heating systems, pneumatic, etc.. The operating parameters: - Maximum operating temperature: 200 ° C - nominal working pressure: 16 bar. The price includes: - fittings - miscellaneous supplies.
Irreversible valve, 1"
| Central plant – air conditioning |  | 3
| Total amount |  | 3
TC.321.A11 | IRREVERSIBLE VALVE WITH DISCS FROM THE BRASS / CAST IRON, EXTRA STRAIGHT (BETWEEN FLANGES), PN 16 | piece
IRREVERSIBLE VALVE WITH DISCS FROM THE BRASS / CAST IRON, EXTRA STRAIGHT (BETWEEN FLANGES), PN 16 Construction and installation characteristics: Body of the irreversible valve is from the brass/bronze for the diameters to DN100 and from the cast iron for the larger diameters, disc zipper is from the austenitic steel or stainless with stainless steel spring, or the zipper from the cast iron for larger diameters than DN200; the performance of the extra flat between the fixing flange (wafer) with a centering ring; used generally for any type of hydraulic installation: liquid, gas, vapor, etc..; The operating parameters: - Maximum operating temperature: 200 ° C - nominal working pressure: 16 bar. Price includes: - the equipment, the opposing flanges and screws; - Various supplies.
Irreversible valve, DN 100
| Central plant – air conditioning |  | 2
| Total amount |  | 2
TC.321.A12 | IRREVERSIBLE VALVE WITH DISCS FROM THE BRASS / CAST IRON, EXTRA STRAIGHT (BETWEEN FLANGES), PN 16 | piece
IRREVERSIBLE VALVE WITH DISCS FROM THE BRASS / CAST IRON, EXTRA STRAIGHT (BETWEEN FLANGES), PN 16 Construction and installation characteristics: Body of the irreversible valve is from the brass/bronze for the diameters to DN100 and from the cast iron for the larger diameters, disc zipper is from the austenitic steel or stainless with stainless steel spring, or the zipper from the cast iron for larger diameters than DN200; the performance of the extra flat between the fixing flange (wafer) with a centering ring; used generally for any type of hydraulic installation: liquid, gas, vapor, etc..; The operating parameters: - Maximum operating temperature: 200 ° C - nominal working pressure: 16 bar. Price includes: - the equipment, the opposing flanges and screws; - Various supplies.
Irreversible valve, DN 125
| Central plant – air conditioning |  | 4
| Total amount |  | 4
TC.321.A9 | IRREVERSIBLE VALVE WITH DISCS FROM THE BRASS / CAST IRON, EXTRA STRAIGHT (BETWEEN FLANGES), PN 16 | piece
IRREVERSIBLE VALVE WITH DISCS FROM THE BRASS / CAST IRON, EXTRA STRAIGHT (BETWEEN FLANGES), PN 16 Construction and installation characteristics: Body of the irreversible valve is from the brass/bronze for the diameters to DN100 and from the cast iron for the larger diameters, disc zipper is from the austenitic steel or stainless with stainless steel spring, or the zipper from the cast iron for larger diameters than DN200; the performance of the extra flat between the fixing flange (wafer) with a centering ring; used generally for any type of hydraulic installation: liquid, gas, vapor, etc..; The operating parameters: - Maximum operating temperature: 200 ° C - nominal working pressure: 16 bar. Price includes: - the equipment, the opposing flanges and screws; - Various supplies.
Irreversible valve, DN 65
| Central plant – air conditioning |  | 4
| Total amount |  | 4
TC.330.A12 | IRREVERSIBLE VALVE MADE FROM THE CAST IRON, WITH BALL, FLANGES PN 10 | piece
IRREVERSIBLE VALVE MADE FROM THE CAST IRON, WITH BALL, FLANGES PN 10 Construction and installation characteristics: body of the irreversible valve is from the cast iron GG40 coated or epoxy coated with hollow seat and seals for the ball from the light alloy coated with rubber. The interior walls are smooth and provide a safe and completely free flow and on that way ball is free to move into place. Performing with screw flanges according to rule is exempt from maintenance; generally used for each type of hydraulic installation. Characteristics of operation: Maximum operating temperature: 85 ° C - nominal working pressure of 10 bar. Price includes: - the equipment, the opposing flanges and bolts: - various supplies.
Irreversible valve with ball , DN 125
| Central plant – air conditioning |  | 3
| Total amount |  | 3
TC.410.A4 | SAFETY VALVE WITH CONE FOR WATER | piece
SAFETY VALVE WITH CONE FOR WATER Regulatory compliance: I.S.P.E.S.L. Construction and installation characteristics: Safety valve have body and place from the brass, with cone from the synthetic material and spring from the stainless steel; valve of fixed calibration; confirmed qualification certificate ISPESL, with manual control of the jagged wheel of the plastic material and the possibility of removing the cover, without modifying the value of calibration. Characteristics of operation: maximum operating temperature of 110 ° C. Price includes: - equipment - various supplies.
Safety valve , diameter 3/4" x 1"
| Central plant – air conditioning |  | 3
| Total amount |  | 3
TC.620.A12 | FILTER COLLECTOR IMPURITIES AS "Y" IN CAST IRON, PN 16 | piece
FILTER COLLECTOR IMPURITIES AS "Y" IN CAST IRON, PN 16 Construction and installation characteristics. Angle filter in the form of a "Y" with the body and lid made of cast iron, filtering basket and net ejection of stainless steel. Construction of the connector with flanges by default; suitable for water (cold, warm, chilled, vapor), oil and similar liquids. Characteristics of operation: Maximum operating temperature: 300 ° C - nominal working pressure of 16 bar. Price includes: - the equipment, the opposing flanges and screws; - Various supplies.
Traps, DN125
| Central plant – air conditioning |  | 1
| Total amount |  | 1
TC.620.A13 | FILTER COLLECTOR IMPURITIES AS "Y" IN CAST IRON, PN 16 | piece
FILTER COLLECTOR IMPURITIES AS "Y" IN CAST IRON, PN 16
FILTER COLLECTOR IMPURITIES AS "Y" IN CAST IRON, PN 16 Construction and installation characteristics. Angle filter in the form of a "Y" with the body and lid made of cast iron, filtering basket and net ejection of stainless steel. Construction of the connector with flanges by default; suitable for water (cold, warm, chilled, vapor), oil and similar liquids. Characteristics of operation: Maximum operating temperature: 300 ° C - nominal working pressure of 16 bar. Price includes: - the equipment, the opposing flanges and screws; - Various supplies.
| Traps, DN150 |  | 1
| Total amount |  | 1
TOTAL VALVES AND PIPE COMPONENTS
TD | DEVICES FOR AIR DISTRIBUTION AND DIFFUSION
TD.110.A1 | METAL RECTANGULAR AIR PIPES | kg
METAL RECTANGULAR AIR PIPES Regulatory compliance: UNI EN 1505:2000; UNI EN 12236:2003; UNI EN 10327:2004; UNI EN 12237:2004; UNI EN 12097:2007. Construction and installation characteristics: air network made up of: - rectangular metal pipes, performed depending on how much was requested or required, from the galvanized steel panels (UNI EN 10327:2004 Sendzimir Z 275), or from stainless steel, or from aluminum; - Seal with flanged or bayonet-seal depending of the size and complete inspection door, devices for calibration (perforated plate or inspection doors), sensors, fins for air and whatever else is necessary and provided. Typology of used equipment , thickness, etc., are indicated in the specifications. Technical features: the sealing class "B" (which includes the seal of the all connections, either the longitudinal or between different transmitters) according to UNI EN 12237:2004; level of purity (UNI EN 12097:2007): Medium. The price included: waste and scrap; - Equipment and special pieces; holders and different bonding; - Various supplies.
Rectangular channels from galvanized sheet
| Central plant – air conditioning |  | 200
| Total amount |  | 200
TD.520.B4 | RECTANGULAR AIR FLOW REGULATOR | piece
RECTANGULAR AIR FLOW REGULATOR Construction and installation characteristics: zipper for calibration or retention of air comprising: a robust molded frame from galvanized steel or from aluminum insulation (depending on the material of the channel, which is loaded), a square or rectangular cross-section; - A profiled horizontal blades , the opposite movement, made of galvanized steel or aluminum, and placed on the shaft from the galvanized steel with the bearings from plastic material resistant to the maximum temperature of 100 ° C, the opening from the brass or bronze; - A system of gears and / or throttle control (internal or external) , for blades moving , made of galvanized steel or high resistance plastic material, with manual control along with handle for positioning, locking device and a visible sign of the position Open and Close.
Where necessary and / or the following: - an airtight seal for sealing the longitudinal profiles on the blades made of plastic material which is resistant to high temperatures and the angular discs made of plastic, for high-temperature strength and activity of the antibacterial substances; - Hermetic sealing closure according to Regulation DIN 1946 part IV; electric servomotor (on the place of manual controls), full of limit and device for blocking for hand-operated mechanism. Type of installation that is applied is that described in the CSA. The most widespread is the usage of air conditioning and ventilation systems,for retention or control the flow of the air pressure. Price includes: - equipment - supports and various fasteners; - Connecting with pipes and measuring the flow rate and / or anticipated pressure; - Various supplies
Automatic damper, galvanized steel, with dimensions of 12.1 to 16 dm2
| Central plant – air conditioning |  | 1
| Total amount |  | 1
TD.610.A10 | RECTANGULAR SILENCER | piece
RECTANGULAR SILENCER Regulatory compliance: - Reaction on the fire (DIN 4102 A2) certification in the class 0-1. Construction and installation features: acoustic regulator straight-through type with compartments, made of: - robust layer for suppression of rectangular cross-section in the panel made of galvanized steel, with a minimum thickness from 1mm scheduled for end flanges that connect two ends with channel node; - A series of acoustic barrier, in the variable number, placed along, implemented with perimeter edge in the galavanized board and from muffled addition from mineral wool with a density of not less than 40 kg/m3, which is protected from the outside of the coating peeling of glass wool which is resistant to air velocity of 20 m / s, is impregnated against moisture and rot, and further protected by a membrane made ​​of plastic polymer (clean flow); compartments will have a thickness of 100mm and interface from the100mm edge drains and air supply will be form curved galvanized steel.
Half of each compartment will be coated with galvanized steel thickness of 0.5 mm, with the function of absorption at low frequencies and the other half with galvanized or galvanized plating a dense network. Technical features: - maximum operating temperature of 100 ° C; - A minimum of acoustic attenuation, very little acoustic attenuation, the frequency of the octave (Hz) 63,125,250,500 1K 2K 4K 8K (dB) 5 8 13 15 18 18 14 12 L = 1000 mm (dB) 7 12 16 28 27 27 22 18 L = 1500 mm (dB) 9 15 22 28 34 34 26 22 L = 2000 mm. Such effects can be shown to the pressure drop, which is measured by the flow of the working, which is not higher than 30 Pa, and should be understood as a minimum requirement. In order to calculate the pressure loss within the limit of 30 Pa, the dimensions of the silencer should be generally improved in comparison to the dimensions of the pipeline, which is set up. Acoustic properties of the regeneration control, and, in any case, must be adapted to the limitation of the noise caused by the environment, under the conditions CSA.
Price includes: - equipment; - Connecting pipes; - Tuning - technical files inside the site; - Various supplies.
Rectangular silencer, 1000 mm in length, from 40.1 to 50 dm2
| Central plant - ventilation |  | 2
| Total amount |  | 2
TOTAL DEVICES FOR AIR DISTRIBUTION AND DIFFUSION
TE | SYSTEM OF REGULATION
TE.340.A1 |  | piece
UNIVERSAL THERMOSTAT WITH TWO POSITIONS
Construction and installation characteristics
Thermostat with services devices which are present in the hydrothermal installations and air conditioning units, for the purpose of control the ambient temperature. It will be universal type, suitable for installation on the wall or on the devices (if it is applicable), whose base consists of:
element sensitive on the vapor pressure or bi-metal, with resistance to counter-reaction in the heating mode
Regulation button for set-point with an appropriate scale
Two control outputs ON / OFF, which are separated, with the removal of the contact
Closure box from the strong plastic material
Technical characteristics
Rated insulation voltage: 230V(+/-10%)-50Hz
Rated uninterrupted current 10 A;
Degree of protection: not less than IP30;
working field: from +5 to +35 °C
intervention differential : not more than 0.5 ° C.
Price includes :
Equipment for completion and fixing;
electrical connection with the propulsion equipment in the installation
miscellaneous supplies.
room thermostat
| Central plant - ventilation |  | 2
| Total amount |  | 2
TE.700.A3 |  | piece
ELECTRICAL INSTALLATIONS MADE OF COMMAND TABLE AND ELECTRICAL LINES FOR ALL NECESSARY USAGE
Construction and installation characteristics
electrical command table for users of thermo mechanical installation, implemented and ended by demanded and / or predicted in reports and specifications of the project and which include connections for incoming power supply on the command table;
lines from the command table to all necessary users, which include conductive tubes, pipes and channels and all necessary small goods to complete the installation and proper operation;
switch-disconnector of safety valve for all user service
connection of the all user services at the appropriate lines from the command table.
Method of installing a specified with particular specification.
Electric board for mechanical installation H_LV_SB
| Central plant – air conditioning |  | 1
| Total amount |  | 1
TE.700.A5 |  | piece
ELECTRICAL INSTALLATIONS MADE OF COMMAND TABLE AND ELECTRICAL LINES FOR ALL NECESSARY USAGE
Construction and installation characteristics
electrical command table for users of thermo mechanical installation, implemented and ended by demanded and / or predicted in reports and specifications of the project and which include connections for incoming power supply on the command table;
lines from the command table to all necessary users, which include conductive tubes, pipes and channels and all necessary small goods to complete the installation and proper operation;
switch-disconnector of safety valve for all user service
connection of the all user services at the appropriate lines from the command table.
Method of installing a specified with particular specification.
Electric board for mechanical installation, EB_GWP
| Central plant – air conditioning |  | 1
| Total amount |  | 1
TE.710.A3 |  | piece
MONITORING SYSTEM DDC
BMS system of control-automation with Directly Digital Control (DDC), without a central unit of monitoring (workstation) - peripheral sub-DDK ... in service ... made and finished as the specifications and other elaborates the project, which basically includes:
peripheral sub-DDK ,which is located in the appropriate section of electrical comand table, made of CPU units, power form, module of input-otput, access terminal
lines for connection from the substation to the all the elements in the field or on the command table
elements in the field or on the command table, such as probes, sensors, relays, transmitters, etc.., with the exception of the servo valves and actuator lock, where the predicted and calculated seperately
part of the lines quota for connection to other peripheral
- engineering, start-up;
instruction for personnel and everything what is necessary to make the system complete and how to function in a professional manner.
The control system of air conditioning, DDC3 (H_LV_SB)
| Central plant – air conditioning |  | 1
| Total amount |  | 1
TE.710.A6 |  | piece
MONITORING SYSTEM DDC
BMS system of control-automation with Directly Digital Control (DDC), without a central unit of monitoring (workstation) - peripheral sub-DDK ... in service ... made and finished as the specifications and other elaborates the project, which basically includes:
peripheral sub-DDK ,which is located in the appropriate section of electrical comand table, made of CPU units, power form, module of input-otput, access terminal
lines for connection from the substation to the all the elements in the field or on the command table
elements in the field or on the command table, such as probes, sensors, relays, transmitters, etc.., with the exception of the servo valves and actuator lock, where the predicted and calculated seperately
part of the lines quota for connection to other peripheral
- engineering, start-up;
instruction for personnel and everything what is necessary to make the system complete and how to function in a professional manner.
The control system of air conditioning, DDC6 (UPS rooms)
| Central plant – air conditioning |  | 1
| Total amount |  | 1
TE.710.A7 |  | piece
MONITORING SYSTEM DDC
BMS system of control-automation with Directly Digital Control (DDC), without a central unit of monitoring (workstation) - peripheral sub-DDK ... in service ... made and finished as the specifications and other elaborates the project, which basically includes:
peripheral sub-DDK ,which is located in the appropriate section of electrical comand table, made of CPU units, power form, module of input-otput, access terminal
lines for connection from the substation to the all the elements in the field or on the command table
elements in the field or on the command table, such as probes, sensors, relays, transmitters, etc.., with the exception of the servo valves and actuator lock, where the predicted and calculated seperately
part of the lines quota for connection to other peripheral
- engineering, start-up;
instruction for personnel and everything what is necessary to make the system complete and how to function in a professional manner.
The control system of air conditioning,DDC7 (CED-1)
| Central plant – air conditioning |  | 1
| Total amount |  | 1
TE.710.A8 |  | piece
MONITORING SYSTEM DDC
BMS system of control-automation with Directly Digital Control (DDC), without a central unit of monitoring (workstation) - peripheral sub-DDK ... in service ... made and finished as the specifications and other elaborates the project, which basically includes:
peripheral sub-DDK ,which is located in the appropriate section of electrical comand table, made of CPU units, power form, module of input-otput, access terminal
lines for connection from the substation to the all the elements in the field or on the command table
elements in the field or on the command table, such as probes, sensors, relays, transmitters, etc.., with the exception of the servo valves and actuator lock, where the predicted and calculated seperately
part of the lines quota for connection to other peripheral
- engineering, start-up;
instruction for personnel and everything what is necessary to make the system complete and how to function in a professional manner.
The control system of air conditioning, DDC8 (EB_GWP)
| Central plant – air conditioning |  | 1
| Total amount |  | 1
TOTAL SYSTEM OF REGULATION
TM | HEAT EXCHANGERS
TM.120.A1 | PLATE HEAT EXCHANGER WITH SCREWS FROM STAINLESS STEEL | piece
PLATE HEAT EXCHANGER WITH SCREWS FROM STAINLESS STEEL compliance with standards: UNI EN 307; Instruction PED 97/23/CE; I.S.P.E.S.L..Construction and installation characteristics: Plate heat exchanger, which is essentially made of:: -piles of printed plates made of stainless steel AISI 304 or 306, depending of required and / or specified quantities, which are provided with openings for the passage of two different fluids which change heat and passage same fluids, obtained by cleavage patterns in the form of fish bones on the board. The thickness of each panel will be less than 5/10 mm; - Two heads at the ends with bars for mounting printed plates, one of head is fixed and other mobile(plate for pressure), made from carbonic steel with a thickness of not less than 20 mm, which have connections with flanges or charges (as appropriate), and colored from outside with epoxy paint resistant to high temperatures;
Plates and heads will be connected between themselves with connections made of steel, with bolts on their heads, and closing of exchanger will be done with the help of butyl sealant, resistant to high temperature; - External thermal insulation, is derived from a mat from glass wool thickness not less than 60 mm (density not less than 30kg/m3) for the operation of the hot fluid, and the extended elastomeric, a thickness not less than 30 mm during the works with chilled water.
The ends in both cases will be with aluminum sheet minimum 10/10 mm. For delivery of exchangers must be provided: - special vehicles and / or support for mounting heads; - Plate with name, strongly anchored, reported all the features of exchanger (operating pressure, thermal power, flow, temperature and pressure drop of two liquids) Functional features: as indicated in the items. Price includes: - hydraulic connections; - Various consumable materials.
PLATE HEAT EXCHANGER WITH SCREWS FROM STAINLESS STEEL AISI 304, capacity 650 kW
| Central plant – air conditioning |  | 2
| Total amount |  | 2
TM.120.A2 | PLATE HEAT EXCHANGER WITH SCREWS FROM STAINLESS STEEL | piece
PLATE HEAT EXCHANGER WITH SCREWS FROM STAINLESS STEEL compliance with standards: UNI EN 307; Instruction PED 97/23/CE; I.S.P.E.S.L..Construction and installation characteristics: Plate heat exchanger, which is essentially made of:: -piles of printed plates made of stainless steel AISI 304 or 306, depending of required and / or specified quantities, which are provided with openings for the passage of two different fluids which change heat and passage same fluids, obtained by cleavage patterns in the form of fish bones on the board. The thickness of each panel will be less than 5/10 mm; - Two heads at the ends with bars for mounting printed plates, one of head is fixed and other mobile(plate for pressure), made from carbonic steel with a thickness of not less than 20 mm, which have connections with flanges or charges (as appropriate), and colored from outside with epoxy paint resistant to high temperatures;
Plates and heads will be connected between themselves with connections made of steel, with bolts on their heads, and closing of exchanger will be done with the help of butyl sealant, resistant to high temperature; - External thermal insulation, is derived from a mat from glass wool thickness not less than 60 mm (density not less than 30kg/m3) for the operation of the hot fluid, and the extended elastomeric, a thickness not less than 30 mm during the works with chilled water.
The ends in both cases will be with aluminum sheet minimum 10/10 mm. For delivery of exchangers must be provided: - special vehicles and / or support for mounting heads; - Plate with name, strongly anchored, reported all the features of exchanger (operating pressure, thermal power, flow, temperature and pressure drop of two liquids) Functional features: as indicated in the items. Price includes: - hydraulic connections; - Various consumable materials.
PLATE HEAT EXCHANGER WITH SCREWS FROM STAINLESS STEEL AISI 304, capacity 90 kW
| Central plant – air conditioning |  | 1
| Total amount |  | 1
TOTAL HEAT EXCHANGERS
TN | THERMAL INSULATION AND CLADDING
TN.110.A5 | THERMAL INSULATION FOR PIPE COATING (OR PLATE ) EXTENDED ELASTOMERIC FOAM | m2
THERMAL INSULATION FOR PIPE COATING (OR PLATE ) EXTENDED ELASTOMERIC FOAM compliance with standards: - UNI 10376; - UNI EN ISO 8497; - UNI EN 12086; - Reaction on the fire: confirmation reaction on the fire class "1". Construction and installation features: expanded elastomeric insulation with closed cells, made for extrusion and vulcanization of nitrile synthetic rubber with a smooth surface and a cylindrical part, self-extinguishing and resistant to heating oil, common chemical solvents and springs. For larger diameter ,where the shell is not available, will adapt the plate of the same material. Connections between the various parts will be glued with heads and a separate sealed with adhesive tape, which will provide the same manufacturer.
The typology of the installation are described in the project-CSA or other technical documents. Technical Features: thermal conductivity at a temperature of +40 ° C, does not exceed 0.040 W / mK (value specified university laboratory); - Factor of resistance to water vapor diffusion is greater than 7000; - Operating temperature: between -50 ° C Fr e + 100 ° C; - Product CFC and HCFC, PVC and halogens (chlorine and bromine); - Reaction to fire as it is described above, with a low toxicity and smoke opacity. Price includes: - waste and scrap, special pieces; - Various supplies.
Thermal insulation for pipes, 19 mm thickness
| Central plant – air conditioning |  | 35
| Total amount |  | 35
TN.110.A7 | THERMAL INSULATION FOR PIPE COATING (OR PLATE ) EXTENDED ELASTOMERIC FOAM | m2
THERMAL INSULATION FOR PIPE COATING (OR PLATE ) EXTENDED ELASTOMERIC FOAM compliance with standards: - UNI 10376; - UNI EN ISO 8497; - UNI EN 12086; - Reaction on the fire: confirmation reaction on the fire class "1". Construction and installation features: expanded elastomeric insulation with closed cells, made for extrusion and vulcanization of nitrile synthetic rubber with a smooth surface and a cylindrical part, self-extinguishing and resistant to heating oil, common chemical solvents and springs. For larger diameter ,where the shell is not available, will adapt the plate of the same material. Connections between the various parts will be glued with heads and a separate sealed with adhesive tape, which will provide the same manufacturer.
The typology of the installation are described in the project-CSA or other technical documents. Technical Features: thermal conductivity at a temperature of +40 ° C, does not exceed 0.040 W / mK (value specified university laboratoriy); - Factor of resistance to water vapor diffusion is greater than 7000; - Operating temperature: between -50 ° C Fr e + 100 ° C; - Product CFC and HCFC, PVC and halogens (chlorine and bromine); - Reaction to fire as it is described above, with a low toxicity and smoke opacity. Price includes: - waste and scrap, special pieces; - Various supplies.
Thermal insulation for pipes, 30 mm thickness
| Central plant – air conditioning |  | 46
| Total amount |  | 46
TN.120.A4 | THERMAL INSULATION FROM THE PURE SEMI-RIGID FIBERGLASS | m2
THERMAL INSULATION FROM THE PURE SEMI-RIGID FIBERGLASS : compliance with standards: : - UNI 10376; - UNI EN ISO 8497; - UNI EN 12086; - Reaction to fire: confirmation reaction on the fire class “0-1”. Construction and installation features: isolation of the solid was conducted with hand-made cup (with only one longitudinal section) made of glass wool, and a cylindrical shape, which is treated with a thermosetting resin..The typology of the installation are described in the project-CSA or other technical documents and taking into account the same price cups installed with wires and aluminum craft paper and then coated with craft paper. Technical features: - Density: not less than 60 kg/m3 - the final operating temperature: 400 ° C; - Thermal conductivity at a temperature of +40 ° C, which is greater than 0.040 W / mK (stated value of university laboratories). Price includes: - waste and scrap, special chipping; - Various supplies.
Mineral wool insulation for the pipes, a thickness of 50 mm
| Central plant – air conditioning |  | 35
| Total amount |  | 35
TN.410.A1 |  | m2
SHEET FACING
Construction and installation features:
External impregnation with tin (aluminum, galvanized or painted steel or stainless steel according to what is required and / or specified in project study) minimum thickness of 0.6 mm, constructed in links (cylindrical tubes and circular cannels)cut along a generator
The method of installation is specified in the specification.
Price includes
Waste and scrap and separate chipping
Various supplies.
Facing from Al sheet
| Central plant – air conditioning |  | 103
| Total amount |  | 103
TOTAL THERMAL INSULATION AND CLADDING
TO | INSTRUMENTS AND MEASURES
TO.120.A1 | THERMOMETER WITH DIAL FOR EXTENSION OF INERT GAS (nitrogen) | piece
THERMOMETER WITH DIAL FOR EXTENSION OF INERT GAS (nitrogen) compliance with standards: approval of ISPESL (thermometers in the central heating for hot water); Construction and installation features: device temperatures testing in the plumbing and air conditioning air type for the expansion of an inert gas (nitrogen) with thermal metric and capillary coil springs, chrome-plated steel, which consists of: - a strong cash from chrome or brass (same price) from stainless steel diameter 100 mm, with the rear threaded radial or optionally, together with an annular glass door of the same material, with a waterproof seal and the glass; - Dial with white aluminum with a number system that has been put on unchangeable way the scale in Celsius (° C) degrees with the temperature and the type of working fluid.
In the event that a thermometer is installed on the pipe or the air channels, it would be a spherical type, together with a strong rounding which is to be inserted into the pipe or channel, and the connections with the hollow balls with the aid of the flange or the threaded sleeve. Technical features: readability: with + / - 1% of range scale. Price includes: Insert recess; - Special chipping; - Various supplies.
THERMOMETER
| Central plant – air conditioning |  | 28
| Total amount |  | 28
TO.210.B1 | PRESSURE GAUGE WITH DIALS FOR LIQUIDS BOURDON SPRINGS | piece
PRESSURE GAUGE WITH DIALS FOR LIQUIDS BOURDON SPRINGS complience wth standards : approval of ISPESL. Construction and installation features: device for viewing and controling the pressure in the plumbing, the type of elastic material type Bourdon, glycerin filling, made with vibration damper, made of: -strong registers of stainless steel, with a diameter of not less than 80 mm, the ring glass door from the same material and with a water-resistant closure, a glass; - The main part and accessories made of brass; Bourdon spring of phosphor bronze; - Swirl curl; - Mikrometrički screw for regulation; - Dial with white aluminum custom scale for the work pressure and the type of working fluid, the numbering system that was put in immutable way.
Depending on what is required and / or indicated: - measuring a pressure gauge will be fitted with pipe fittings and ball valve seal; - For measuring the pressure of the double or triple (with a difference of the flow or return from the front and rear parts of the pumps, etc..), Gauge to be placed together with the hose fitting to the measurement points in the pipes of carbon steel, or galvanized, or copper and spherical sealing valve. Gauge will be installed with flanges for control gauge, along with three-way sealing valve. Technical features: - Scale range is determined based on the correspondence between the merged table ISPESL and the maximum working pressure generator (4,6,10,16,25 bar). Price includes: - Special chipping; - Various supplies.
PRESSURE GAUGE
| Central plant – air conditioning |  | 10
| Total amount |  | 10
TOTAL INSTRUMENTS AND MEASURES
TR | DEVICES FOR INSTALLATIONS
TR.130.B10 | EXPANSION JOINT - NO VIBRATING RUBBER PN 10/16 | piece
EXPANSION JOINT - NO VIBRATING RUBBER PN 10/16 Construction and installation features: - rubber compound compensator, type tubes with spherical undulation, good elasticity nylon reinforcements. The pipe ends are equipped with two rubber collar with moveable flanges on the ends of steel suitable for the passage of screws; or connections with the charge of wrought iron.A compound suitable for the flexible flow tube (transient liquid: water, acids, oils, etc.), For absorbing the voltage, oscillation, tilting, vibration, etc..; suitable for absorbing sound and vibration transmission in pumps, machines and devices at all; - Typology install it marked the CSA. Functional features: - Maximum operating temperature: 90 ° C - nominal working pressure: 10/16 bar. The price includes: enhancements in three parts (or opposing flanges and screws); - Various supplies.
PIPE COMPENSATOR , DN80
| Central plant – air conditioning |  | 4
| Total amount |  | 4
TR.130.B11 | EXPANSION JOINT - NO VIBRATING RUBBER PN 10/16 | piece
EXPANSION JOINT - NO VIBRATING RUBBER PN 10/16 Construction and installation features: - rubber compound compensator, type tubes with spherical undulation, good elasticity nylon reinforcements. The pipe ends are equipped with two rubber collar with moveable flanges on the ends of steel suitable for the passage of screws; or connections with the charge of wrought iron.A compound suitable for the flexible flow tube (transient liquid: water, acids, oils, etc.), For absorbing the voltage, oscillation, tilting, vibration, etc..; suitable for absorbing sound and vibration transmission in pumps, machines and devices at all; - Typology install it marked the CSA. Functional features: - Maximum operating temperature: 90 ° C - nominal working pressure: 10/16 bar. The price includes: enhancements in three parts (or opposing flanges and screws); - Various supplies.
PIPE COMPENSATOR , DN100
| Central plant – air conditioning |  | 8
| Total amount |  | 8
TR.130.B12 | EXPANSION JOINT - NO VIBRATING RUBBER PN 10/16 | piece
EXPANSION JOINT - NO VIBRATING RUBBER PN 10/16 Construction and installation features: - rubber compound compensator, type tubes with spherical undulation, good elasticity nylon reinforcements. The pipe ends are equipped with two rubber collar with moveable flanges on the ends of steel suitable for the passage of screws; or connections with the charge of wrought iron.A compound suitable for the flexible flow tube (transient liquid: water, acids, oils, etc.), For absorbing the voltage, oscillation, tilting, vibration, etc..; suitable for absorbing sound and vibration transmission in pumps, machines and devices at all; - Typology install it marked the CSA. Functional features: - Maximum operating temperature: 90 ° C - nominal working pressure: 10/16 bar. The price includes: enhancements in three parts (or opposing flanges and screws); - Various supplies.
PIPE COMPENSATOR , DN125
| Central plant – air conditioning |  | 12
| Total amount |  | 12
TR.130.B9 | EXPANSION JOINT - NO VIBRATING RUBBER PN 10/16 | piece
EXPANSION JOINT - NO VIBRATING RUBBER PN 10/16 Construction and installation features: - rubber compound compensator, type tubes with spherical undulation, good elasticity nylon reinforcements. The pipe ends are equipped with two rubber collar with moveable flanges on the ends of steel suitable for the passage of screws; or connections with the charge of wrought iron.A compound suitable for the flexible flow tube (transient liquid: water, acids, oils, etc.), For absorbing the voltage, oscillation, tilting, vibration, etc..; suitable for absorbing sound and vibration transmission in pumps, machines and devices at all; - Typology install it marked the CSA. Functional features: - Maximum operating temperature: 90 ° C - nominal working pressure: 10/16 bar. The price includes: enhancements in three parts (or opposing flanges and screws); - Various supplies.
PIPE COMPENSATOR , DN65
| Central plant – air conditioning |  | 8
| Total amount |  | 8
TR.210.A11 | EXPANSION TANK WITH MEMBRANE | piece
EXPANSION TANK WITH MEMBRANE complience wth standards : - Instruction 97/23/CE (PED) . Construction and installation features: - Expansion vessel with a fixed diaphragm (via density of 500 liters, a Removable membranes), of welded steel plates, cylindrical; equipped with a membrane made of special rubber and fulfill with inert gas (nitrogen), with an appropriate pressure. The outer end with epoxy powder coating; is used to heat the water and the installations in general to absorb the volume expansion of the water, caused by the variation of the temperature in the installation. Functional features: - Maximum operating temperature: 99 ° C; - Maximum operating pressure of 5 bar (the capacity to 200LT); - Maximum working pressure of 6 bar (capacity for over 200 lt). The price includes: - a support installation (when necessary); - Equipment; - Various supplies.
EXPANSION TANKE, 200 litres
| Central plant – air conditioning |  | 4
| Total amount |  | 4
TR.210.A14 | EXPANSION TANK WITH MEMBRANE | piece
EXPANSION TANK WITH MEMBRANE complience wth standards : - Instruction 97/23/CE (PED) . Construction and installation features: - Expansion vessel with a fixed diaphragm (via density of 500 liters, a Removable membranes), of welded steel plates, cylindrical; equipped with a membrane made of special rubber and fulfill with inert gas (nitrogen), with an appropriate pressure. The outer end with epoxy powder coating; is used to heat the water and the installations in general to absorb the volume expansion of the water, caused by the variation of the temperature in the installation. Functional features: - Maximum operating temperature: 99 ° C; - Maximum operating pressure of 5 bar (the capacity to 200LT); - Maximum working pressure of 6 bar (capacity for over 200 lt). The price includes: - a support installation (when necessary); - Equipment; - Various supplies.
EXPANSION TANKE, 500 litres
| Central plant – air conditioning |  | 1
| Total amount |  | 1
TR.210.A5 | EXPANSION TANK WITH MEMBRANE | piece
EXPANSION TANK WITH MEMBRANE complience wth standards : - Instruction 97/23/CE (PED) . Construction and installation features: - Expansion vessel with a fixed diaphragm (via density of 500 liters, a Removable membranes), of welded steel plates, cylindrical; equipped with a membrane made of special rubber and fulfill with inert gas (nitrogen), with an appropriate pressure. The outer end with epoxy powder coating; is used to heat the water and the installations in general to absorb the volume expansion of the water, caused by the variation of the temperature in the installation. Functional features: - Maximum operating temperature: 99 ° C; - Maximum operating pressure of 5 bar (the capacity to 200LT); - Maximum working pressure of 6 bar (capacity for over 200 lt). The price includes: - a support installation (when necessary); - Equipment; - Various supplies.
EXPANSION TANKE, 24 litres
| Central plant – air conditioning |  | 1
| Total amount |  | 1
TR.700.A1 |  | m
RACKS - CABLE TRAYS
RACKS - CABLE TRAYS
Cable Tray for tubes made of galvanized steel plate of at least 10/10 with removable lid for access to the inner tube, made up of brackets, hooks, mounts, stamping, special pieces and all that was necessary to complete the work and perfect functioning
Cable Tray made of galvanized sheet metal fumes. 200x100 mm
| Central plant – air conditioning |  | 82
| Total amount |  | 82
TOTAL DEVICES FOR INSTALLATION
TOTAL – CENTRAL PLANT
02 | THERMAL TECHNOLOGY - UNDERGROUND LEVEL
TB | PIPELINES
TB.110.A1 | PIPES SYSTEM MADE OF BLACK MILLED STEEL | kg
PIPES SYSTEM MADE OF BLACK MILLED STEEL in accordance with standards : UNI EN 10255 midlle series for cross section in inch or DN; UNI EN 10216-1/TR1 for cross section in mm or DN (the minimum thickness of the table 5). Construction and installation features:- seamless pipe with dark milled steel (pipe UNI EN 10255 is permitted, at the same price, the use of welded Fretz-Moon) compounds for digestion; normal weight for different sections and typology of installing pipes for various installations are taken from the norms laid down in the specifications and / or other elaborates related to the project; for making the calculation will be taken of the values ​​of mass per unit of length, depending on the type of pipe used, and their cross-section as specified in the respective tables UNI EN.Price includes:-coating with two coats of anti-rust paint a different color or the same price, pre-coating the factory epoxy resins; in both cases included the restoration of the color of the compounds; - If required, buried pipes, instead of anti-rust coating layer can be coated extruded polyethylene, with the restoration of the compounds. Residues and waste; -Separate parts and accessories; Elements from poptoru and consolidation; - Various supplies.
Black steel pipes
| Underground level - air conditioning |  | 6260
| Underground level - air conditioning- University |  | 35
| Total amount |  | 6295
TOTAL PIPELINES
TC | VALVES AND PIPE COMPONENTS
TC.110.A6 | BALL VALVE FROM BRASS , WITH THREAD,PN16 | piece
BALL VALVE FROM BRASS , WITH THREAD,PN16 in accordance with : UNIT EN 1074; UNI 8858 Construction and installation characteristics: Two-way or three-way valve (according to what is required or as needed) with brass body POT 58Pb nickel or chrome and stainless steel ball- AISI 304; with total open, which have control spring mounted on the inner side of the body with double sealing (2 o-ring Viton and joints from PTFE), handle in the lever maneuver or butterfly, plastic coated metal (with connection on extension, included in the price when it comes to insulated pipes) and connection with thread ; for use in the round of cold or chilled water, potable water, fire alarm installation and gas / air network; - Supply the version with hose, connectors male / female species or open thread, where appropriate; The operating parameters: - Maximum temperature: 110 ° C - nominal working pressure: PN16. Price includes: - pipe fittings, connectors, accessories; - Various supplies.
Ball valve 1"1/4
| Underground level - air conditioning |  | 2
| Total amount |  | 2
TC.110.A7 | BALL VALVE FROM BRASS , WITH THREAD,PN16 | piece
BALL VALVE FROM BRASS , WITH THREAD,PN16 in accordance with : UNIT EN 1074; UNI 8858 Construction and installation characteristics: Two-way or three-way valve (according to what is required or as needed) with brass body POT 58Pb nickel or chrome and stainless steel ball- AISI 304; with total open, which have control spring mounted on the inner side of the body with double sealing (2 o-ring Viton and joints from PTFE), handle in the lever maneuver or butterfly, plastic coated metal (with connection on extension, included in the price when it comes to insulated pipes) and connection with thread ; for use in the round of cold or chilled water, potable water, fire alarm installation and gas / air network; - Supply the version with hose, connectors male / female species or open thread, where appropriate; The operating parameters: - Maximum temperature: 110 ° C - nominal working pressure: PN16. Price includes: - pipe fittings, connectors, accessories; - Various supplies.
Ball valve 1"1/2
| Underground level - air conditioning |  | 6
| Total amount |  | 6
TC.110.A8 | BALL VALVE FROM BRASS , WITH THREAD,PN16 | piece
BALL VALVE FROM BRASS , WITH THREAD,PN16 in accordance with : UNIT EN 1074; UNI 8858 Construction and installation characteristics: Two-way or three-way valve (according to what is required or as needed) with brass body POT 58Pb nickel or chrome and stainless steel ball- AISI 304; with total open, which have control spring mounted on the inner side of the body with double sealing (2 o-ring Viton and joints from PTFE), handle in the lever maneuver or butterfly, plastic coated metal (with connection on extension, included in the price when it comes to insulated pipes) and connection with thread ; for use in the round of cold or chilled water, potable water, fire alarm installation and gas / air network; - Supply the version with hose, connectors male / female species or open thread, where appropriate; The operating parameters: - Maximum temperature: 110 ° C - nominal working pressure: PN16. Price includes: - pipe fittings, connectors, accessories; - Various supplies.
Ball valve 2"
| Underground level - air conditioning |  | 4
| Total amount |  | 4
TC.130.A10 | BUTERFLLY VALVE FROM THE CAST IRON , WITH FLANGES PN 16 | piece
BUTTERFLY VALVE FROM THE CAST IRON FLANGE PN 16 Construction and installation characteristics: butterfly valve with body from cast iron spherical shape GG40, inside lined with EPDM rubber and preformed resilient rings with: round holes with threaded screws fixed to the middle, in the same number as a number of open holes in the flange joints in pipes, or round central hole (type wafer) fixing the clamp and screws ; installed to provide , when the valve is closed, disassembling the pipe and/or intercept components either forward or backward; axle and disc-type lens cap stainless steel or cast iron GG40 spheroidal shape, coated materials unpulsing ; -leverage solid-resistant material and perforated appropriately for the application lock on the key with the seal covered the price when it comes to butterfly valve for fire protection installations; - Locking device and / or pre-positioning (for diameters larger than DN200 lighted wheel with gear). In the case of drinking water usage , the valve shall be supplied with epoxy with appropriate internal processing in accordance with the regulations. In the case of the fire installations usage, all locks must have the same key. In the case of flammable gases usage, butterfly valve shall be of the type described above, except that sealing has to be the seal of the nitrile. The operating parameters: - Maximum operating temperature: 120 ° C - nominal working pressure: 16 bar. Price includes: - fittings, flanges and screws opposite; - Various supplies.
Buterflly valve, DN80
| Underground level - air conditioning |  | 2
| Total amount |  | 2
TC.130.A9 | BUTERFLLY VALVE FROM THE CAST IRON , WITH FLANGES PN 16 | piece
BUTTERFLY VALVE FROM THE CAST IRON FLANGE PN 16 Construction and installation characteristics: butterfly valve with body from cast iron spherical shape GG40, inside lined with EPDM rubber and preformed resilient rings with: round holes with threaded screws fixed to the middle, in the same number as a number of open holes in the flange joints in pipes, or round central hole (type wafer) fixing the clamp and screws ; installed to provide , when the valve is closed, disassembling the pipe and/or intercept components either forward or backward; axle and disc-type lens cap stainless steel or cast iron GG40 spheroidal shape, coated materials unpulsing ; -leverage solid-resistant material and perforated appropriately for the application lock on the key with the seal covered the price when it comes to butterfly valve for fire protection installations; - Locking device and / or pre-positioning (for diameters larger than DN200 lighted wheel with gear). In the case of drinking water usage , the valve shall be supplied with epoxy with appropriate internal processing in accordance with the regulations. In the case of the fire installations usage, all locks must have the same key. In the case of flammable gases usage, butterfly valve shall be of the type described above, except that sealing has to be the seal of the nitrile. The operating parameters: - Maximum operating temperature: 120 ° C - nominal working pressure: 16 bar. Price includes: - fittings, flanges and screws opposite; - Various supplies.
Buterflly valve, DN65
| Underground level - air conditioning |  | 18
| Total amount |  | 18
TOTAL VALVES AND PIPE COMPONENTS
TD | DEVICES FOR AIR DISTRIBUTION AND DIFUSION
TD.110.A1 | METAL RECTANGULAR AIR PIPES | kg
METAL RECTANGULAR AIR PIPES Regulatory compliance: UNI EN 1505:2000; UNI EN 12236:2003; UNI EN 10327:2004; UNI EN 12237:2004; UNI EN 12097:2007. Construction and installation characteristics: air network made up of: - rectangular metal pipes, performed depending on how much was requested or required, from the galvanized steel panels (UNI EN 10327:2004 Sendzimir Z 275), or from stainless steel, or from aluminum; - Seal with flanged or bayonet-seal depending of the size and complete inspection door, devices for calibration (perforated plate or inspection doors), sensors, fins for air and whatever else is necessary and provided. Typology of used equipment , thickness, etc., are indicated in the specifications. Technical features: the sealing class "B" (which includes the seal of the all connections, either the longitudinal or between different transmitters) according to UNI EN 12237:2004; level of purity (UNI EN 12097:2007): Medium. The price included: waste and scrap; - Equipment and special pieces; holders and different bonding; - Various supplies.
Rectangular channels from galvanized sheet
| Underground level – air conditioning |  | 2750
| Total amount |  | 2750
TD.115.A1 |  | m2
RECTANGULAR DUCTS OF INSULATING SENDWICH PANELS (REACTION ON FIRE CLASS ZERO - ONE)
Construction and installation featurese:
Air Network made of:
rectangular channel of solid insulation panels (class strength not less than R4) a "sandwich" which comprises:
a smooth inner aluminum plate and outer plate from the emboss aluminum, thickness 70/80 micron each, well bonded to the foam surface. For channels which are installed outside, the outer plate will have a minimum thickness of 200 microns with a rubbery outer coating for the protection of hail (separately calculated); -
layer of the solid polyurethane foam, thickness not less than 20mm, with a coefficient of thermal conductivity at 10 ° C 0.02 to 0.025 W (m ° C) and a density about 50kg/mc. Expansion agent will only be CO2 or other gases with analog characteristics, with the exception of CFC, HCFC, HFC or other hydrocarbons or flammable gases. The expansion of the CO2 will be occur by the addition of water as a reagent, or by using some other equivalent method. For channels that have been installed outside the thickness of polyurethane will not be less than 30 mm;
Compounds realized through the proper flanges which belong to the type of "invisible" associated bayonet coupling, with the revision doors, equipment calibration, collectors, paddle-deflectors and other necessary and / or required elements
external final processing, placing of the brackets and bands of aluminum symmetrically with sloping sides
Where it is specifically requested and / or required: the inner surface of the panel and accessories for installation which may be in the contact with the air being treated surface means plasticized sanitization with antibacterial properties and activity against mold, in accordance with the standards UNI EN 13403:2004. The validity of the treatment must be documented by a certificate issued by the appropriate laboratory under the applicable regulations ASTM, ISO and so on.
Technical characteristics:
minimum required characteristics of certain standards ISO 9705 (Room Corner test);
class strength not less than R4 per UNI EN 13403:2004;
class endurance "B" (Hermetic closure of the resulting compounds, in the longitudinal as well as between the different parts of it) in accordance with the UNI EN 12237:2004;
Class 1 - 0 reaction to fire (the decision of the Ministry of 31/03/03. article 2) certified by an accredited institute;
toxicity / Dark smoke in case of fire: LA F1 by NF F16-101
level of purity (UNI EN 12097:2007). middle.
Price includes
waste and scrap
allowances and special parts of the
elements of support and fixing
various consumables
The pre-insulated rectangular ducts, 20 mm thick
| Underground levels - ventilation - University |  | 13
| Total amount |  | 13
TD.150.A15 | FLEXIBLE PRE-INSULATED DAMPING AIR CHANNELS FROM THE ALUMINUM AND SPIRAL FROM THE STEEL FOR SPRING | m
FLEXIBLE PRE-INSULATED DAMPING AIR CHANNELS FROM THE ALUMINUM AND SPIRAL FROM THE STEEL FOR SPRING Compliance with standards: reaction on fire class no higher than "1" the decision of the Ministry of 26/06/84. and subsequent modifications by the decision of 03/09/2001; ISO 7235 Cosntruction and installation features: - flexible channel of perforated aluminum with a protective film of polyethylene suitable for use in the food industry; reinforced by a spiral spring steel with external insulation layer of glass fiber and a protective sheath of a thin layer of aluminum / kraft paper. Joints at the ends must be implemented by inserting a suitable material for sealing and holders for tubes made of stainless steel or other material with high corrosion resistance (except for galvanized steel), all included in the contract price. If the cross-section of the flexible hose is different from the connections of devices which should be connected, will be used a part of a conic terminal which will be connected with a flexible tube as indicated above. Typology of installation is listed in the CSA Technical specifications: minimum noise per octave (Hz) 125 250 500 1K 2K 4K (dB) 17 21 21 27 19 14 L = 1000 mm (dB) 19 34 32 35 30 22 L = 2000 mm ; - Operating temperature: -30 to + 140 ⁰ C - flexible ducts must withstand, without leakage, permanent damage, pressure and pressure drop of at least 2kPa (about 200 mm). Price includes: - waste and scrap; - Accessories and special parts; - Complete set of equipment for repair of possible damage to the channels; - Elements for supporting and fixing; - Different consumable items.
Sound-insulated flexible duct diameter 150 mm
| Underground levels - ventilation - University |  | 1
| Total amount |  | 1
TD.220.A20 | OPENING FOR SUPPLY OF AIR FROM THE ANODIZED ALUMINUM WITH DOUBLE ROW OF ADJUSTABLE VANES , WITH TIPPER C | piece
OPENING FOR SUPPLY OF AIR FROM THE ANODIZED ALUMINUM WITH DOUBLE ROW OF ADJUSTABLE VANES , WITH TIPPER Construction and installation: opening for air supply, with double row of blades, which have possibility of individually adjustable: - a frame made of extruded aluminum whit natural final anodized layer (or other color - choice of sueprvisor); - profiled blades with a distances form the 20 mm,from natural anodized aluminum (or other color -choice of supervisor ); - Optionally fixing frame for installation in the wall; - Control damper with aluminum blades, with lamellas in the opposite directions. In any case, a system of fixing holes will be such as to allow easy disassembly and reassembly, without damage to the system as well as the construction component. Using for air diffusion in installation for air-conditioning. The price includes: - additional parts; - Various studs and beams; - Miscellaneous supplies; - Connect to the channel and calibrate the value predicted flow.
Aluminum grille with damper, from 6.1 to 8 dm2
| Underground levels - ventilation |  | 46
| Total amount |  | 46
TOTAL DEVICES FOR AIR DISTRIBUTION AND DIFUSION O
TH | TERMINALS AND HEATING UNITS
TH.230.B2 | CASSETTE FAN COIL UNIT FOR CEILING MOUNTING | piece
CASSETTE FAN COIL UNIT FOR CEILING MOUNTING Compliance with regulations: - UNI EN 1397; CE mark. Design features and installation: - Unit for the treatment of air in a space, For mounting on the ceiling, with bar for the suction outlet opening, with axial-centrifugal fan which is directly connected; suction of air through the central part of the grid and ejection through the side openings with directional deflector. Integral elements: frame made of galvanized steel or rigid plastic material, easy removal for access to internal components, tools required for mounting to the ceiling; - square outer shell of coated galvanized steel or rigid plastic material, with square grille that can be opened for access to the filter and the outer openings for exhaust air with hand-directional deflector; - one or two heat exchangers for the systems with two or four pipes, made of copper tubes with aluminum blades which are fixed to their mechanical spreading.Heat exchanger will have copper collectors with air hole and with two shut-off valves, one with single and one with double regulation (or the valve and bracket) For devices with two tubes: the exchanger with at least three segments of the device with a four-tube refrigerator with at least three segments by heating with only one segment, unless otherwise specified; axial-centrifugal fan with three speeds and thermal protection; air filter that can be recycled, durable, with a protective grille and support (same filter will be spare); - Condensation under the heat to the valve (possibly an extra bowl); lift pump for condensate with alarm for high liquid level and / or problems in the functioning of the pump, the electrical connection to the control box; - Control box for controling the fan speed, pump control for lifting condensate, etc.; - Control panel with switch and speed switch with at least three positions (plus position "off") with remote control, installed with cables to connect to the camera (all included in the price). If the fan coil unit specifically sought a permanent speed regulator instead of the dashboard will be used PCB for the position; Connection terminal for electrical connection with the electrical cable of the correct length.Specifications: Power supply: about 230 (+ / - 10%); Frequency: 50 Hz; - Heating and cooling capacity listed in the following standard conditions does not necessarily correspond with the actual conditions of application equipment: heating water 70/60 ⁰ C ambient at 20 ⁰ C; Cooling: voda7/12 ° C ambient to 27 ° C * bs - 19 ° C bu; speed: Max. Price includes: various additions; Replacement filter; fastening and digested fixing ;
Ceiling cassette 4-pipe fan coil equipment, model UC2
| The underground level - air conditioning - university |  | 2
| Total amount |  | 2
TOTAL TERMINALS AND HEATING BODIES
TI | DEVICES FOR AIR TREATMENT
TI.631.A4 | Supply and installation of manhole fan type KD 450XL3 manufacturer SYSTEMAIR, the operating point Q = 3600m3 / h, H = 250 Pa | piece | 5
TI.631.A5 | Delivery and installation of aluminum protective ventilation grilles AZR 4 - IMP manufacturer or the like
| 800x600 | piece | 5
TI.631.A6 | Delivery and installation of galvanized sheet channels thickness 0.55 to 1.25 mm, depending on the dimensions of the channel | kg | 350
TI.631.A7 | Flange material for tying, hanging, sealing takes 50% of the previous item |  | 0.5
TI.631.A8 | Delivery and installation of mechanical valves type: PL 560X450-TN-40/3300-50 producer Marvent or the like, to maintain overpressure in the staircase.
|  | piece | 5
TOTAL DEVICES FOR AIR TREATMENT
TN | THERMAL INSULATION AND CLADDING
TN.110.A4 | THERMAL INSULATION FOR PIPE COATING (OR PLATE ) EXTENDED ELASTOMERIC FOAM | m2
THERMAL INSULATION FOR PIPE COATING (OR PLATE ) EXTENDED ELASTOMERIC FOAM compliance with standards: - UNI 10376; - UNI EN ISO 8497; - UNI EN 12086; - Reaction on the fire: confirmation reaction on the fire class "1". Construction and installation features: expanded elastomeric insulation with closed cells, made for extrusion and vulcanization of nitrile synthetic rubber with a smooth surface and a cylindrical part, self-extinguishing and resistant to heating oil, common chemical solvents and springs. For larger diameter ,where the shell is not available, will adapt the plate of the same material. Connections between the various parts will be glued with heads and a separate sealed with adhesive tape, which will provide the same manufacturer. The typology of the installation are described in the project-CSA or other technical documents. Technical Features: thermal conductivity at a temperature of +40 ° C, does not exceed 0.040 W / mK (value specified university laboratories); - Factor of resistance to water vapor diffusion is greater than 7000; - Operating temperature: between -50 ° C Fr e + 100 ° C; - Product bezCFC and HCFC, PVC and halogens (chlorine and bromine); - Reaction to fire as it is described above, with a low toxicity and smoke opacity. Price includes: - waste and scrap, special pieces; - Various supplies.
Flexible insulation for pipe, 13 mm in thickness
| Underground level - air conditioning- University |  | 5
| Total amount |  | 5
TN.110.A7 | THERMAL INSULATION FOR PIPE COATING (OR PLATE ) EXTENDED ELASTOMERIC FOAM | m2
THERMAL INSULATION FOR PIPE COATING (OR PLATE ) EXTENDED ELASTOMERIC FOAM compliance with standards: - UNI 10376; - UNI EN ISO 8497; - UNI EN 12086; - Reaction on the fire: confirmation reaction on the fire class "1". Construction and installation features: expanded elastomeric insulation with closed cells, made for extrusion and vulcanization of nitrile synthetic rubber with a smooth surface and a cylindrical part, self-extinguishing and resistant to heating oil, common chemical solvents and springs. For larger diameter ,where the shell is not available, will adapt the plate of the same material. Connections between the various parts will be glued with heads and a separate sealed with adhesive tape, which will provide the same manufacturer. The typology of the installation are described in the project-CSA or other technical documents. Technical Features: thermal conductivity at a temperature of +40 ° C, does not exceed 0.040 W / mK (value specified university laboratories); - Factor of resistance to water vapor diffusion is greater than 7000; - Operating temperature: between -50 ° C Fr e + 100 ° C; - Product bezCFC and HCFC, PVC and halogens (chlorine and bromine); - Reaction to fire as it is described above, with a low toxicity and smoke opacity. Price includes: - waste and scrap, special pieces; - Various supplies.
Flexible insulation for pipe, 30 mm in thickness
| Underground level - air conditioning- University |  | 48
| Total amount |  | 48
TN.120.A4 | THERMAL INSULATION OF PURE SEMI-RIGID FIBERGLASS | m2
THERMAL INSULATION OF PURE SEMI-RIGID FIBERGLASS : compliance with standards: : - UNI 10376; - UNI EN ISO 8497; - UNI EN 12086; - Reaction to fire: confirmation reaction to fire class “0-1”. Construction and installation features: isolation of the solid was conducted with hand-made cup (with only one longitudinal section) made of glass wool, and a cylindrical shape, which is treated with a thermosetting resin..The typology of the installation are described in the project-CSA or other technical documents and taking into account the same price cups installed with wires and aluminum craft paper and then coated with craft paper. Technical features: - Density: not less than 60 kg/m3 - the final operating temperature: 400 ° C; - Thermal conductivity at a temperature of +40 ° C, which is greater than 0.040 W / mK (stated value of university laboratories). Price includes: - waste and scrap, special chipping; - Various supplies.
Pipe insulation form the mineral wool 50 mm thickness
| Underground level - air conditioning- |  | 490
| Total amount |  | 490
TN.410.A1 |  | m2
SHEET FACING
Construction and installation features:
Foreign impregnation with tin (aluminum, galvanized or painted steel or stainless steel according to what is required and / or specified in project study) minimum thickness of 0.6 mm, derived from calendered connections (cylindrical tubes and circular canals) that were visited along a generato
The method of installation is specified in the specification.
Price includes
Waste and scrap and separate chipping
Various supplies.
Facing from Al sheet
| Underground level – air conditioning |  | 540
| Total amount |  | 540
TOTAL THERMAL INSULATION AND CLADDING
TOTAL THERMAL TECHNOLOGY – UNDERGROUND LEVEL
03 | THERMAL TECHNOLOGY - FLOOR AND HIGHER FLOORS
TB | PIPES
TB.110.A1 | PIPES FROM THE BLACK MILLED STEEL | kg
PIPES FROM THE BLACK MILLED STEEL in accordance with standards : UNI EN 10255 middle series for cross section in inch or NP; UNI EN 10216-1/TR1 for cross section in mm or DN (the minimum thickness described in the table 5). Construction and installation features:- seamless pipes from the black milled steel (for the pipes UNI EN 10255 middle series are permitted, at the same price, usage of welded Fretz-Moon) welded connections; normal weight for the different diameters and typology of pipes installing for various installations are those taken from the norms, prescribed in the specifications and / or other elaborates related to the project; for calculation will be taken values of linear density as specified in the respective tables UNI EN.
Price includes:-coating with two coats of anti-rust paint in a different colors or, for the same price, pre-coating in the factory with epoxy resins; in both cases are included again painting on the each connections; - If required, buried pipes, instead of anti-rust coating layer is possible coating from the extruded polyethylene, with again painting of each connections. Residues and waste; -Separate parts and accessories; Elements from supporting and consolidation; - Various supplies.
Pipes from the black steel
| Ground floor - Air Conditioning |  | 1460
| Ground floor - Air Conditioning -Universty |  | 1080
| First floor - Air Conditioning |  | 7920
| Second floor - Air Conditioning |  | 2420
| Roof - Air Conditioning |  | 590
| Total amount |  | 13470
TOTAL PIPES
TC | VALVES AND PIPE COMPONENTS
TC.110.A5 | BALL VALVE FROM BRASS , WITH THREAD,PN16 | piece
BALL VALVE FROM BRASS , WITH THREAD,PN16 in accordance with : UNIT EN 1074; UNI 8858 Construction and installation characteristics: Two-way or three-way valve (according to what is required or as needed) with brass body POT 58Pb nickel or chrome and stainless steel ball- AISI 304; with total open, which have control spring mounted on the inner side of the body with double sealing (2 o-ring Viton and joints from PTFE), handle in the lever maneuver or butterfly, plastic coated metal (with connection on extension, included in the price when it comes to insulated pipes) and connection with thread ; for use in the round of cold or chilled water, potable water, fire alarm installation and gas / air network; - Supply the version with hose, connectors male / female species or open thread, where appropriate; The operating parameters: - Maximum temperature: 110 ° C - nominal working pressure: PN16. Price includes: - pipe fittings, connectors, accessories; - Various supplies.
Ball valve diameter 1"
| Second floor - Air Conditioning |  | 4
| Total amount |  | 4
TC.110.A6 | BALL VALVE FROM BRASS , WITH THREAD,PN16 | piece
BALL VALVE FROM BRASS , WITH THREAD,PN16 in accordance with : UNIT EN 1074; UNI 8858 Construction and installation characteristics: Two-way or three-way valve (according to what is required or as needed) with brass body POT 58Pb nickel or chrome and stainless steel ball- AISI 304; with total open, which have control spring mounted on the inner side of the body with double sealing (2 o-ring Viton and joints from PTFE), handle in the lever maneuver or butterfly, plastic coated metal (with connection on extension, included in the price when it comes to insulated pipes) and connection with thread ; for use in the round of cold or chilled water, potable water, fire alarm installation and gas / air network; - Supply the version with hose, connectors male / female species or open thread, where appropriate; The operating parameters: - Maximum temperature: 110 ° C - nominal working pressure: PN16. Price includes: - pipe fittings, connectors, accessories; - Various supplies.
Ball valve diameter 1"1/4
| Ground floor - Air Conditioning -Universty |  | 4
| Ground floor - Air Conditioning |  | 6
| Second floor - Air Conditioning |  | 4
| Total amount |  | 14
TC.110.A7 | BALL VALVE FROM BRASS , WITH THREAD,PN16 | piece
BALL VALVE FROM BRASS , WITH THREAD,PN16 in accordance with : UNIT EN 1074; UNI 8858 Construction and installation characteristics: Two-way or three-way valve (according to what is required or as needed) with brass body POT 58Pb nickel or chrome and stainless steel ball- AISI 304; with total open, which have control spring mounted on the inner side of the body with double sealing (2 o-ring Viton and joints from PTFE), handle in the lever maneuver or butterfly, plastic coated metal (with connection on extension, included in the price when it comes to insulated pipes) and connection with thread ; for use in the round of cold or chilled water, potable water, fire alarm installation and gas / air network; - Supply the version with hose, connectors male / female species or open thread, where appropriate; The operating parameters: - Maximum temperature: 110 ° C - nominal working pressure: PN16. Price includes: - pipe fittings, connectors, accessories; - Various supplies.
Ball valve diameter 1"1/2
| Ground floor - Air Conditioning -Universty |  | 4
| Ground floor - Air Conditioning |  | 2
| Second floor - Air Conditioning |  | 4
| Total amount |  | 10
TC.110.A8 | BALL VALVE FROM BRASS , WITH THREAD,PN16 | piece
BALL VALVE FROM BRASS , WITH THREAD,PN16 in accordance with : UNIT EN 1074; UNI 8858 Construction and installation characteristics: Two-way or three-way valve (according to what is required or as needed) with brass body POT 58Pb nickel or chrome and stainless steel ball- AISI 304; with total open, which have control spring mounted on the inner side of the body with double sealing (2 o-ring Viton and joints from PTFE), handle in the lever maneuver or butterfly, plastic coated metal (with connection on extension, included in the price when it comes to insulated pipes) and connection with thread ; for use in the round of cold or chilled water, potable water, fire alarm installation and gas / air network; - Supply the version with hose, connectors male / female species or open thread, where appropriate; The operating parameters: - Maximum temperature: 110 ° C - nominal working pressure: PN16. Price includes: - pipe fittings, connectors, accessories; - Various supplies.
Ball valve diameter 2"
| First floor - Air Conditioning |  | 10
| Total amount |  | 10
TC.130.A9 | BUTTERFLY VALVE FROM CAST IRON FLANGE PN 16 | piece
BUTTERFLY VALVE FROM THE CAST IRON FLANGE PN 16Construction and installation characteristics: butterfly valve with body from cast iron spherical shape GG40, inside lined with EPDM rubber and preformed resilient rings with: round holes with threaded screws fixed to the middle, in the same number as a number of open holes in the flange joints in pipes, or round central hole (type wafer) fixing the clamp and screws ; installed to provide , when the valve is closed, disassembling the pipe and/or intercept components either forward or backward; axle and disc-type lens cap stainless steel or cast iron GG40 spherical shape, coated materials unpulsing ; -leverage solid-resistant material and perforated appropriately for the application lock on the key with the seal covered the price when it comes to butterfly valve for fire protection installations; - Locking device and / or pre-positioning (for diameters larger than DN200 lighted wheel with gear) In the case of drinking water usage , the valve shall be supplied with epoxy with appropriate internal processing in accordance with the regulations. In the case of the fire installations usage, all locks must have the same key. In the case of flammable gases usage, butterfly valve shall be of the type described above, except that sealing has to be the seal of the nitrile. The operating parameters: - Maximum operating temperature: 120 ° C - nominal working pressure: 16 bar. Price includes: - fittings, flanges and screws opposite; - Various supplies.
BUTTERFLY VALVE DN65
| First floor - Air Conditioning |  | 6
| Total amount |  | 6
TC.220.A3 | SHUT - OFF VALVE | piece
SHUT - OFF VALVE Construction and installation characteristics: A valve for closing consisting of a body of chrome-plated brass, brass closure, and the shutter coupling with threads for the pipes from the copper or iron, which are at right angles for the same price and according to the demand, and / or optionally; has command of the closure / adjustment micrometer screw-capped plastic cover. Hydraulic sealing gaskets in EPDM with PTFE. Used for radiators for the heating / air conditioning. Functioning: - Maximum operating temperature: 110 ° C; - Nominal working pressure: 10 bar; Price includes: - Additional parts; - Various supplies.
Shut - of valve 1/2"
| Ground floor - Air Conditioning |  | 8
| Ground floor - Air Conditioning -Universty |  | 6
| First floor - Air Conditioning |  | 9
| Second floor - Air Conditioning |  | 6
| Total amount |  | 29
TC.233.A3 | THERMOSTATIC VALVE FOR A RADIATOR | piece
THERMOSTATIC VALVE FOR A RADIATOR Construction and installation characteristics: Thermostatic valve with body from chrome-plated brass, brass closure and couplings with threads for the pipes of iron or copper, which are at right angles at the same price and under the demand and / or required;; has a thermostatic head with ribbed button (which can be stopped at 20 ° C and "antifreeze" positions) form plastic adjustment circulating fluid and the internal thermostat command with sensitive element for the expansion of liquid or gas (which can be replaced by a device to function without leakage). Hydraulic sealing gaskets in EPDM with PTFE. The valve is used in the final parts of the heating / air conditioning to maintain a constant temperature at the set value in the interior space; Functioning: - Maximum operating temperature: 110 ° C - nominal working pressure of 10 bar; - Setting range from 6 ° C to 30 ° C. Price includes: - Additional parts; - Various supplies.
THERMOSTATIC VALVE FOR A RADIATOR 1/2"
| Ground floor - Air Conditioning |  | 8
| Ground floor - Air Conditioning -Universty |  | 6
| First floor - Air Conditioning |  | 9
| Second floor - Air Conditioning |  | 6
| Total amount |  | 29
TOTAL VALVES AND PIPE COMPONENTS
TD | DEVICES FOR AIR DISTRIBUTION
TD.115.A1 |  | m2
RECTANGULAR AIR CHANNELS FROM THE INSULATING SANDWICH PANELS (REACTION ON THE FIRE CLASS ZERO - ONE)
Construction and installation featurese:
Air Networks made of:
rectangular channels made of solid insulation panels (class strength not less than R4) a "sandwich" which made of :
a smooth inner aluminum plate and outer plate from the emboss aluminum, thickness 70/80 micron each, well bonded to the foam surface. For channels which are installed outside, the outer plate will have a minimum thickness of 200 microns with a rubbery outer coating for the protection of hail (separately calculated); -
layer of the solid polyurethane foam, thickness not less than 20mm, with a coefficient of thermal conductivity at 10 ° C 0.02 to 0.025 W (m ° C) and a density about 50kg/mc. Expansion agent will only be CO2 or other gases with analog characteristics, with the exception of CFC, HCFC, HFC or other hydrocarbons or flammable gases. The expansion of the CO2 will be occur by the addition of water as a reagent, or by using some other equivalent method. For channels that have been installed outside the thickness of polyurethane will not be less than 30 mm;
Compounds realized through the proper flanges which belong to the type of "invisible" associated bayonet coupling, with the revision doors, equipment calibration, collectors, paddle-deflectors and other necessary and / or required elements
external final processing, placing of the brackets and bands of aluminum symmetrically with sloping sides
Where it is specifically requested and / or required: the inner surface of the panel and accessories for installation which may been in contact with the air will be surface treated with means for plasticized sanitization with antibacterial properties and activity against mold, in accordance with the standards UNI EN 13403:2004. The validity of the treatment must be documented by a certificate issued by the appropriate laboratory under the applicable regulations ASTM, ISO and so on.
Technical characteristics:
minimum required characteristics prescribed with standard ISO 9705 (Room Corner test);
strength class not less than R4 per UNI EN 13403:2004;
endurance class "B" (obtained by hermetic closure of each connections, in the longitudinal as well as between the different parts of it) in accordance with the UNI EN 12237:2004;
Class 1 - 0 reaction on the fire (the decision of the Ministry of 31/03/03. article 2) certified by an accredited institute;
toxicity / Dark smoke in the case of fire: LA F1 by NF F16-101
level of purity (UNI EN 12097:2007). middle.
Price includes
waste and scrap
allowances and special parts of the
elements of support and fixing
various consumables
The pre-insulated rectangular channels , 20 mm thickness
| Underground levels - ventilation - |  | 115
| Underground levels - ventilation - University |  | 350
| First floor - Ventilation |  | 660
| Second floor - Ventilation |  | 800
| Total amount |  | 1925
TD.120.A1 | CIRCLE AIR CHANNELS FROM THE GALVANIZED STEEL SHEET | kg
CIRCLE AIR CHANNELS FROM THE GALVANIZED STEEL SHEETCompliance with standards: UNI EN 12236:2003; UNI EN 10327:2004; UNI EN 12237:2004; UNI EN 12097:2007; UNI EN 1506:2008. Construction and installation: networks for airflow: - with circular metal channels, performed according to requrement and / or need, with diameters of channelswhich when they are the largest , are the same as those of the unique series (63,80,100,125,160 mm, ecc.), from the galvanized steel (UNI EN 10327:2004 Sendzimir Z 275 ), or stainless steel, or aluminum. At the same price, the channels will be able to be helical if the predicted structural reinforcements; - the compounds with the socket,with the insertion of double seals (in the shape of fins, a U-shaped, with a double o-ring), such that it is not necessary to use other materials for sealing. According to the application and / or regulations will be able to be accepted and other types of sealing without gaskets, but with the use of polyurethane seals, or the like, as well as the outer tube clamps. Installation type, thickness, etc.. are listed in the CSA. Features: - Class seal of not less than "B" (produced by sealing all joints, whether longitudinal, were among other parts) to the UNI EN 12237:2004; - The level of purity (UNI EN 12097:2007): Medium. Price includes: - waste and scrap; - Additional and separate offense; - Various studs and beams; - Various supplies.
CIRCLE AIR CHANNELS FROM THE GALVANIZED STEEL SHEET
| Ground floor - Air Conditioning |  | 38
| Ground floor - Air Conditioning -Universty |  | 88
| First floor - Air Conditioning |  | 750
| Second floor - Air Conditioning |  | 165
| Total amount |  | 1041
TD.150.A12 | FLEXIBLE PRE-INSULATED DAMPING AIR CHANNELS FROM THE ALUMINUM AND SPIRAL FROM THE STEEL FOR SPRING | m
FLEXIBLE PRE-INSULATED DAMPING AIR CHANNELS FROM THE ALUMINUM AND SPIRAL FROM THE STEEL FOR SPRING Compliance with standards: reaction on fire class no higher than "1" the decision of the Ministry of 26/06/84. and subsequent modifications by the decision of 03/09/2001; ISO 7235 Cosntruction and installation features: - flexible channel of perforated aluminum with a protective film of polyethylene suitable for use in the food industry; reinforced by a spiral spring steel with external insulation layer of glass fiber and a protective sheath of a thin layer of aluminum / kraft paper. Joints at the ends must be implemented by inserting a suitable material for sealing and holders for tubes made of stainless steel or other material with high corrosion resistance (except for galvanized steel), all included in the contract price. If the cross-section of the flexible hose is different from the connections of devices which should be connected, will be used a part of a conic terminal which will be connected with a flexible tube as indicated above. Typology of installation is listed in the CSA Technical specifications: minimum noise per octave (Hz) 125 250 500 1K 2K 4K (dB) 17 21 21 27 19 14 L = 1000 mm (dB) 19 34 32 35 30 22 L = 2000 mm ; - Operating temperature: -30 to + 140 ⁰ C - flexible ducts must withstand, without leakage, permanent damage, pressure and pressure drop of at least 2kPa (about 200 mm). Price includes: - waste and scrap; - Accessories and special parts; - Complete set of equipment for repair of possible damage to the channels; - Elements for supporting and fixing; - Different consumable items.
Sound-insulated flexible channels diameter 125 mm
| Ground floor - Air Conditioning |  | 10
| Ground floor - Air Conditioning -Universty |  | 38
| First floor - Air Conditioning |  | 150
| Second floor - Air Conditioning |  | 45
| Total amount |  | 243
TD.150.A15 | FLEXIBLE PRE-INSULATED DAMPING AIR CHANNELS FROM THE ALUMINUM AND SPIRAL FROM THE STEEL FOR SPRING | m
FLEXIBLE PRE-INSULATED DAMPING AIR CHANNELS FROM THE ALUMINUM AND SPIRAL FROM THE STEEL FOR SPRING Compliance with standards: reaction on fire class no higher than "1" the decision of the Ministry of 26/06/84. and subsequent modifications by the decision of 03/09/2001; ISO 7235 Cosntruction and installation features: - flexible channel of perforated aluminum with a protective film of polyethylene suitable for use in the food industry; reinforced by a spiral spring steel with external insulation layer of glass fiber and a protective sheath of a thin layer of aluminum / kraft paper. Joints at the ends must be implemented by inserting a suitable material for sealing and holders for tubes made of stainless steel or other material with high corrosion resistance (except for galvanized steel), all included in the contract price. If the cross-section of the flexible hose is different from the connections of devices which should be connected, will be used a part of a conic terminal which will be connected with a flexible tube as indicated above. Typology of installation is listed in the CSA Technical specifications: minimum noise per octave (Hz) 125 250 500 1K 2K 4K (dB) 17 21 21 27 19 14 L = 1000 mm (dB) 19 34 32 35 30 22 L = 2000 mm ; - Operating temperature: -30 to + 140 ⁰ C - flexible ducts must withstand, without leakage, permanent damage, pressure and pressure drop of at least 2kPa (about 200 mm). Price includes: - waste and scrap; - Accessories and special parts; - Complete set of equipment for repair of possible damage to the channels; - Elements for supporting and fixing; - Different consumable items.
Sound-insulated flexible channels diameter 150 mm
| Second floor - ventilation |  | 18
| Total amount |  | 18
TD.150.A23 | FLEXIBLE PRE-INSULATED DAMPING AIR CHANNELS FROM THE ALUMINUM AND SPIRAL FROM THE STEEL FOR SPRING | m
FLEXIBLE PRE-INSULATED DAMPING AIR CHANNELS FROM THE ALUMINUM AND SPIRAL FROM THE STEEL FOR SPRING Compliance with standards: reaction on fire class no higher than "1" the decision of the Ministry of 26/06/84. and subsequent modifications by the decision of 03/09/2001; ISO 7235 Cosntruction and installation features: - flexible channel of perforated aluminum with a protective film of polyethylene suitable for use in the food industry; reinforced by a spiral spring steel with external insulation layer of glass fiber and a protective sheath of a thin layer of aluminum / kraft paper. Joints at the ends must be implemented by inserting a suitable material for sealing and holders for tubes made of stainless steel or other material with high corrosion resistance (except for galvanized steel), all included in the contract price. If the cross-section of the flexible hose is different from the connections of devices which should be connected, will be used a part of a conic terminal which will be connected with a flexible tube as indicated above. Typology of installation is listed in the CSA Technical specifications: minimum noise per octave (Hz) 125 250 500 1K 2K 4K (dB) 17 21 21 27 19 14 L = 1000 mm (dB) 19 34 32 35 30 22 L = 2000 mm ; - Operating temperature: -30 to + 140 ⁰ C - flexible ducts must withstand, without leakage, permanent damage, pressure and pressure drop of at least 2kPa (about 200 mm). Price includes: - waste and scrap; - Accessories and special parts; - Complete set of equipment for repair of possible damage to the channels; - Elements for supporting and fixing; - Different consumable items.
Sound-insulated flexible channels diameter 200 mm
| Second floor - Ventilation |  | 10
| Total amount |  | 10
TD.220.A10 | OPENING FOR SUPPLY OF AIR FROM THE ANODIZED ALUMINUM WITH DOUBLE ROW OF ADJUSTABLE VANES , WITH TIPPER | piece
OPENING FOR SUPPLY OF AIR FROM THE ANODIZED ALUMINUM WITH DOUBLE ROW OF ADJUSTABLE VANES , WITH TIPPER Construction and installation: opening for air supply, with double row of blades, which have possibility of individually adjustable: - a frame made of extruded aluminum whit natural final anodized layer (or other color - choice of sueprvisor); - profiled blades with a distances form the 20 mm,from natural anodized aluminum (or other color -choice of supervisor ); - Optionally fixing frame for installation in the wall; - Control damper with aluminum blades, with lamellas in the opposite directions. In any case, a system of fixing holes will be such as to allow easy disassembly and reassembly, without damage to the system as well as the construction component. Using for air diffusion in installation for air-conditioning. The price includes: - additional parts; - Various studs and beams; - Miscellaneous supplies; - Connect to the channel and calibrate the value predicted flow.
The aluminum air opening, with a damper, from 2.1 to 4 dm2
| Ground floor - Ventilation |  | 2
| Ground floor - Ventilation -Universty |  | 1
| Second floor - Ventilation |  | 2
| Total amount |  | 5
TD.220.A15 | OPENING FOR SUPPLY OF AIR FROM THE ANODIZED ALUMINUM WITH DOUBLE ROW OF ADJUSTABLE VANES , WITH TIPPER | piece
OPENING FOR SUPPLY OF AIR FROM THE ANODIZED ALUMINUM WITH DOUBLE ROW OF ADJUSTABLE VANES , WITH TIPPER Construction and installation: opening for air supply, with double row of blades, which have possibility of individually adjustable: - a frame made of extruded aluminum whit natural final anodized layer (or other color - choice of sueprvisor); - profiled blades with a distances form the 20 mm,from natural anodized aluminum (or other color -choice of supervisor ); - Optionally fixing frame for installation in the wall; - Control damper with aluminum blades, with lamellas in the opposite directions. In any case, a system of fixing holes will be such as to allow easy disassembly and reassembly, without damage to the system as well as the construction component. Using for air diffusion in installation for air-conditioning. The price includes: - additional parts; - Various studs and beams; - Miscellaneous supplies; - Connect to the channel and calibrate the value predicted flow.
The aluminum air opening, with a damper, from 4.1 to 6 dm2
| Second floor - Ventilation |  | 2
| Total amount |  | 2
TD.220.A20 | OPENING FOR SUPPLY OF AIR FROM THE ANODIZED ALUMINUM WITH DOUBLE ROW OF ADJUSTABLE VANES , WITH TIPPER | piece
OPENING FOR SUPPLY OF AIR FROM THE ANODIZED ALUMINUM WITH DOUBLE ROW OF ADJUSTABLE VANES , WITH TIPPER Construction and installation: opening for air supply, with double row of blades, which have possibility of individually adjustable: - a frame made of extruded aluminum whit natural final anodized layer (or other color - choice of sueprvisor); - profiled blades with a distances form the 20 mm,from natural anodized aluminum (or other color -choice of supervisor ); - Optionally fixing frame for installation in the wall; - Control damper with aluminum blades, with lamellas in the opposite directions. In any case, a system of fixing holes will be such as to allow easy disassembly and reassembly, without damage to the system as well as the construction component. Using for air diffusion in installation for air-conditioning. The price includes: - additional parts; - Various studs and beams; - Miscellaneous supplies; - Connect to the channel and calibrate the value predicted flow.
The aluminum air opening, with a damper, from 6.1 to 8 dm2
| Ground floor - Ventilation |  | 2
| Ground floor - Ventilation -Universty |  | 6
| Total amount |  | 8
TD.220.A35 | OPENING FOR SUPPLY OF AIR FROM THE ANODIZED ALUMINUM WITH DOUBLE ROW OF ADJUSTABLE VANES , WITH TIPPER | piece
OPENING FOR SUPPLY OF AIR FROM THE ANODIZED ALUMINUM WITH DOUBLE ROW OF ADJUSTABLE VANES , WITH TIPPER Construction and installation: opening for air supply, with double row of blades, which have possibility of individually adjustable: - a frame made of extruded aluminum whit natural final anodized layer (or other color - choice of sueprvisor); - profiled blades with a distances form the 20 mm,from natural anodized aluminum (or other color -choice of supervisor ); - Optionally fixing frame for installation in the wall; - Control damper with aluminum blades, with lamellas in the opposite directions. In any case, a system of fixing holes will be such as to allow easy disassembly and reassembly, without damage to the system as well as the construction component. Using for air diffusion in installation for air-conditioning. The price includes: - additional parts; - Various studs and beams; - Miscellaneous supplies; - Connect to the channel and calibrate the value predicted flow.
The aluminum air opening, with a damper, from 13.1 to16 dm2
| Ground floor - Ventilation |  | 1
| Total amount |  | 1
TD.220.A40 | OPENING FOR SUPPLY OF AIR FROM THE ANODIZED ALUMINUM WITH DOUBLE ROW OF ADJUSTABLE VANES , WITH TIPPER | piece
OPENING FOR SUPPLY OF AIR FROM THE ANODIZED ALUMINUM WITH DOUBLE ROW OF ADJUSTABLE VANES , WITH TIPPER Construction and installation: opening for air supply, with double row of blades, which have possibility of individually adjustable: - a frame made of extruded aluminum whit natural final anodized layer (or other color - choice of sueprvisor); - profiled blades with a distances form the 20 mm,from natural anodized aluminum (or other color -choice of supervisor ); - Optionally fixing frame for installation in the wall; - Control damper with aluminum blades, with lamellas in the opposite directions. In any case, a system of fixing holes will be such as to allow easy disassembly and reassembly, without damage to the system as well as the construction component. Using for air diffusion in installation for air-conditioning. The price includes: - additional parts; - Various studs and beams; - Miscellaneous supplies; - Connect to the channel and calibrate the value predicted flow.
The aluminum air opening, with a damper, from 16.1 to20 dm2
| Ground floor - Ventilation -Universty |  | 2
| Second floor - Ventilation |  | 2
| Total amount |  | 4
TD.220.B75 | OPENING FOR SUPPLY OF AIR FROM THE ANODIZED ALUMINUM WITH DOUBLE ROW OF ADJUSTABLE VANES , WITH TIPPER | piece
OPENING FOR SUPPLY OF AIR FROM THE ANODIZED ALUMINUM WITH DOUBLE ROW OF ADJUSTABLE VANES , WITH TIPPER Construction and installation: opening for air supply, with double row of blades, which have possibility of individually adjustable: - a frame made of extruded aluminum whit natural final anodized layer (or other color - choice of sueprvisor); - profiled blades with a distances form the 20 mm,from natural anodized aluminum (or other color -choice of supervisor ); - Optionally fixing frame for installation in the wall; - Control damper with aluminum blades, with lamellas in the opposite directions. In any case, a system of fixing holes will be such as to allow easy disassembly and reassembly, without damage to the system as well as the construction component. Using for air diffusion in installation for air-conditioning. The price includes: - additional parts; - Various studs and beams; - Miscellaneous supplies; - Connect to the channel and calibrate the value predicted flow.
The aluminum air opening, with a damper, from 70.1 to 75 dm2
| Second floor - Ventilation |  | 2
| Total amount |  | 2
TD.222.A7 | RECTANGULAR FLOOR OPENING FROM ANODIZED ALUMINUM WITH A BASKET | piece
RECTANGULAR FLOOR OPENING FROM ANODIZED ALUMINUM WITH A BASKET Construction and installation: opening for water and air supply from the floor, with: - a series of solid and fixed mechanically connected rods, straight or oblique,from the extruded anodized aluminum; - outer perimeter aluminum frame for holding and fixing the central parts (rods), removable couplings; - Basket of galvanized steel, which is located below and serves to collect dirt, easy to disassemble and clean the orifice and cannell supply. Suitable for installation in raised floors (standard thickness of 30 mm). Specifications: - possible weight of cargo passing over from 200 to 350 kg.Price includes: - additional parts; - Various studs and beams; - Miscellaneous supplies; - Connect to the channel and calibrate the value predicted flow.
Hidden floor air diffuser with a basket, 600x150 mm
| Second floor - Ventilation |  | 4
| Total amount |  | 4
TD.318.A10 | PLASTIC VALVE FOR AIR INTAKE | piece
PLASTIC VALVE FOR AIR INTAKE Construction and installation: air valve plastic (polypropylene or the like), shock-resistant, it can be wet, circular and inner molded disk with adjustable aperture for calibration of air flow whic is drawnen.As an alternative to plastics company reserves the right of acceptance the development of light steel, for the same price; Fixing will be carried out by special screws, and the pressure spring, or in any other manner identical. Generally used for ventilation of bathrooms, kitchens and similar spaces. Price includes: - additional parts; - Various studs and beams; - Connect to the channel and calibrate the value predicted flow; - Various supplies.
Air valve , DN150
| Ground floor - Ventilation |  | 7
| Ground floor - Ventilation -Universty |  | 8
| First floor - Ventilation |  | 21
| Second floor - Ventilation |  | 10
| Total amount |  | 46
TD.322.A35 | SQUARE SWIRL DIFFUSER FROM THE STEEL (WITH RADIAL HOLES), VARIABLE GEOMETRY, WITH INTEGRATED PLENUM BOXES | piece
SQUARE SWIRL DIFFUSER FROM THE STEEL (WITH RADIAL HOLES), VARIABLE GEOMETRY, WITH INTEGRATED PLENUM BOXES Construction and installation: swirl diffuser air with high induction , with: - plenum box, which is an integral part of the diffuser, made of galvanized sheet steel, for direct circular horizontal or vertical connection to the channel, equipped with a perforated plate, small damper for calibration with whome is managing by side, galvanized hook for hanging; - in front of the air diffusion in the form of panels in painted steel (choice of color by company) with radial holes; each of the apertures will be fitted into the interior of a molded deflector, which can be directed manually (alone), so that there is a swirling movement of air, or in multiple directions,diffusion plate may be disassembled, and attached to the plenum box with central screw or special couplings or on identical manner, In any case, fixing the diffuser system will allow easy disassembly and reassembly without damage to the system and building components (ceilings or false ceilings). It is used especially for air-conditioning (installation height of 2.6 to 4 m) where it is necessary to perfect fit architectural requirements and to change the direction of the range at any time by changing the position of the deflector.Price includes: - additional parts; - Various racks and carriers; - Connect to the channel and calibrate the value predicted flow; - Various supplies.
Adjustable swirl diffuser with plenum box, 400x400
| Second floor - Ventilation |  | 12
| Total amount |  | 12
TD.322.A45 | SQUARE SWIRL DIFFUSER FROM THE STEEL (WITH RADIAL HOLES), VARIABLE GEOMETRY, WITH INTEGRATED PLENUM BOXES | piece
SQUARE SWIRL DIFFUSER FROM THE STEEL (WITH RADIAL HOLES), VARIABLE GEOMETRY, WITH INTEGRATED PLENUM BOXES Construction and installation: swirl diffuser air with high induction , with: - plenum box, which is an integral part of the diffuser, made of galvanized sheet steel, for direct circular horizontal or vertical connection to the channel, equipped with a perforated plate, small damper for calibration with whome is managing by side, galvanized hook for hanging; - in front of the air diffusion in the form of panels in painted steel (choice of color by company) with radial holes; each of the apertures will be fitted into the interior of a molded deflector, which can be directed manually (alone), so that there is a swirling movement of air, or in multiple directions,diffusion plate may be disassembled, and attached to the plenum box with central screw or special couplings or on identical manner, In any case, fixing the diffuser system will allow easy disassembly and reassembly without damage to the system and building components (ceilings or false ceilings). It is used especially for air-conditioning (installation height of 2.6 to 4 m) where it is necessary to perfect fit architectural requirements and to change the direction of the range at any time by changing the position of the deflector.Price includes: - additional parts; - Various racks and carriers; - Connect to the channel and calibrate the value predicted flow; - Various supplies.
Adjustable swirl diffuser with plenum box,, 600x600
| Second floor - Ventilation |  | 8
| Total amount |  | 8
TD.330.A2 | SLOT DIFFUSER OF ALUMINUM WITH HOLES, WITH LONGITUDINAL ADJUSTABLE DEFLECTORS | m
SLOT DIFFUSER OF ALUMINUM WITH HOLES WITH LONGITUDINAL ADJUSTABLE DEFLECTORS Construction and installation: slot diffuser with air vents and adjustable deflectors, with: - case diffusers with side blades and the final parts of aluminum extrusion profiles with, anodized in natural color or other as choice of company; - one or more openings facing towards the underside of the profile, each of which has a separate longitudinal flow diverter (deflector), adjustable by hand, for changing the direction of air flow around the openings; each opening will have a width of about 15 mm; - Grid (isolated or in profile) sliding trucks for calibration. It is used especially for air-conditioning the perimeter diffusion of air (eg, along the outside of large windows) and the diffusion of air to the center of the room. Database profile of the diffuser will have to have the side scoops for supporting the possible edges false ceiling.Price includes: - additional parts; - Various studs and beams; - Connect to the channel and calibrate the value predicted flow; - Various supplies. NB: plenum supply, necessary for the use of diffusers for supply, or the supply, must be carried out under the direction of the company that made the diffuser and will be included with the associated air ducts. As an alternative to the sliding damper blade can be used in the form of a butterfly damper on the inlet plenum.
Linear diffuser with two holes
| Ground floor - Ventilation |  | 5
| Total amount |  | 5
TD.340.A15 | CIRCULAR FLOOR DIFFUSER | piece
CIRCULAR FLOOR DIFFUSER Construction and installation: a circular floor air diffuser, swirl, high induction with: - flanges for mounting to the floor (cast aluminum or self-extinguishing polyamide) with screwed retainer ring located behind; color choice of company- circular grid for the flow of air in the form of concentric circles of the same material as the flange, and is located in the interior, with a swirl of air that is below, all can be easily lifted; - Basket for collecting dirt with the function of damper calibration, attached to the grid so that it can change the distance (ie the central screw). It is used especially for devices where the flow of air or air supply comes from below (areas with floating floors), in order to better utilize convection flow, and, in addition, to allow the targeted removal of local thermal stresses. Price includes: - additional parts; - Various racks and carriers; - Calibrating the flow predicted value; - Various supplies.
Hidden floor diffuser with a basket, diameter 200 mm
| Ground floor - Ventilation -Universty |  | 36
| Ground floor - Ventilation |  | 89
| Second floor - Ventilation |  | 24
| Total amount |  | 149
TD.361.A5 |  | piece
DIFFUSER WITH MOVABLE NOZZLE, WITH A FAR RANG, FROM THE PAINTED ALUMINUM/STEEL WITH SLIDING DAMPER
Technical characteristics and installation:
Air diffuser with movable and sideling nozzle with the distant range, comprising of :
nozzle with an external conical profile from the aluminum or steel, painted surfaces (company choice of color ); the housing of the same material as the nozzle, with the possible manual setting, or (where explicitly required) by using an electric drive
ring assembly and assembly of galvanized sheet steel (suitable, if necessary, to be mounted on a circular channel);
Circular sliding damper for calibration, easy to handle from the outside
Where is requsted and/or specified
electric drive, the ON / OFF; voltage 24V or 230V claim and / or required;
Price includes:
- additional parts;
- various carriers and holders;
- connecting the channel and calibrate the value predicted flow;
- various supplies.
Doble 100mm diffuser with nozzle 300x150 mm
| Ground floor - Ventilation |  | 9
| Total amount |  | 9
TD.410.A7 | GRID FOR INLET/OUTLET FROM THE GALAVNIZED STEEL RAIN RESISTANT | piece
GRID FOR INLET/OUTLET FROM THE GALAVNIZED STEEL RAIN RESISTANT Construction and installation: grid for vacuuming or blowing air, with: - strong perimeter frame made of galvanized steel, square or rectangular with holes for mounting with screws visible; - blades with a profile against the light and against the rain horizontally spaced and tilted 45 ° downwards;gap around 25 mm for sizes up to 100 dm2; 35 mm for greater dimensions; - The second frame of galvanized steel, for mounting to the wall; - Insect screen made of galvanized steel with spacing on the side of not greater than 1 cm; - Painted in RAL color selected by the company. Where was required and / or specified: - spiral with self electric cable heating functions with antifreeze and against obstacles, complete electrical equipment for power.The installation will be directly to the channel, the panel or the wall, with a possible second box (included in price) and, if necessary, the grid will be divided into several parts depending on the space available and the structure to which it is attached. It is used in air-conditioning supply Ae: or blowing in the exterior or interior of the suction in the large space. Price includes: - additional parts; - Various racks and carriers; - Connection to channels or installation of wall and calibrate the value predvinog flow; - Possible electrical connection of the heating cable; - Various supplies.
Open for suction / blowing, from 25.1 to 30 dm2
| Ground floor - Ventilation |  | 4
| Total amount |  | 4
TD.430.A1 | ALUMINUM GRID FOR AIR PASSAGE – OVERFLOW | piece
ALUMINUM GRID FOR AIR PASSAGE – OVERFLOW Construction and installation: grille air passage, the door, in painted steel or aluminum, with: - frame and perimeter frame made of extruded anodized aluminum, square or rectangular in shape, with holes for mounting with screws visible;- blades with a profile in the Y-shaped or V, against the light, arranged horizontally; - second frame of aluminum, which is due to the aesthetics adjusted from the rear; - Painted in RAL color of company choice.It is used in air-conditioning for the passage of air from an air-conditioned room to the other, using a lattice door interior space for housing, industrial, commercial, etc. The price includes: - additional parts; - Various studs and beams; - Various supplies.
Grid for the door, to 9 dm2
| Ground floor - Ventilation-Universty |  | 1
| Ground floor - Ventilation |  | 4
| Total amount |  | 5
TD.430.A2 | ALUMINUM GRID FOR AIR PASSAGE – OVERFLOW | piece
ALUMINUM GRID FOR AIR PASSAGE – OVERFLOW Construction and installation: grille air passage, the door, in painted steel or aluminum, with: - frame and perimeter frame made of extruded anodized aluminum, square or rectangular in shape, with holes for mounting with screws visible;- blades with a profile in the Y-shaped or V, against the light, arranged horizontally; - second frame of aluminum, which is due to the aesthetics adjusted from the rear; - Painted in RAL color of company choice.It is used in air-conditioning for the passage of air from an air-conditioned room to the other, using a lattice door interior space for housing, industrial, commercial, etc. The price includes: - additional parts; - Various studs and beams; - Various supplies.
Grid for the door, of 9.1 to 20 dm2
| Ground floor - Ventilation-Universty |  | 4
| Ground floor - Ventilation |  | 1
| First floor - Ventilation |  | 6
| Second floor - Ventilation |  | 2
| Total amount |  | 13
TD.520.A10 | RECTANGULAR DEMPER FOR CALIBRATION AND / OR SHUT RECTANGULAR DEMPER | piece
RECTANGULAR DEMPER FOR CALIBRATION AND / OR SHUT RECTANGULAR DEMPER Technical characteristics and installation : demper for calibration or preventing air from: -strong molded frame , from the galvanized steel or extruded aluminum (depending of the channel material that is inserted in the), square or rectangular cross-section; - horizontal profiled blades, with the movement in opposite directions, from the galvanized steel or extruded aluminum; placed on galvanized steel shafts with stand made of plastic material resistant to a maximum temperature of 100 ° C, bearing shaft made of brass or bronze; - system of gears and / or levers (internal or external) for moving the blades of galvanized steel or high-resistance plastic, manually operated lever for adjusting the position, locking device and visible position indication open or closed .Where was required and / or specified: - gaskets for sealing on the longitudinal profiles of the blades of a plastic material resistant to high temperature, and side slip rings of PTFE for high temperature resistance and treatment of antibacterial substances; - sealing damper to the anticipated standard DIN 1946 part IV; - Electric servomotor (for manual operation), with locking device for automatic actuators. Type of installation is described in the CSA is used mainly in air-conditioning, for the prevention or control of air flow and air pressure. Price includes: - additional parts: - various carriers and holders; - Connect to the channel and calibrate the value predicted flow and / or pressure; - Various supplies.
Control damper, galvanized steel, with a diameter of 40.1 to 50 dm2
| Ground floor - Ventilation |  | 1
| Total amount |  | 1
TD.520.A2 | RECTANGULAR DEMPER FOR CALIBRATION AND / OR SHUT RECTANGULAR DEMPER | piece
RECTANGULAR DEMPER FOR CALIBRATION AND / OR SHUT RECTANGULAR DEMPER Technical characteristics and installation : demper for calibration or preventing air from: -strong molded frame , from the galvanized steel or extruded aluminum (depending of the channel material that is inserted in the), square or rectangular cross-section; - horizontal profiled blades, with the movement in opposite directions, from the galvanized steel or extruded aluminum; placed on galvanized steel shafts with stand made of plastic material resistant to a maximum temperature of 100 ° C, bearing shaft made of brass or bronze; - system of gears and / or levers (internal or external) for moving the blades of galvanized steel or high-resistance plastic, manually operated lever for adjusting the position, locking device and visible position indication open or closed .Where was required and / or specified: - gaskets for sealing on the longitudinal profiles of the blades of a plastic material resistant to high temperature, and side slip rings of PTFE for high temperature resistance and treatment of antibacterial substances; - sealing damper to the anticipated standard DIN 1946 part IV; - Electric servomotor (for manual operation), with locking device for automatic actuators. Type of installation is described in the CSA is used mainly in air-conditioning, for the prevention or control of air flow and air pressure. Price includes: - additional parts: - various carriers and holders; - Connect to the channel and calibrate the value predicted flow and / or pressure; - Various supplies.
Control damper, galvanized steel, with a diameter of 4.1 to 8 dm2
| First floor - Ventilation |  | 1
| Second floor - Ventilation |  | 1
| Total amount |  | 2
TD.520.A3 | RECTANGULAR DEMPER FOR CALIBRATION AND / OR SHUT RECTANGULAR DEMPER | piece
RECTANGULAR DEMPER FOR CALIBRATION AND / OR SHUT RECTANGULAR DEMPER Technical characteristics and installation : demper for calibration or preventing air from: -strong molded frame ,galvanized steel or extruded aluminum (depending of the channel material that is inserted in the), square or rectangular cross-section; - horizontal profiled blades, with the movement in opposite directions, form the galvanized steel or extruded aluminum; placed on galvanized steel shafts with stand made of plastic material resistant to a maximum temperature of 100 ° C, bearing shaft made of brass or bronze; - system of gears and / or levers (internal or external) to start the blades of galvanized steel or high-resistance plastic, manually operated lever for adjusting the position, locking device and visible position indication open or closed .Where was required and / or specified: - gaskets for sealing the longitudinal profiles of the blades of a plastic material resistant to high temperature, and side slip rings of PTFE for high temperature resistance and treatment of antibacterial substances; - sealing damper to the anticipated standard DIN 1946 part IV; - Electric servomotor (for manual operation), with locking device for automatic actuators. Type of installation is described in the CSA is used mainly in air-conditioning, for the prevention or control of air flow and air pressure. Price includes: - additional parts: - various carriers and holders; - Connect to the channel and calibrate the value predicted flow and / or pressure; - Various supplies.
Control damper, galvanized steel, with a diameter of 8.1 to 12 dm2
| First floor - Ventilation |  | 4
| Total amount |  | 4
TD.531.A2 | FIRE PROTECTION DAMPER WITH TUNNEL AND BLADE REI 120 | piece
FIRE PROTECTION DAMPER WITH TUNNEL AND BLADE REI 120 Compliance with standards: - DM 16/02/2007; - DM 09/03/2007; - EN 1366-2; - EN 13501-3; - Certificates of fire resistance REI 120 for the tunnel and blade, issued by the authorized organization. Construction and installation: fire damper with a tunnel, with: - housing in the form of a tunnel full of refractory materials, on which end are firmly fixed two metal elements (flanges) for connection to air ducts; - only fire blades, the swivel axis of the steel axle with bearings made of fireproof material and with the command at the end by a thermal device with a spring with a fuse or by a device to smoke detecting. For security perimeter seal will guarantee PVC cover that spreads the heat; - small switch that signals repeatable stroke on the distance. Systems of lever blade damper will have to be designed so that it would not allow the reopening of the blades in case the electric servomotor physically separated from the axis of rotation of the paddle.It will have to happen with the damper mounted in any position. In any case lever system will have to allow proper opening blade damper, either manually operated or motorized. Where the required and / or specified: - activating the drive with a return spring, with a metal sheath, and an electric motor intended to activate the power supply to about 230 V, the electric absorption in a differentiated stage of the opening (8 W) opposite of the maintenance phase (W 3) with: * extra electrical contacts for signaling the opening and closing of the damper; * Thermal switch previously connected with cables for temperature discovering inside the channel, and testing device used for simulation of safety intervention;* plate with signal lights / LED lights green and red (for installation on an invisible position near the damper, a piece of paper for the label, * the possibility of manual activation with stops at each position. plant will in addition have the following features: the life expectancy of not less than 5000 security position; * closing time: 16 seconds * Opening: 140 seconds * time for guaranteed operation: 24 hours at 75 ° C; * Mechanical degree of engine protection : IP 42; * angle of rotation axis 90 °. Used with the device for ventilation and air conditioning, with an automatic stop and fire protection; suitable for installation on the channels and in the walls of the functioning independent of mounting position and direction of air flow. Price includes: - additional parts; - Connections to ducts and electrical connections; - Various supplies.
The fire protection damper, 2 hours resistance, from 4.1 to 8 dm2
| Second floor- ventilation |  | 4
| Roof - ventilation |  | 3
| Total amount |  | 7
TD.531.A3 | FIRE PROTECTION DAMPER WITH TUNNEL AND BLADE REI 120 | piece
FIRE PROTECTION DAMPER WITH TUNNEL AND BLADE REI 120 Compliance with standards: - DM 16/02/2007; - DM 09/03/2007; - EN 1366-2; - EN 13501-3; - Certificates of fire resistance REI 120 for the tunnel and blade, issued by the authorized organization. Construction and installation: fire damper with a tunnel, with: - housing in the form of a tunnel full of refractory materials, on which end are firmly fixed two metal elements (flanges) for connection to air ducts; - only fire blades, the swivel axis of the steel axle with bearings made of fireproof material and with the command at the end by a thermal device with a spring with a fuse or by a device to smoke detecting. For security perimeter seal will guarantee PVC cover that spreads the heat; - small switch that signals repeatable stroke on the distance. Systems of lever blade damper will have to be designed so that it would not allow the reopening of the blades in case the electric servomotor physically separated from the axis of rotation of the paddle.It will have to happen with the damper mounted in any position. In any case lever system will have to allow proper opening blade damper, either manually operated or motorized. Where the required and / or specified: - activating the drive with a return spring, with a metal sheath, and an electric motor intended to activate the power supply to about 230 V, the electric absorption in a differentiated stage of the opening (8 W) opposite of the maintenance phase (W 3) with: * extra electrical contacts for signaling the opening and closing of the damper; * Thermal switch previously connected with cables for temperature discovering inside the channel, and testing device used for simulation of safety intervention;* plate with signal lights / LED lights green and red (for installation on an invisible position near the damper, a piece of paper for the label, * the possibility of manual activation with stops at each position. plant will in addition have the following features: the life expectancy of not less than 5000 security position; * closing time: 16 seconds * Opening: 140 seconds * time for guaranteed operation: 24 hours at 75 ° C; * Mechanical degree of engine protection : IP 42; * angle of rotation axis 90 °. Used with the device for ventilation and air conditioning, with an automatic stop and fire protection; suitable for installation on the channels and in the walls of the functioning independent of mounting position and direction of air flow. Price includes: - additional parts; - Connections to ducts and electrical connections; - Various supplies.
The fire protection damper, 2 hours resistance, from 8.1 to 12 dm2
| Second floor- ventilation |  | 11
| Roof - ventilation |  | 5
| Total amount |  | 16
TD.531.A4 | FIRE PROTECTION DAMPER WITH TUNNEL AND SHOVEL REI 120 | piece
FIRE PROTECTION DAMPER WITH TUNNEL AND SHOVEL REI 120 Compliance with standards: - DM 16/02/2007; - DM 09/03/2007; - EN 1366-2; - EN 13501-3; - Certificates of fire resistance REI 120 for the tunnel and shovel, issued by the authorized organization. Construction and installation: fire damper with a tunnel, with: - housing in the form of a tunnel full of refractory materials, which are firmly fixed to the end of the two metal elements (flanges) for connection to air ducts; - only fire blades, the swivel axis of the steel axle with bearings made of fireproof material and with the command at the end by a thermal device with a spring with a fuse or by a device to detect smoke. For security perimeter seal to guarantee PVC cover that spreads the heat; - small switch that signals repeatable stroke distance. Systems lever blade damper will have to be designed so that it would not allow the reopening of the blades in case the electric servomotor physically separated from the axis of rotation of the paddle.It will have to happen with the damper mounted in any position. In any case lever system will have to allow proper opening blade damper, either manually operated or motorized. Where the required and / or specified: - activating the drive with a return spring, with a metal sheath, and an electric motor intended to activate the power supply to about 230 V, the electric absorption in a differentiated stage of the opening (8 W) opposite of the maintenance phase (W 3) with: * extra electrical contacts for signaling the opening and closing of the damper; * Thermal switch previously tethered to discover the temperature inside the channel, and test a device that simulates a safety intervention;* plate with signal lights / LED lights green and red (for installation on an invisible position near the damper, a piece of paper for the label, * the possibility of manual activation with stops at each position. plant will in addition have the following features: the life expectancy of not less than 5000 security position; * closing time: 16 seconds * Opening: 140 seconds * time guaranteed operation: 24 hours at 75 ° C; * Mechanical degree of protection engine: IP 42; * angle of rotation axis 90 °. Used with the device for ventilation and air conditioning, with an automatic stop and fire protection; suitable for installation in ducts in the walls of the functioning independent of mounting position and direction of air flow. Price includes: - additional parts; - Connections to ducts and electrical connections; - Various supplies.
The fire protection damper, 2 hours resistance, from 12.1 to 16 dm2
| Second floor- ventilation |  | 9
| Roof - ventilation |  | 4
| Total amount |  | 13
TD.531.A5 | FIRE PROTECTION DAMPER WITH TUNNEL AND BLADE REI 120 | piece
FIRE PROTECTION DAMPER WITH TUNNEL AND BLADE REI 120 Compliance with standards: - DM 16/02/2007; - DM 09/03/2007; - EN 1366-2; - EN 13501-3; - Certificates of fire resistance REI 120 for the tunnel and blade, issued by the authorized organization. Construction and installation: fire damper with a tunnel, with: - housing in the form of a tunnel full of refractory materials, on which end are firmly fixed two metal elements (flanges) for connection to air ducts; - only fire blades, the swivel axis of the steel axle with bearings made of fireproof material and with the command at the end by a thermal device with a spring with a fuse or by a device to smoke detecting. For security perimeter seal will guarantee PVC cover that spreads the heat; - small switch that signals repeatable stroke on the distance. Systems of lever blade damper will have to be designed so that it would not allow the reopening of the blades in case the electric servomotor physically separated from the axis of rotation of the paddle.It will have to happen with the damper mounted in any position. In any case lever system will have to allow proper opening blade damper, either manually operated or motorized. Where the required and / or specified: - activating the drive with a return spring, with a metal sheath, and an electric motor intended to activate the power supply to about 230 V, the electric absorption in a differentiated stage of the opening (8 W) opposite of the maintenance phase (W 3) with: * extra electrical contacts for signaling the opening and closing of the damper; * Thermal switch previously connected with cables for temperature discovering inside the channel, and testing device used for simulation of safety intervention;* plate with signal lights / LED lights green and red (for installation on an invisible position near the damper, a piece of paper for the label, * the possibility of manual activation with stops at each position. plant will in addition have the following features: the life expectancy of not less than 5000 security position; * closing time: 16 seconds * Opening: 140 seconds * time for guaranteed operation: 24 hours at 75 ° C; * Mechanical degree of engine protection : IP 42; * angle of rotation axis 90 °. Used with the device for ventilation and air conditioning, with an automatic stop and fire protection; suitable for installation on the channels and in the walls of the functioning independent of mounting position and direction of air flow. Price includes: - additional parts; - Connections to ducts and electrical connections; - Various supplies.
The fire protection damper, 2 hours resistance, from 16.1 to 20 dm2
| Roof - ventilation |  | 1
| Total amount |  | 1
TD.531.A6 | FIRE PROTECTION DAMPER WITH TUNNEL AND BLADE REI 120 | piece
FIRE PROTECTION DAMPER WITH TUNNEL AND BLADE REI 120 Compliance with standards: - DM 16/02/2007; - DM 09/03/2007; - EN 1366-2; - EN 13501-3; - Certificates of fire resistance REI 120 for the tunnel and blade, issued by the authorized organization. Construction and installation: fire damper with a tunnel, with: - housing in the form of a tunnel full of refractory materials, on which end are firmly fixed two metal elements (flanges) for connection to air ducts; - only fire blades, the swivel axis of the steel axle with bearings made of fireproof material and with the command at the end by a thermal device with a spring with a fuse or by a device to smoke detecting. For security perimeter seal will guarantee PVC cover that spreads the heat; - small switch that signals repeatable stroke on the distance. Systems of lever blade damper will have to be designed so that it would not allow the reopening of the blades in case the electric servomotor physically separated from the axis of rotation of the paddle.It will have to happen with the damper mounted in any position. In any case lever system will have to allow proper opening blade damper, either manually operated or motorized. Where the required and / or specified: - activating the drive with a return spring, with a metal sheath, and an electric motor intended to activate the power supply to about 230 V, the electric absorption in a differentiated stage of the opening (8 W) opposite of the maintenance phase (W 3) with: * extra electrical contacts for signaling the opening and closing of the damper; * Thermal switch previously connected with cables for temperature discovering inside the channel, and testing device used for simulation of safety intervention;* plate with signal lights / LED lights green and red (for installation on an invisible position near the damper, a piece of paper for the label, * the possibility of manual activation with stops at each position. plant will in addition have the following features: the life expectancy of not less than 5000 security position; * closing time: 16 seconds * Opening: 140 seconds * time for guaranteed operation: 24 hours at 75 ° C; * Mechanical degree of engine protection : IP 42; * angle of rotation axis 90 °. Used with the device for ventilation and air conditioning, with an automatic stop and fire protection; suitable for installation on the channels and in the walls of the functioning independent of mounting position and direction of air flow. Price includes: - additional parts; - Connections to ducts and electrical connections; - Various supplies.
The fire protection damper, 2 hours resistance, from 20.1 to 25 dm2
| Roof - ventilation |  | 1
| Total amount |  | 1
TD.610.A11 | RECTANGULAR DUCTED SILENCERS WITH COMPARTMENTS | piece
RECTANGULAR DUCTED SILENCERS WITH COMPARTMENTS in accordance with standards : - -Reaction on the fire (DIN 4102 A2) certification of the class of 0-1. Construction and Installation: straight acoustic silencer with compartments, with: - Powerful locking sheath with a rectangular cross-section from the galvanized steel sheet, minimum thickness of 1 mm, with end flanges to connect the two sides of the connection to the channel; - series of the sound barrier, the number of which varies, arranged longitudinally, earned a perimeter frame made of galvanized steel and the insert with a sound absorbing mineral wool with a density of not less than 40 kg/m3, which is protected from the outside coating delamination of glass fiber, resistant the air velocity of 20 m / s, anti-fungal and anti-impregnated with moisture, is still protected by a membrane made of plastic polymers (flow clean 'the flow of clean');compartments will have a thickness of 100 mm and 100 mm from the interface; edges entering and leaving air will be rounded and made of galvanized sheet metal. One half of each compartment shall be coated with zinc thickness of about 0.5 mm, with the function of absorption at low frequencies, a second perforated galvanized steel or galvanized densely woven network . Specifications: - Maximum operating temperature: 100 ° C; - Minimum sound damping, per octave (Hz) 63,125,250,500 1K 2K 4K 8K (dB) 5 8 13 15 18 18 14 12 L = 1000 mm (dB) 7 12 16 28 27 27 22 18 L = 1500 mm ( dB) 9 15 22 28 34 34 26 22 L = 2000 mm These features will need to be at a loss of cargo, valued the work flow, not more than 30 Pa and will be seen as a minimum requirement. For preventing loss of cargo within the limit of 30 Pa, the dimensions of the silencer will have to be increased in relation to the channel in which it is inserted. Characteristics of damping and sound recovery will in any case have to be adapted to stop the noise induced in the area, according to the regulations of CSA price includes: - additional parts; - Connecting the channels; - Grooming, checking the correctness of the site; - Various supplies.
Rectangular sound damper, the length of 1000 mm, from 50.1 to 60 dm2
| Second floor - Ventilation |  | 1
| Total amount |  | 1
TD.610.A13 | RECTANGULAR DUCTED SILENCERS WITH COMPARTMENTS | piece
RECTANGULAR DUCTED SILENCERS WITH COMPARTMENTS in accordance with standards : - -Reaction on the fire (DIN 4102 A2) certification of the class of 0-1. Construction and Installation: straight acoustic silencer with compartments, with: - Powerful locking sheath with a rectangular cross-section from the galvanized steel sheet, minimum thickness of 1 mm, with end flanges to connect the two sides of the connection to the channel; - series of the sound barrier, the number of which varies, arranged longitudinally, earned a perimeter frame made of galvanized steel and the insert with a sound absorbing mineral wool with a density of not less than 40 kg/m3, which is protected from the outside coating delamination of glass fiber, resistant the air velocity of 20 m / s, anti-fungal and anti-impregnated with moisture, is still protected by a membrane made of plastic polymers (flow clean 'the flow of clean');compartments will have a thickness of 100 mm and 100 mm from the interface; edges entering and leaving air will be rounded and made of galvanized sheet metal. One half of each compartment shall be coated with zinc thickness of about 0.5 mm, with the function of absorption at low frequencies, a second perforated galvanized steel or galvanized densely woven network . Specifications: - Maximum operating temperature: 100 ° C; - Minimum sound damping, per octave (Hz) 63,125,250,500 1K 2K 4K 8K (dB) 5 8 13 15 18 18 14 12 L = 1000 mm (dB) 7 12 16 28 27 27 22 18 L = 1500 mm ( dB) 9 15 22 28 34 34 26 22 L = 2000 mm These features will need to be at a loss of cargo, valued the work flow, not more than 30 Pa and will be seen as a minimum requirement. For preventing loss of cargo within the limit of 30 Pa, the dimensions of the silencer will have to be increased in relation to the channel in which it is inserted. Characteristics of damping and sound recovery will in any case have to be adapted to stop the noise induced in the area, according to the regulations of CSA price includes: - additional parts; - Connecting the channels; - Grooming, checking the correctness of the site; - Various supplies.
Rectangular sound damper, the length of 1000 mm, from 70.1 to 80 dm2
| Second floor - Ventilation |  | 3
| Total amount |  | 3
TD.610.A14 | RECTANGULAR DUCTED SILENCERS WITH COMPARTMENTS | piece
RECTANGULAR DUCTED SILENCERS WITH COMPARTMENTS in accordance with standards : - -Reaction on the fire (DIN 4102 A2) certification of the class of 0-1. Construction and Installation: straight acoustic silencer with compartments, with: - Powerful locking sheath with a rectangular cross-section from the galvanized steel sheet, minimum thickness of 1 mm, with end flanges to connect the two sides of the connection to the channel; - series of the sound barrier, the number of which varies, arranged longitudinally, earned a perimeter frame made of galvanized steel and the insert with a sound absorbing mineral wool with a density of not less than 40 kg/m3, which is protected from the outside coating delamination of glass fiber, resistant the air velocity of 20 m / s, anti-fungal and anti-impregnated with moisture, is still protected by a membrane made of plastic polymers (flow clean 'the flow of clean');compartments will have a thickness of 100 mm and 100 mm from the interface; edges entering and leaving air will be rounded and made of galvanized sheet metal. One half of each compartment shall be coated with zinc thickness of about 0.5 mm, with the function of absorption at low frequencies, a second perforated galvanized steel or galvanized densely woven network . Specifications: - Maximum operating temperature: 100 ° C; - Minimum sound damping, per octave (Hz) 63,125,250,500 1K 2K 4K 8K (dB) 5 8 13 15 18 18 14 12 L = 1000 mm (dB) 7 12 16 28 27 27 22 18 L = 1500 mm ( dB) 9 15 22 28 34 34 26 22 L = 2000 mm These features will need to be at a loss of cargo, valued the work flow, not more than 30 Pa and will be seen as a minimum requirement. For preventing loss of cargo within the limit of 30 Pa, the dimensions of the silencer will have to be increased in relation to the channel in which it is inserted. Characteristics of damping and sound recovery will in any case have to be adapted to stop the noise induced in the area, according to the regulations of CSA price includes: - additional parts; - Connecting the channels; - Grooming, checking the correctness of the site; - Various supplies.
Rectangular sound damper, the length of 1000 mm, from 80.1 to 90 dm2
| Second floor - Ventilation |  | 4
| Total amount |  | 4
TD.610.A3 | RECTANGULAR DUCTED SILENCERS WITH COMPARTMENTS | piece
RECTANGULAR DUCTED SILENCERS WITH COMPARTMENTS in accordance with standards : - -Reaction on the fire (DIN 4102 A2) certification of the class of 0-1. Construction and Installation: straight acoustic silencer with compartments, with: - Powerful locking sheath with a rectangular cross-section from the galvanized steel sheet, minimum thickness of 1 mm, with end flanges to connect the two sides of the connection to the channel; - series of the sound barrier, the number of which varies, arranged longitudinally, earned a perimeter frame made of galvanized steel and the insert with a sound absorbing mineral wool with a density of not less than 40 kg/m3, which is protected from the outside coating delamination of glass fiber, resistant the air velocity of 20 m / s, anti-fungal and anti-impregnated with moisture, is still protected by a membrane made of plastic polymers (flow clean 'the flow of clean');compartments will have a thickness of 100 mm and 100 mm from the interface; edges entering and leaving air will be rounded and made of galvanized sheet metal. One half of each compartment shall be coated with zinc thickness of about 0.5 mm, with the function of absorption at low frequencies, a second perforated galvanized steel or galvanized densely woven network . Specifications: - Maximum operating temperature: 100 ° C; - Minimum sound damping, per octave (Hz) 63,125,250,500 1K 2K 4K 8K (dB) 5 8 13 15 18 18 14 12 L = 1000 mm (dB) 7 12 16 28 27 27 22 18 L = 1500 mm ( dB) 9 15 22 28 34 34 26 22 L = 2000 mm These features will need to be at a loss of cargo, valued the work flow, not more than 30 Pa and will be seen as a minimum requirement. For preventing loss of cargo within the limit of 30 Pa, the dimensions of the silencer will have to be increased in relation to the channel in which it is inserted. Characteristics of damping and sound recovery will in any case have to be adapted to stop the noise induced in the area, according to the regulations of CSA price includes: - additional parts; - Connecting the channels; - Grooming, checking the correctness of the site; - Various supplies.
Rectangular sound damper, the length of 1000 mm,from 8.1 to 12 dm2
| Second floor - Ventilation |  | 2
| Total amount |  | 2
TD.840.A1 | SELF - RECTANGULAR REGULATOR OF CONSTANT FLOW FROM THE GALVANIZED STEEL (SUPPLY / FEEDER) | piece
SELF - RECTANGULAR REGULATOR OF CONSTANT FLOW FROM THE GALVANIZED STEEL (SUPPLY / FEEDER) Construction and installation : device for flow regulation or air pressure , self-acting, without additional energy, with : - frame of galvanized steel sheet, rectangular cross-section, suitable for connecting channels with flanges and holes for the installation of hanging; frame will be enveloped in sound-insulated coating, made of galvanized steel sheet, thickness not less than 0.7 mm, thermal and soundproof insulated with sponge from the mineral wool thickness of not less than 30 mm and density not less than 70 kg / mc; - control damper made of galvanized steel, which is located and who turns to grips with extremely low friction of PTFE; - Control bellows made of polyurethane (muffling element) with pneumatic action; - Leaf spring made of stainless steel; - An external indicator (scale) for calibration of flow on-site or in the factory. Where specifically required and / or specified, the regulator will have also the following additional components: - electric drive connected to the damper SD and the power supply to 24 V - 50 Hz; - Battery post-heating in two rows of pipes made of copper with aluminum blades, frame of galvanized steel and hydraulic fittings for connection; - Sound damper regulator facing downward (upward if the acceleration),the double layer made up of a galvanized steel sheet (the inner part of the holes) with an interposed layer of glass fiber density of not less than 70 kg / mc in a minimum thickness of 30 mm and a coating or surface treatment in order to prevent the release of fibers. Functioning: self-acting regulator maintains a constant calibrated flow for the full range of anticipated differential pressure; will be able to be connected (if it is explicitly requested) to an external body (plants) for regulation on the distance value delivery of the flow. Terms functioning of the system: - Differential pressure range: 50 to 1000 Pa; - The range of variation of the flow: 4: 1 - Operating temperature: 10 to 50 ° C. The controller will be mounted under the authority of a construction firm in respect of parts of the channel controller piloted up and down. In addition, the regulator will be suitable for the channel supply / supply rectangular cross section. Price includes: - connect the channels and internal electrical connection of the facility; - Water connection to the water supply system battery post-heating when provided; - Sizing accuracy verification and calibration of the site; - Various supplies.
RECTANGULAR REGULATOR OF AIR FLOW 200x100 mm
| Second floor - Ventilation |  | 2
| Total amount |  | 2
TD.840.B4 | SELF - RECTANGULAR REGULATOR OF CONSTANT FLOW FROM THE GALVANIZED STEEL (SUPPLY / FEEDER) | piece
SELF - RECTANGULAR REGULATOR OF CONSTANT FLOW FROM THE GALVANIZED STEEL (SUPPLY / FEEDER) Construction and installation : device for flow regulation or air pressure , self-acting, without additional energy, with : - frame of galvanized steel sheet, rectangular cross-section, suitable for connecting channels with flanges and holes for the installation of hanging; frame will be enveloped in sound-insulated coating, made of galvanized steel sheet, thickness not less than 0.7 mm, thermal and soundproof insulated with sponge from the mineral wool thickness of not less than 30 mm and density not less than 70 kg / mc; - control damper made of galvanized steel, which is located and who turns to grips with extremely low friction of PTFE; - Control bellows made of polyurethane (muffling element) with pneumatic action; - Leaf spring made of stainless steel; - An external indicator (scale) for calibration of flow on-site or in the factory. Where specifically required and / or specified, the regulator will have also the following additional components: - electric drive connected to the damper SD and the power supply to 24 V - 50 Hz; - Battery post-heating in two rows of pipes made of copper with aluminum blades, frame of galvanized steel and hydraulic fittings for connection; - Sound damper regulator facing downward (upward if the acceleration),the double layer made up of a galvanized steel sheet (the inner part of the holes) with an interposed layer of glass fiber density of not less than 70 kg / mc in a minimum thickness of 30 mm and a coating or surface treatment in order to prevent the release of fibers. Functioning: self-acting regulator maintains a constant calibrated flow for the full range of anticipated differential pressure; will be able to be connected (if it is explicitly requested) to an external body (plants) for regulation on the distance value delivery of the flow. Terms functioning of the system: - Differential pressure range: 50 to 1000 Pa; - The range of variation of the flow: 4: 1 - Operating temperature: 10 to 50 ° C. The controller will be mounted under the authority of a construction firm in respect of parts of the channel controller piloted up and down. In addition, the regulator will be suitable for the channel supply / supply rectangular cross section. Price includes: - connect the channels and internal electrical connection of the facility; - Water connection to the water supply system battery post-heating when provided; - Sizing accuracy verification and calibration of the site; - Various supplies.
RECTANGULAR REGULATOR OF AIR FLOW 300x200 mm
| Underground levels - ventilation - University |  | 4
| Total amount |  | 4
TD.840.B5 | SELF - RECTANGULAR REGULATOR OF CONSTANT FLOW OF GALVANIZED STEEL (SUPPLY / FEEDER) | piece
SELF - RECTANGULAR REGULATOR OF CONSTANT FLOW FROM THE GALVANIZED STEEL (SUPPLY / FEEDER) Construction and installation : device for flow regulation or air pressure , self-acting, without additional energy, with : - frame of galvanized steel sheet, rectangular cross-section, suitable for connecting channels with flanges and holes for the installation of hanging; frame will be enveloped in sound-insulated coating, made of galvanized steel sheet, thickness not less than 0.7 mm, thermal and soundproof insulated with sponge from the mineral wool thickness of not less than 30 mm and density not less than 70 kg / mc; - control damper made of galvanized steel, which is located and who turns to grips with extremely low friction of PTFE; - Control bellows made of polyurethane (muffling element) with pneumatic action; - Leaf spring made of stainless steel; - An external indicator (scale) for calibration of flow on-site or in the factory. Where specifically required and / or specified, the regulator will have also the following additional components: - electric drive connected to the damper SD and the power supply to 24 V - 50 Hz; - Battery post-heating in two rows of pipes made of copper with aluminum blades, frame of galvanized steel and hydraulic fittings for connection; - Sound damper regulator facing downward (upward if the acceleration),the double layer made up of a galvanized steel sheet (the inner part of the holes) with an interposed layer of glass fiber density of not less than 70 kg / mc in a minimum thickness of 30 mm and a coating or surface treatment in order to prevent the release of fibers. Functioning: self-acting regulator maintains a constant calibrated flow for the full range of anticipated differential pressure; will be able to be connected (if it is explicitly requested) to an external body (plants) for regulation on the distance value delivery of the flow. Terms functioning of the system: - Differential pressure range: 50 to 1000 Pa; - The range of variation of the flow: 4: 1 - Operating temperature: 10 to 50 ° C. The controller will be mounted under the authority of a construction firm in respect of parts of the channel controller piloted up and down. In addition, the regulator will be suitable for the channel supply / supply rectangular cross section. Price includes: - connect the channels and internal electrical connection of the facility; - Water connection to the water supply system battery post-heating when provided; - Sizing accuracy verification and calibration of the site; - Various supplies.
RECTANGULAR REGULATOR OF AIR FLOW 400x200 mm
| Underground levels - ventilation - University |  | 6
| Second floor - Ventilation |  | 2
| Total amount |  | 8
TD.841.A3 | SELF - CIRCULAR REGULATOR OF CONSTANT FLOW | kom
SELF - CIRCULAR REGULATOR OF CONSTANT FLOW Construction and installation : device for flow regulation or air pressure , self-acting, without additional energy, with : - frame of galvanized steel sheet, circular cross-section, suitable for connecting channels with circular connections which have groove for seals inserting or connection with flange if that is requested ; frame will be enveloped in sound-insulated coating, made of galvanized steel sheet, thickness not less than 0.7 mm, thermal and soundproof insulated with sponge from the mineral wool thickness of not less than 30 mm and density not less than 70 kg / mc; - control damper made of galvanized steel, which is located and who turns to grips with extremely low friction of PTFE; - Control bellows made of polyurethane (muffling element) with pneumatic action; - Leaf spring made of stainless steel; - An external indicator (scale) for calibration of flow on-site or in the factory. Where specifically required and / or specified, the regulator will have also the following additional components: - electric drive connected to the damper SD and the power supply to 24 V - 50 Hz; - Battery post-heating in two rows of pipes made of copper with aluminum blades, frame of galvanized steel and hydraulic fittings for connection; - Sound damper regulator facing downward (upward if the acceleration),the double layer made up of a galvanized steel sheet (the inner part of the holes) with an interposed layer of glass fiber density of not less than 70 kg / mc in a minimum thickness of 30 mm and a coating or surface treatment in order to prevent the release of fibers. Functioning: self-acting regulator maintains a constant calibrated flow for the full range of anticipated differential pressure; will be able to be connected (if it is explicitly requested) to an external body (plants) for regulation on the distance value delivery of the flow. Terms functioning of the system: - Differential pressure range: 50 to 1000 Pa; - The range of variation of the flow: 4: 1 - Operating temperature: 10 to 50 ° C. The controller will be mounted under the authority of a construction firm in respect of parts of the channel controller piloted up and down. In addition, the regulator will be suitable for the channel supply / supply circular cross section. Price includes: - connect the channels and internal electrical connection of the facility; - Water connection to the water supply system battery post-heating when provided; - Sizing accuracy verification and calibration of the site; - Various supplies.
Circular regulator of air flow DN 125
| Underground levels - ventilation - University |  | 8
| Underground levels - ventilation |  | 7
| First floor - Ventilation |  | 117
| Second floor - Ventilation |  | 21
| Total amount |  | 153
TOTAL DEVICES FOR AIR DISTRIBUTION
TE | CONTROL SYSTEMS
TE.700.A6 |  | piece
ELECTRICAL DEVICE WHICH INCLUDE THE COMMAND TABLE AND POWER LINES FOR ALL ELEMENTS
Construction and installation
Electrical control panel for elements such as thermo-mechanical devices, implemented and completed accordingly as required and / or specified in the project documents and specifications, including connection to the line / power line to the command table;
Line of electrical command table to the all elements, including the installation hoses, pipes, ducts and all small items necessary for completeness of installation and proper operation;
Security switch - insulators / Blocking for all the elements
Connection of all elements on the lines which are coming from the command table
Methods of installation are those specified in the specification.
Command table with elements EB_AHU1
| Second floor -ventilation |  | 1
| Total amount |  | 1
TE.700.A7 |  | piece
Command table with elements EB_AHU2
| Roof- ventilation |  | 1
| Total amount |  | 1
TE.700.A8 |  | piece
Command table with elements EB_AHU3
| Second floor -ventilation |  | 1
| Total amount |  | 1
TE.700.A9 |  | piece
Command table with elements EB_AHU4
| Roof- ventilation |  | 1
| Total amount |  | 1
TE.710.A10 |  | piece
MONITORING SYSTEM DDC
BMS system of control-automation with Directly Digital Control (DDC), without a central unit of monitoring (workstation) - peripheral sub-DDK ... in service ... made and finished as the specifications and other elaborates the project, which basically includes:
peripheral sub-DDK ,which is located in the appropriate section of electrical comand table, made of CPU units, power form, module of input-otput, access terminal
lines for connection from the substation to the all the elements in the field or on the command table
elements in the field or on the command table, such as probes, sensors, relays, transmitters, etc.., with the exception of the servo valves and actuator lock, where the predicted and calculated seperately
part of the lines quota for connection to other peripheral
- engineering, start-up;
instruction for personnel and everything what is necessary to make the system complete and how to function in a professional manner.
HVAC control system , DDC10 (EB_AHU1-6 )
| Second floor -ventilation |  | 1
| Total amount |  | 1
TE.710.A11 |  | piece
HVAC control system , DDC10 (EB_AHU3-5 )
| Second floor -ventilation |  | 1
| Total amount |  | 1
TE.710.A12 |  | piece
HVAC control system , DDC10 (EB_AHU4)
| Roof- ventilation |  | 1
| Total amount |  | 1
TE.710.A13 |  | piece
HVAC control system , DDC10 (EB_AHU2)
| Roof- ventilation |  | 1
| Total amount |  | 1
TE.710.A9 |  | piece
HVAC control system, DDC9 (CED first floor)
| FIRST FLOOR - ​​Air Conditioning |  | 1
| Total amount |  | 1
TOTAL CONTROL SYSTEM
TH | TERMINAL UNITS AND RADIATORS
TH.111.A1 |  | watts
STEEL RADIATOR WITH TUBULAR ELEMENTS
Constructon and installation
Radiator for space heating, type with tubular elements which are assembled, made of steel with low carbon content (type FePO1) thickness not less than 10/10 mm, painted with pretreatment phosphation, first painting with electrophoresis, final varnish with epoxy powder. Each radiator will have a small relief valve of the 1/4 ".
The radiator will have (at the same price) shape, size, height, number of fins, and color according to the instructions of the company.
Installation methods are those specified in the specification.
Technical features:
Thermal performance is determined in accordance with the standards UNI EN 442:2004 with ∆T = 50 ° and certified with certificates of technical testings;
Working pressure is adjusted to the actual operating conditions and in any event not less than 8 bar, .
Price includes:
additional parts;
various brackets and suports (including props)
various consumables.
Steel radiators
| GROUND - Air Conditioning |  | 9400
| GROUND - Air Conditioning - UNIVERSITY |  | 5000
| FIRST FLOOR - ​​Air Conditioning |  | 1800
| SECOND FLOOR - ​​Air Conditioning |  | 4900
| Total amount |  | 21100
TH.220.B4 | VALVE CONVECTOR FOR VERTICAL INSTALLATION | piece
VALVE CONVECTOR FOR VERTICAL INSTALLATION Compliance with standards: - UNI EN 1397; - CE mark. Construction and installation like specified in the design documents and primarily made of: - supporting structure (frame) made of galvanized steel sheet occasional thickness, with holes for the screws and retaining elements; - Damping outer coating of the frame (on the 5 pages) with polyester fiber 10 mm thickness and density of 40 kg / mc taped and perfectly sealed on the surface of the galvanized steel frame; - One or two batteries for heat exchange, for the circuit with two tubes and circuit for four tubes, made of copper tubes and aluminum blades blocked on the tubes by mechanical expansion of the same. The battery / batteries will have copper collectors with a small air valve and two shut-off, one normal and the other with double adjustment (or shut-off valve). For devices with two tubes: the battery from at least three rows; for devices with four tubes: cooling battery with at least three rows;battery for heating from only one row , unless otherwise indicated; - Centrifugal electro fan / electro fans, each with a rotating stator and double-reliance; - Reduced Archimedes screw with increased aluminum rotor; - Filter for air regeneration by washing or blowing, embedded in supporting frame which is located in the lower part of the device and which can easily be extracted beacuse of cleaning (another filter will serve as a backup); - The main container for condensation collecting, heat-insulated materials with closed cells and secondary vessel leak valve; - Control panel which includes ignition switch and speed switch for at least three positions (out), which is located on the edge of the device, or at the same price and on the request and / or regulation, remote, with cables for connection to valve convector (all in the price). If it is explicitly claimed valve convector type with constant varying of speed, instead of the panel will be provided electronic card, which will have such a function; - connection head of electrical connections with the electrical cable of the correct length. Valve convector will have to have : - bifurcated electrothermal valve for hot and cold battery battery placed at the edge of valve convector , also including special fittings and insulation against condensation with a well-sealed envelope; - Connections for supply and suction from the galvanized steel, the front panel for closing (RAL according to choice of company) with openings for supply and suction with adjustable blades, which will be deliver by the same supply company of valve convectors, what should be the first to go on the approval of the company. Features: - Supply voltage: 230 V (+ / - 10%); - Frequency: 50 Hz; - A cooling and thermally valve convector potential according to the following conditions: * Heating in water at 50/40 ° C, ambient at 20 ° C; * Cooling water 8/13 ° C, ambient 26 ° C bs - 50% RH; * Speed: Medium; * Thickness: 190 mm max. Price includes: - Various extra parts; - Replacement filter; - Various studs and beams; - Hydraulic compounds, elimination of condensation and electrical connections; - Various supplies.
Wall hidden valve convector mmodel FC-4
| GROUND - AIR CONDITIONS |  | 4
| Total value |  | 4
TH.250.B1 | VALVE CONVECTOR FOR FLOOR INSTALLATION | piece
VALVE CONVECTOR FOR FLOOR INSTALLATION Compliance with standards: - UNI EN 1397; - CE mark. Construction and installation: terminal for air treatment in some space, type for floor installation, with tangential fan, battery for heat exchange and movable grid for supply-exhaust of air , visible on the surface of the floor, air intake of the grid facing to the center of the room where it is installed terminal and supply with treated air over the remaining holes of the same grid , located near the perimeter wall. The terminal will be made of rectangular self-supporting locking structure of galvanized steel, painted with dark epoxy color, for filter closing, electro fan and battery for heat exchange, for floor installation with suitable connections for concrete with supporting unvibration legs, with sound insulation, tangential electro fan with with induction motor , one or two battery for heated exchange , depends of that is it for circuit with two pipes and for circuit with four pipes realized from the copper tubes with aluminum blades blocked on the tubes by mechanical expansion of the same. Battery will have release system of air and two shut-off valves, one orderinary and the other with double adjustment ( or valve for closing). For the device with two pipes: battery from at least three line, for the devices with four pipes: cooling battery with at least three line, battery for heating from only one line, filer for air regeneration, long-term, grid and external supporting frame from anodized aluminum same color as a grid, , grid will be also made of anodized aluminum with profile as (double caps T) inability of falling heels. Frame will have protecting foil against scratch and transverse props for longitudinal grid and connection of the grid profile will be with steel spring and with bumpers in the same color like a grid, - container for collecting condensation, welded, connected with a structure with additional props, with space and under the valve, with external insulation against condensation which is performed with impermeable tar tread, command box for control of fan velocity on the devices corner, which consist transmitter speed. central will control launch and will limit the maximum speed by a microprocessor. Besides that " active" electrical contact will allow device connection on the monitoring system of the building GLT/ZLT ( static intel value of number of rotation-system 0-10V),- connection head of electrical joints with electrical cable with electrical cable of appropriate length, specified for the opposite side of the water connection. technical characteristics:- depth of the structure shall be in accordance with the space in the floor, which is available.,- voltage about 230V( +/-10%),- frequency 50Hz,- terminal and cooling potential of valve convector according to the follow standard conditions, which do not necessarily coincide with the actual working conditions of the device :-heating : water 75/76° C, ambient to 20° C, cooling :water 8/14° C, ambient to 28° C b.s.-19° C b.u. maximal velocity.
Price includes : -Spare Eid; - Various studs and beams; - Hydraulic compounds, elimination of condensation and electrical connections; - Various supplies.
Floor hidden valve convector model GR1
| GROUND - AIR CONDITIONS |  | 11
| GROUND - AIR CONDITIONS -UNIVERSITY |  | 23
| FIRST FLOOR -AIR CONDITION |  | 131
| SECOND FLOOR- AIR CONDITION |  | 29
| Total amount |  | 194
TH.250.B2 | VALVE CONVECTOR FOR FLOOR INSTALLATION | piece
VALVE CONVECTOR FOR FLOOR INSTALLATION Compliance with standards: - UNI EN 1397; - CE mark. Construction and installation: terminal for air treatment in some space, type for floor installation, with tangential fan, battery for heat exchange and movable grid for supply-exhaust of air , visible on the surface of the floor, air intake of the grid facing to the center of the room where it is installed terminal and supply with treated air over the remaining holes of the same grid , located near the perimeter wall. The terminal will be made of rectangular self-supporting locking structure of galvanized steel, painted with dark epoxy color, for filter closing, electro fan and battery for heat exchange, for floor installation with suitable connections for concrete with supporting unvibration legs, with sound insulation, tangential electro fan with with induction motor , one or two battery for heated exchange , depends of that is it for circuit with two pipes and for circuit with four pipes realized from the copper tubes with aluminum blades blocked on the tubes by mechanical expansion of the same. Battery will have release system of air and two shut-off valves, one orderinary and the other with double adjustment ( or valve for closing). For the device with two pipes: battery from at least three line, for the devices with four pipes: cooling battery with at least three line, battery for heating from only one line, filer for air regeneration, long-term, grid and external supporting frame from anodized aluminum same color as a grid, , grid will be also made of anodized aluminum with profile as (double caps T) inability of falling heels. Frame will have protecting foil against scratch and transverse props for longitudinal grid and connection of the grid profile will be with steel spring and with bumpers in the same color like a grid, - container for collecting condensation, welded, connected with a structure with additional props, with space and under the valve, with external insulation against condensation which is performed with impermeable tar tread, command box for control of fan velocity on the devices corner, which consist transmitter speed. central will control launch and will limit the maximum speed by a microprocessor. Besides that " active" electrical contact will allow device connection on the monitoring system of the building GLT/ZLT ( static intel value of number of rotation-system 0-10V),- connection head of electrical joints with electrical cable with electrical cable of appropriate length, specified for the opposite side of the water connection. technical characteristics:- depth of the structure shall be in accordance with the space in the floor, which is available.,- voltage about 230V( +/-10%),- frequency 50Hz,- terminal and cooling potential of valve convector according to the follow standard conditions, which do not necessarily coincide with the actual working conditions of the device :-heating : water 75/76° C, ambient to 20° C, cooling :water 8/14° C, ambient to 28° C b.s.-19° C b.u. maximal velocity.
Price includes : -Spare Eid; - Various studs and beams; - Hydraulic compounds, elimination of condensation and electrical connections; - Various supplies.
Floor hidden valve convector model GR2
| GROUND - AIR CONDITIONS |  | 1
| Total amount |  | 1
TH.250.C1 | VALVE CONVECTOR FOR FLOOR INSTALLATION | piece
VALVE CONVECTOR FOR FLOOR INSTALLATION Compliance with standards: - UNI EN 1397; - CE mark. Construction and installation: terminal for air treatment in some space, type for floor installation, with tangential fan, battery for heat exchange and movable grid for supply-exhaust of air , visible on the surface of the floor, air intake of the grid facing to the center of the room where it is installed terminal and supply with treated air over the remaining holes of the same grid , located near the perimeter wall. The terminal will be made of rectangular self-supporting locking structure of galvanized steel, painted with dark epoxy color, for filter closing, electro fan and battery for heat exchange, for floor installation with suitable connections for concrete with supporting unvibration legs, with sound insulation, tangential electro fan with with induction motor , one or two battery for heated exchange , depends of that is it for circuit with two pipes and for circuit with four pipes realized from the copper tubes with aluminum blades blocked on the tubes by mechanical expansion of the same. Battery will have release system of air and two shut-off valves, one orderinary and the other with double adjustment ( or valve for closing). For the device with two pipes: battery from at least three line, for the devices with four pipes: cooling battery with at least three line, battery for heating from only one line, filer for air regeneration, long-term, grid and external supporting frame from anodized aluminum same color as a grid, , grid will be also made of anodized aluminum with profile as (double caps T) inability of falling heels. Frame will have protecting foil against scratch and transverse props for longitudinal grid and connection of the grid profile will be with steel spring and with bumpers in the same color like a grid, - container for collecting condensation, welded, connected with a structure with additional props, with space and under the valve, with external insulation against condensation which is performed with impermeable tar tread, command box for control of fan velocity on the devices corner, which consist transmitter speed. central will control launch and will limit the maximum speed by a microprocessor. Besides that " active" electrical contact will allow device connection on the monitoring system of the building GLT/ZLT ( static intel value of number of rotation-system 0-10V),- connection head of electrical joints with electrical cable with electrical cable of appropriate length, specified for the opposite side of the water connection. technical characteristics:- depth of the structure shall be in accordance with the space in the floor, which is available.,- voltage about 230V( +/-10%),- frequency 50Hz,- terminal and cooling potential of valve convector according to the follow standard conditions, which do not necessarily coincide with the actual working conditions of the device :-heating : water 75/76° C, ambient to 20° C, cooling :water 8/14° C, ambient to 28° C b.s.-19° C b.u. maximal velocity.
Price includes : -Spare Eid; - Various studs and beams; - Hydraulic compounds, elimination of condensation and electrical connections; - Various supplies.
Floor grid made ​​of anodized aluminum, length 1250 mm
| GROUND - AIR CONDITIONS University |  | 24
| FIRST FLOOR -AIR CONDITION |  | 85
| Total amount |  | 109
TOTAL TERMINAL UNITS AND RADIATORS
TI | UNITS FOR AIR TREATMENT
TI.645.A1 |  | piece
ROOF FAN PULL-OUT
Fully will be made of (pedestal, rotor, cap, etc..) of the strong material, resistant on the shocks as well as on the atmospheric agents (strongly galvanized sheet, or strong glass wool, or something like that). All visible parts from the outside will be colored in the mass or with gel-coat color if they are from plastic; If they are from metal will be painted with appropriate color, which ensure good adhesion for metal (possibly with Primer ") as well as good resistance to atmospheric agents.
Screws will only be made from stainless steel
The electric motor will have, in addition to the different specific requirements, the degree of protection not less than IP54 and rotation speed not higher than 900 revolutions per minute. Bearings will have to be exempted from maintenance.
Primary feature of the roof fan will have to be quietness during the operation.
Will be fitted and installed with:
insect screen from the stainless steel or other similar material from;
silencer, located in the intake, in the form of the maze or movable, reduced height (of 30/40 cm),
gravity damper;
Various additional parts for installation and fixing (including gaskets, bolts, etc..). Roofing fan should be fitted at the base of the wall structure with insertion of rubber seals, thickness of about 8/10 mm (or other similar material) and with screws usage with washers, also from the rubber, in order to achieve its complete insulation from the wall structure.
Price includes electrical and air connections
Roof fan, 400 mc / h
| ROOF - VENTILATION |  | 1
| Total amount |  | 1
TI.645.A2 |  | piece
ROOF FAN PULL-OUT
Fully will be made of (pedestal, rotor, cap, etc..) of the strong material, resistant on the shocks as well as on the atmospheric agents (strongly galvanized sheet, or strong glass wool, or something like that). All visible parts from the outside will be colored in the mass or with gel-coat color if they are from plastic; If they are from metal will be painted with appropriate color, which ensure good adhesion for metal (possibly with Primer ") as well as good resistance to atmospheric agents.
Screws will only be made from stainless steel
The electric motor will have, in addition to the different specific requirements, the degree of protection not less than IP54 and rotation speed not higher than 900 revolutions per minute. Bearings will have to be exempted from maintenance.
Primary feature of the roof fan will have to be quietness during the operation.
Will be fitted and installed with:
insect screen from the stainless steel or other similar material from;
silencer, located in the intake, in the form of the maze or movable, reduced height (of 30/40 cm),
gravity damper;
Various additional parts for installation and fixing (including gaskets, bolts, etc..). Roofing fan should be fitted at the base of the wall structure with insertion of rubber seals, thickness of about 8/10 mm (or other similar material) and with screws usage with washers, also from the rubber, in order to achieve its complete insulation from the wall structure.
Price includes electrical and air connections
Roof fan, 700 mc / h
| ROOF - VENTILATION |  | 2
| Total amount |  | 2
TI.645.A3 |  | piece
ROOF FAN PULL-OUT
Fully will be made of (pedestal, rotor, cap, etc..) of the strong material, resistant on the shocks as well as on the atmospheric agents (strongly galvanized sheet, or strong glass wool, or something like that). All visible parts from the outside will be colored in the mass or with gel-coat color if they are from plastic; If they are from metal will be painted with appropriate color, which ensure good adhesion for metal (possibly with Primer ") as well as good resistance to atmospheric agents.
Screws will only be made from stainless steel
The electric motor will have, in addition to the different specific requirements, the degree of protection not less than IP54 and rotation speed not higher than 900 revolutions per minute. Bearings will have to be exempted from maintenance.
Primary feature of the roof fan will have to be quietness during the operation.
Will be fitted and installed with:
insect screen from the stainless steel or other similar material from;
silencer, located in the intake, in the form of the maze or movable, reduced height (of 30/40 cm),
gravity damper;
Various additional parts for installation and fixing (including gaskets, bolts, etc..). Roofing fan should be fitted at the base of the wall structure with insertion of rubber seals, thickness of about 8/10 mm (or other similar material) and with screws usage with washers, also from the rubber, in order to achieve its complete insulation from the wall structure.
Price includes electrical and air connections
Roof fan, 1700 mc / h
| ROOF - VENTILATION |  | 1
| Total amount |  | 1
TOTAL UNITS FOR AIR TREATMENT
TN | THERMAL INSULATION
TN.110.A4 | THERMAL INSULATION OF PIPES WITH LINING (OR PLATE) FROM THE EXPANDED ELASTOMERIC FOAM | m2
THERMAL INSULATION OF PIPES WITH LINING (OR PLATE) FROM THE EXPANDED ELASTOMERIC FOAM Compliance with standards: - UNI 10376; - UNI EN ISO 8497; - UNI EN 12086; - Fire resistance: Certification of reaction on the fire class "1". Construction and Installation: Insulation from the expanded elastomeric with closed cell, realized by extrusion and vulcanization of synthetic nitrile rubber, smooth and cylindrical in cross-section, self-extinguishing and resistant on the attacks by oil, chemical solvents and mildew. For larger diameters, if the lining is not available, will be adopted plate of the same material. The joints between the individual parts will be glued and sealed with appropriate adhesive tape, which will be supplied by construction company . Installation of the type described in the CSA or other technical documents, project. technical features: - Thermal conductivity by temperature of +40 ° C, no greater than 0.040 W / mK (value confirmed by university laboratory); - Factor of resistance to vapor diffusion is larger than 7000; - Operating temperature: comprised between -50 ° C and + 100 ° C; product without CFC and HCFC, PVC and halogens (chlorine and bromine); - Fire resistance as described above, a low smoke toxicity and opacity. Price includes: - scrap, waste and separate parts; - Various consumables. .
Flexible elastomeric insulation foam for pipes, 13 mm
| GROUND - air conditioning |  | 125
| GROUND -air conditioning - UNIVERSITY |  | 108
| FIRST FLOOR - ​​air conditioning |  | 690
| SECOND FLOOR - ​​air conditioning |  | 150
| Total amount |  | 1073
TN.110.A5 | THERMAL INSULATION OF PIPES WITH LINING (OR PLATE) FROM THE EXPANDED ELASTOMERIC FOAM | m2
THERMAL INSULATION OF PIPES WITH LINING (OR PLATE) FROM THE EXPANDED ELASTOMERIC FOAM Compliance with standards: - UNI 10376; - UNI EN ISO 8497; - UNI EN 12086; - Fire resistance: Certification of reaction on the fire class "1". Construction and Installation: Insulation from the expanded elastomeric with closed cell, realized by extrusion and vulcanization of synthetic nitrile rubber, smooth and cylindrical in cross-section, self-extinguishing and resistant on the attacks by oil, chemical solvents and mildew. For larger diameters, if the lining is not available, will be adopted plate of the same material. The joints between the individual parts will be glued and sealed with appropriate adhesive tape, which will be supplied by construction company . Installation of the type described in the CSA or other technical documents, project. technical features: - Thermal conductivity by temperature of +40 ° C, no greater than 0.040 W / mK (value confirmed by university laboratory); - Factor of resistance to vapor diffusion is larger than 7000; - Operating temperature: comprised between -50 ° C and + 100 ° C; product without CFC and HCFC, PVC and halogens (chlorine and bromine); - Fire resistance as described above, a low smoke toxicity and opacity. Price includes: - scrap, waste and separate parts; - Various consumables. .
Flexible elastomeric insulation foam for pipes, 19 mm
| GROUND - air conditioning |  | 11
| FIRST FLOOR - ​​air conditioning |  | 27
| SECOND FLOOR - ​​air conditioning |  | 22
| Total amount |  | 60
TN.110.A7 | THERMAL INSULATION OF PIPES WITH LINING (OR PLATE) FROM THE EXPANDED ELASTOMERIC FOAM | m2
THERMAL INSULATION OF PIPES WITH LINING (OR PLATE) FROM THE EXPANDED ELASTOMERIC FOAM Compliance with standards: - UNI 10376; - UNI EN ISO 8497; - UNI EN 12086; - Fire resistance: Certification of reaction on the fire class "1". Construction and Installation: Insulation from the expanded elastomeric with closed cell, realized by extrusion and vulcanization of synthetic nitrile rubber, smooth and cylindrical in cross-section, self-extinguishing and resistant on the attacks by oil, chemical solvents and mildew. For larger diameters, if the lining is not available, will be adopted plate of the same material. The joints between the individual parts will be glued and sealed with appropriate adhesive tape, which will be supplied by construction company . Installation of the type described in the CSA or other technical documents, project. technical features: - Thermal conductivity by temperature of +40 ° C, no greater than 0.040 W / mK (value confirmed by university laboratory); - Factor of resistance to vapor diffusion is larger than 7000; - Operating temperature: comprised between -50 ° C and + 100 ° C; product without CFC and HCFC, PVC and halogens (chlorine and bromine); - Fire resistance as described above, a low smoke toxicity and opacity. Price includes: - scrap, waste and separate parts; - Various consumables. .
Flexible elastomeric insulation foam for pipes,, 30 mm
| GROUND - AIR CONDITIONING |  | 19
| FIRST FLOOR - ​​Air Conditioning |  | 37
| SECOND FLOOR - ​​Air Conditioning |  | 70
| ROOF - AIR CONDITIONING |  | 27
| Total amount |  | 153
TN.120.A4 | THERMAL INSULATION FROM THE SEMI-RIGID LINING OF GLASS WOOL | m2
THERMAL INSULATION FROM THE SEMI-RIGID LINING OF GLASS WOOL Compliance with standards: - UNI 10376; - UNI EN ISO 8497; - UNI EN 12086 Fire resistance: Certification of reaction on the fire class "0-1". Construction and installation: isolation implemented by handmade rigid lining (with only one longitudinal section) of glass wool and cylindrical shape, treated with thermo resistance resins. Type of installation is the one described in the CSA or other technical documents of the project taking into account that the same price cover lining with conductor and aluminum craft paper and those previously coated with craft paper. Specifications: - density not less than 60 kg / mc - limit operating temperature: 400 ° C; - Thermal conductivity to temperature of +40 ° C, no larger than 0.040 W / mK (value confirmed by university laboratory). Price includes: - scrap, waste and separate parts; - Various consumables.
Preformed fitting insulation in the form of fiberglass for pipes , 50 mm
| ROOF - AIR CONDITIONING |  | 32
| Total amount |  | 32
TN.214.A6 | EXTERNAL THERMAL INSULATION FOR THE CHANNELS IN THE PANEL FORM FROM THE EXPANDED ELASTOMERIC FOAM | m2
EXTERNAL THERMAL INSULATION FOR THE CHANNELS IN THE PANEL FORM FROM THE EXPANDED ELASTOMERIC FOAM Compliance with standards: - UNI 10376; - UNI EN ISO 8497; - UNI EN 12086; - Fire resistance: Certification of reaction on the fire class "1". Construction and Installation: Insulation from the expanded elastomeric with closed cell, realized by extrusion and vulcanization of synthetic nitrile rubber, smooth and self-extinguishing and resistant on the attacks by oil, chemical solvents and mildew. Insulation will be placed on the external side of the channel and will be fixed to the plate with an appropriate adhesive tape , in a such way that will allow a perfect and permanent adhesion, the joints between the individual parts will be glued and sealed with appropriate adhesive tape, which will be supplied by construction company. Installation of the type described in the CSA or other technical documents, project. technical features: - Thermal conductivity by temperature of +40 ° C, no greater than 0.045 W / mK (value confirmed by university laboratory); - Factor of resistance to vapor diffusion is larger than 7000; - Operating temperature: comprised between -50 ° C and + 100 ° C; product without CFC and HCFC, PVC and halogens (chlorine and bromine); - Fire resistance as described above, a low smoke toxicity and opacity. Price includes: - scrap, waste and separate parts; - Various consumables. .
Flexible elastomeric insulation foam for pipes, thickness of 20 mm
| GROUND - Ventilation |  | 11
| GROUND - Ventilation - UNIVERSITY |  | 23
| FIRST FLOOR - ​​Ventilation |  | 200
| SECOND FLOOR - ​​Ventilation |  | 45
| Total amount |  | 279
TN.410.A1 |  | m2
EXTERNAL COATING WITH METAL SHEET
Construction and installation
External costing from the metal sheet (aluminum, or galvanized and previously painted steel, or stainless steel according to request and / or indication in the documents of the project) minimum thickness of 0.06 mm, with polished parts (cylinder for circular pipes and channels) cut along one generating.
Installation methods are those specified in the specification.
scrap, waste and separate parts
scrap, waste and separate parts
various consumables
Coating with aluminum
| GROUND - AIR CONDITIONING |  | 125
| GROUND - AIR CONDITIONING - UNIVERSITY |  | 108
| FIRST FLOOR - ​​Air Conditioning |  | 690
| SECOND FLOOR - ​​Air Conditioning |  | 190
| ROOF - AIR CONDITIONING |  | 59
| Total Amount |  | 1172
TOTAL THERMAL INSULATION AND CASING
TR | ADDITIONAL PARTS FOR DEVICES
TR.700.A1 |  | m
CABLE TRAYS
Cable tray is made of galvanized sheet steel of at least 10/10 with removable lid for the access to the inner pipes, includes supports, hooks, joints, special parts and all that is need for the perfect functioning.
Cable boxes from galvanized steel dimensions 200x100 mm
| GROUND - AIR CONDITIONING |  | 41
| FIRST FLOOR - AIR CONDITIONING |  | 41
| SECOND FLOOR - AIR CONDITIONING |  | 41
| Total amount |  | 123
TOTAL ADDITIONAL PARTS FOR DEVICES
TOTAL - ABOVE-GROUND PART
B | TOTAL THERMOTECHNICAL INSTALLATIONS :