## ELECTRICAL
NOTE | PRICES TO BE INSERTED MUST BE WITHOUT V.A.T.
C.1. | ELECTRICAL - HIGH VOLTAGE
Notes:
If on some position material or equipment manufacturer is indicated, teneder can instal other materials or equiment if with same or equivalent caracteristics in line with project documentation. All materials and equipment to be used in construction must be authorised by the Investor.
All related preparaory works, finishings, cleanings, correction, testing of materials, instalations, equipment, providing of atests or similar would not be quoted or payed separately. All pricess are to be incorporated in positions of the BoQ of this Volume. For execution of all positions all relevant materials, tools, movements, connections, organisations, worksman, insurance and other related, are suposed to be included in order to execute works in defined conditions, finalisation with indicated guarantee periods - everything ready for technical taking over.
COD. | DESCRIPTION | u.m. | Quantity | Unit price | TOTAL
01 | ELECTRICAL PLANTS - OUTDOOR AREAS
01 - CONDUCTORS, CABLES AND ACCESSORIES
A110.A10.A20 |  | m
XHE CABLE MEDIUM TENSION TYPE XHE Isolation: etilenpropilenic gum quality G7. Sheath: PVC. Conductor in : copper string corda annealed tinned with interposition between isolation and conductor in elastomeric sinteticodic semiconductive material
o. Schermo: nastro di rame non stagnato applicato ad elica. Armored (where required): plate in zinc steal positioned under external protection sheath. Reaction to fire: - non causing fire ; - low corrosive gas emission
XHE cable 12/20kV, 1x240 mm2
| OUTDOOR AREA - MV/LV CABLES |  | 1440
| Total amount |  | 1440
TOTAL CONDUCTORS, CABLES AND ACCESSORIES
02 - CONDUITS
B50.A20.A1 |  | m
PEHD FLEXIBLE PIPE TO BURY IN POLIETILENE WITH HIGH DENSITY In line with CEI 23-39, 23-46 and aditional variants. Classification: non under 3441. Crash/pressure resistance: >=
450N. Impact resistance: >= 6J. Electrical isolation resistance : >= 100Mohm. Dielectric density: >= 20kV/mm. Resistance to Chimical agens and micorganisams reaction. Construction caracteristics : -polietilene pipe with high
density (PEHD), entirely double flatt wall with corrugated exteriors ; - connection for congiuntion of more elements . Level of system protection: min. IP4X.
PEHD flexible pipe D=50mm
| OUTDOOR AREA - MV/LV RACEWAYS |  | 868
| Total amount |  | 868
B50.A20.A8 |  | m
PEHD FLEXIBLE PIPE TO BURY IN POLIETILENE WITH HIGH DENSITY In line with CEI 23-39, 23-46 and aditional variants. Classification: non under 3441. Crash/pressure resistance: >=
450N. Impact resistance: >= 6J. Electrical isolation resistance : >= 100Mohm. Dielectric density: >= 20kV/mm. Resistance to Chimical agens and micorganisams reaction. Construction caracteristics : -polietilene pipe with high
density (PEHD), entirely double flatt wall with corrugated exteriors ; - connection for congiuntion of more elements . Level of system protection: min. IP4X.
PEHD flexible pipe D=160mm
| OUTDOOR AREA - MV/LV RACEWAYS |  | 950
| Total amount |  | 950
CD.A16.A1 |  | m3
DIGGING WITH EXCAVATOR Digging in restricted sections, ordinary terrain of any kind and consistency, even in presence of water less than cm 20, feassible with mechanical machines , except rocks
The price is inclusive of foolowing costs: - estraction of masses to m³ 0,400; - removal of elements of any type to m³ 0,400; - cutting and removal of plants and similar
- draining ; - demolition of useless pavements and substrates in roads of any type ; - leveling of excavated terrains; - stocking of materials in proximity to exavation terrain; - back filling with excavated materials
- preventive signalisation of underground electrical and phone cables, water supply pipes, gas pipes, sewerage netowrk pipes, channels, etc... ; - demolition and reconstruction of protective land slopes ruined during construction process
- selection of materials untill without rocks with scope of I° refililling of tubes and land with flora eventualy present on the surface - perfect reconstruction of exavated terrain
; - compaction of materials and evetual refills. Price is not inclusive of: - transport of materials resulting non appropriate for backfilling or being excessive; - landfill costs;
precautional cutting of eventual pavment in asphalt or cement, Excavation volume will be calculated on the basis of conventional width defined from defined from crossections and on the basis of pipes row depth increased by tickeness of the layer defined by related crossections.
Price is inclusive of costs related to any section increasement due to terrain caracteristics, presence of water, rocks, materials ets, or provevient by metereological conditions of any type, all in line with professional standards for execution of works. During excavation works workers securuty should be guaranteed related to bank slopes. In the case of eventual risk banks should be protected with following alternative performances: provvisional protections, appropriate wall shoes where major volumes resulting by wall/bank inclination will be compensated on the same price defined by this position.
Digging with excavator till 1,5 m depth
| OUTDOOR AREA - MV/LV RACEWAYS |  | 365
| Total amount |  | 365
CD.C12.A1 |  | m
CUTTING OF ASPHALT PAVING Cutting of asphalt pavin in bitumen performed with apppropriate scraper, saw or disc, calculated in order to perfom cutting activity.
The price should be inclusive of following costs: trackingn of the excavation with appropriate machines, - underground installations controll ; - cutting of surface and binder with appropriate machines; Only if not particularly instructed by DL
just first cut will be calculated, moreover partial profilation is required in odrer to obtain perfect connection between surface and reconstructed part.
Cutting of asphalt paving
| OUTDOOR AREA - MV/LV RACEWAYS |  | 290
| Total amount |  | 290
CD.D10.A1 |  | m3
FILL UP WITH QUARRY MIXTURE Fill up will be performed with crushed stone granulometri 0-30 mm, originated by excavations and resulting appropriate by DL .
Price should be inclusive of following costs: - transport; - meccanical fillinf; - forming of slopes; - compaction; - part for signal band ; - other relevant to perform works in line with professional standards
Fill up with quarry mixture
| OUTDOOR AREA - MV/LV RACEWAYS |  | 205
| Total amount |  | 205
CD.D32.A1 |  | m3
FILL UP WITH SAND Supply and execution of works of filling layers and covering pipes with sand originated from excavations. Price is inclusive of following costs: : - il transport; - filling
; - compacting; - signal band 30 cm under the filled surface; - other relevant to perform works in line with professional standards
Fill up with sand
| OUTDOOR AREA - MV/LV RACEWAYS |  | 115
| Total amount |  | 115
CE.A11.A16 |  | n
PREFABRICATED CONCRETE BOX PREFABRICATED CONCRETE BOX vibrated and armoured with thickeness 6-8 cm for pipes connection. Price is inclusive of: - costs related to hols opening and closing
; - forming of supporting slabs in concrete; - catchment backfilling. Following is excluded from price: - seals; - excavation.
Prefabricated concrete box size 60x60x20cm
| OUTDOOR AREA - MV/LV RACEWAYS |  | 2
| Total amount |  | 2
CE.A11.A2 |  | n
PREFABRICATED CONCRETE BOX PREFABRICATED CONCRETE BOX vibrated and armoured with thickeness 6-8 cm for pipes connection. Price is inclusive of: - costs related to holes opening and closing
; - forming of supporting slabs in concrete; - catchment backfilling. Following is excluded from price Sono esclusi dal prezzo: - seals; - excavation.
Prefabricated concrete box size 40x40x40cm
| OUTDOOR AREA - MV/LV RACEWAYS |  | 31
| OUTDOOR AREA - EARTHING AND LIGHTNING PLANT |  | 7
| Total amount |  | 38
CE.A19.A1 |  | n
WORK FOR CONCRETE BOX UNDERGROUND Forming of concrete underground box of any kind and dimensioor the purpose of network inspections usually situated in location of class B125 e C250 as per
UNI EN 124. Construction caracteristics: - concrete conglomerate with guaranteed performances as per UNI EN 206-1, UNI 11104 in line with DM 14/09/2005 with ambience exposure class XC and caracteristic minimal resistance Rck UNI EN 124
> 25 N/mmq, mechanicaly prepared; - steal armour FeB44k with upgraded adherence controlled by manufacturer and formed in quantities defined by static calculations to be provided by investor .
price is inclusive of : - adjusted alignement with the project ; - forming and removing of tranch sheet ; - mechanical vibration; - forming of holes; - access stairs in plastic steal dimensions
16x33 cm completed by positioning grips d. 25 mm; - backfilling; - other relevant to perform works in line with professional standards .
Price is exclusive of : - pavment works. The price should be understood per m3 full/empty calculated out of the box.
Work for concrete box underground size 150x150x100cm
| OUTDOOR AREA - MV/LV RACEWAYS |  | 9
| Total amount |  | 9
CE.C10.A43 |  | n
CAST IRON COVER Cast iron sferoic cover is composed by fixing chase and cover. In line withUNI EN 124 and tables UNI 4544. Resistance class (depending on type):
B125 with tension density >= 125 kN (12,5t) for sidewalk locations, pedestrian zones occasionaly open for traffic, parking zones and floor garage ; - C250 with tension density >= 250 kN
(25t) for instalation on street sides where lanes to 0,5 m and side walk to 0,2 m sui marciapiedi, quay sides and parking lots for heavy veichles; - D400 with tension density >= 400 kN (4
0t) for trafic lanes (state roads), parking areas for all types of veichels. Construction caracteristics: - quadrate chase form both for basis and extremities provided with: * alett
perimetric continuative exterior wing all over four sides, rounded on angles, non under 20 mm large in order to obtain better anchorage to the base ; * where required, U chase profile in order to limit penetrations
of liquids (hermetic type); * elastomer noise proof and tilt proof gasket, inserted in appropriate space; * fastener zipper blocking the cover in opening position 110^; * place
for positioning closing system; * anti slide shapes on the cover ; - quadrate form cover with: * anti slide shapes; * slot for the key ; *
closure with rotating key ; * supplement able to guarantee mobility of the frame and opening with possibility of cover extraction; * height : from 20 mm for resistance class B125
, 40 mm for resistance class C250, 60mm for D400. Works: - fixing of boxes with cement mortar of at least 2 cm and final sealing all over the chase perimeter; - bullone di messa a terra (se richiesto d
alla DL). Marks: covers shall have a legible and permanent mark which indicates: - compliance with norms UNI EN 124; - indication on the central part of the cover (es. PUBBLIC LIGHTS) to be defined by DL
; - resistance class; - standard and/or manufacter's label; - possible sign of compliance of third authority for certification
Cast iron cover for box 40x40cm, grade C250
| OUTDOOR AREA - MV/LV RACEWAYS |  | 31
| OUTDOOR AREA - EARTHING AND LIGHTNING PLANT |  | 7
| Total amount |  | 38
CE.C10.A45 |  | n
CAST IRON COVER Cast iron sferoic cover is composed by fixing chase and cover. In line withUNI EN 124 and tables UNI 4544. Resistance class (depending on type):
B125 with tension density >= 125 kN (12,5t) for sidewalk locations, pedestrian zones occasionaly open for traffic, parking zones and floor garage ; - C250 with tension density >= 250 kN
(25t) for instalation on street sides where lanes to 0,5 m and side walk to 0,2 m sui marciapiedi, quay sides and parking lots for heavy veichles; - D400 with tension density >= 400 kN (4
0t) for trafic lanes (state roads), parking areas for all types of veichels. Construction caracteristics: - quadrate chase form both for basis and extremities provided with: * alett
perimetric continuative exterior wing all over four sides, rounded on angles, non under 20 mm large in order to obtain better anchorage to the base ; * where required, U chase profile in order to limit penetrations
of liquids (hermetic type); * elastomer noise proof and tilt proof gasket, inserted in appropriate space; * fastener zipper blocking the cover in opening position 110^; * place
for positioning closing system; * anti slide shapes on the cover ; - quadrate form cover with: * anti slide shapes; * slot for the key ; *
closure with rotating key ; * supplement able to guarantee mobility of the frame and opening with possibility of cover extraction; * height : from 20 mm for resistance class B125
, 40 mm for resistance class C250, 60mm for D400. Works: - fixing of boxes with cement mortar of at least 2 cm and final sealing all over the chase perimeter; - bullone di messa a terra (se richiesto d
alla DL). Marks: covers shall have a legible and permanent mark which indicates: - compliance with norms UNI EN 124; - indication on the central part of the cover (es. PUBBLIC LIGHTS) to be defined by DL
; - resistance class; - standard and/or manufacter's label; - possible sign of compliance of third authority for certification
Cast iron cover for box 60x60cm, grade C250
| OUTDOOR AREA - MV/LV RACEWAYS |  | 2
| Total amount |  | 2
CE.C10.C2 |  | n
CAST IRON COVER Cast iron sferoic cover is composed by fixing chase and cover. In line withUNI EN 124 and tables UNI 4544. Resistance class (depending on type):
B125 with tension density >= 125 kN (12,5t) for sidewalk locations, pedestrian zones occasionaly open for traffic, parking zones and floor garage ; - C250 with tension density >= 250 kN
(25t) for instalation on street sides where lanes to 0,5 m and side walk to 0,2 m sui marciapiedi, quay sides and parking lots for heavy veichles; - D400 with tension density >= 400 kN (4
0t) for trafic lanes (state roads), parking areas for all types of veichels. Construction caracteristics: - quadrate chase form both for basis and extremities provided with: * alett
perimetric continuative exterior wing all over four sides, rounded on angles, non under 20 mm large in order to obtain better anchorage to the base ; * where required, U chase profile in order to limit penetrations
of liquids (hermetic type); * elastomer noise proof and tilt proof gasket, inserted in appropriate space; * fastener zipper blocking the cover in opening position 110^; * place
for positioning closing system; * anti slide shapes on the cover ; - quadrate form cover with: * anti slide shapes; * slot for the key ; *
closure with rotating key ; * supplement able to guarantee mobility of the frame and opening with possibility of cover extraction; * height : from 20 mm for resistance class B125
, 40 mm for resistance class C250, 60mm for D400. Works: - fixing of boxes with cement mortar of at least 2 cm and final sealing all over the chase perimeter; - bullone di messa a terra (se richiesto d
alla DL). Marks: covers shall have a legible and permanent mark which indicates: - compliance with norms UNI EN 124; - indication on the central part of the cover (es. PUBBLIC LIGHTS) to be defined by DL
; - resistance class; - standard and/or manufacter's label; - possible sign of compliance of third authority for certification
Cast iron cover for box 150x150cm, grade D400
| OUTDOOR AREA - MV/LV RACEWAYS |  | 9
| Total amount |  | 9
CF.E10.A1 | BINDER | m2
Purchasing, setting and compacting the layer of bitumen, which is stored in the warm, to form the bonding layer, the grain size of 0-25 mm and which is made up of an aggregate obtained by crushing the originally used, is mixed, if possible, with the bitumen.
The price includes compensations and following expenses:
cleaning and later spraying del piano d'appoggio;
guard/safe keeping and signs of security;
everything else necessary to perform the work professionally.
Binder depth 7 cm
| OUTDOOR AREA - MV/LV RACEWAYS |  | 290
| Total amount |  | 290
TOTAL CONDUITS
08 - DISTRIBUTION TERMINAL AND ENERGY SUPPLY CONNECTION POINTS
M10.A10.A1 |  | n
LIGHT SUPPLY EQUIVALENT Light supply composed by: - part of the quote for distribution box installed on the voltage tower, conduits passing from the distribution box to light device (priced appart)
connection box supplying light device (where required). In the case of two different lamps situated in one light device aditional price should be quoted (to equivalent light source) for doubled light source which includes modification or integration of cabbling.
In the case of dimmable light devices aditional price should be chargged (to equivalent light source) which includes modification or integration of cabbling (dimmable reactors and control point included).
Cabling typology should be prescribed by tables and grafics.
Materials forming points shouId have caracteristics indicated in thespecific chapter of this study.
Light supply on wall with flexible PVC pipe and cable
| OUTDOOR AREA - LIGHTING SYSTEM |  | 249
| Total amount |  | 249
M10.A10.A8 |  | n
LIGHT SUPPLY EQUIVALENT Light supply composed by: - part of the quote for distribution box installed on the voltage tower, conduits passing from the distribution box to light device (priced appart)
connection box supplying light device (where required). In the case of two different lamps situated in one light device aditional price should be quoted (to equivalent light source) for doubled light source which includes modification or integration of cabbling.
In the case of dimmable light devices aditional price should be chargged (to equivalent light source) which includes modification or integration of cabbling (dimmable reactors and control switch included).
Cabling typology should be prescribed by tables and grafics.
Materials forming points shouId have caracteristics indicated in thespecific chapter of this study.
Visible light supply with rigid PVC pipe and cable, IP65
| OUTDOOR AREA - LIGHTING SYSTEM |  | 68
| Total amount |  | 68
M20.A10.A32 |  | n
LIGHT CONTROL SWITCH EQUIVALENT Control switch equivalent is composed by: - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks
; - jacks to be inserted in walls, completed, where required, by grips and conduits; - modular control jacks with following caracteristics: SWITCHES, DIVERTERS,
AND BUTTONS * in line with: CEI 23-9 and subsequent variants; * voltage and nominal frequency: 250V c.a., 50Hz; * nominal energy power : 10A for buttons and 16A for switches; * testing voltage: 2000V on 50Hz for 1 min.; *
interuption power: 200 opening and closing movements on 1,25 In, 275V c.a., cosfi'0,3; * functionality testing : 50000 movements on In, 250V c.a., cosfi'0,6; * isolation resistance: >15Mohm a 500V; * signal identification lamp
(where by type required); DIMMERS * voltage and nominal frequency: 230V c.a.+/-10%, 50Hz; * controled power: 60-500W (for resistent resistance); * isolation resistance: >15Mohm on 500V; * regolatione with
rotating command or swith with double function: longer pressure for continual regolation in increasement or decreasement, with electronic memory on release; fast touch for on/of funtion of the lamp on selected level of lighting
; * safety fuse; - jack chase in policarbonat self-extinguishing (UL94-V0) for click instalation and removal with tool, having punctures for screw instalation
with possibility of adjustment in the case of defectouse instalation; - box closures or finishes with covering elements enabling following protection : * at least IP21 (where not specified)
with covers of type selected by D.L. fixed by pressure and removable with tools; * IP55 with closure doors with transparent elastic sheath in silicone gum or similar, resistant to
humidity and water jets, allowing secure functionality of control devices with closed doors; * IP67 with non movable cover and elastic membrain in elastomer anti-age resistant to atmosferic agents
(heat, solar light, low temperatures ecc.), salt e/o acide, alcals, mineral and plant oil, animal oil and fat, carburants and non fire materials, fixed on jack box with stainless steal screws
; - eventually transit boxes.In the case of light signal command aditional price shoud be quoted for equivalent light source. In case of dimmed command
aditional price shoul be quoted fordimmed light source having caracteristics indicated by type. The price should include interior jacks cabbling. Cabbling type should be prescribed by chapter and grafic tables.
Matrials composing control swittch should have caracteristics indicated in the specific chapter of the present study.
Control switch equivalent is composed by: - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks
; - jacks to be inserted in walls, completed, where required, by grips and conduits; - modular control jacks with following caracteristics: SWITCHES, DIVERTERS,
AND BUTTONS * in line with: CEI 23-9 and subsequent variants; * voltage and nominal frequency: 250V c.a., 50Hz; * nominal energy power : 10A for buttons and 16A for switches; * testing voltage: 2000V on 50Hz for 1 min.; *
interuption power: 200 opening and closing movements on 1,25 In, 275V c.a., cosfi'0,3; * functionality testing : 50000 movements on In, 250V c.a., cosfi'0,6; * isolation resistance: >15Mohm a 500V; * signal identification lamp
(where by type required); DIMMERS * voltage and nominal frequency: 230V c.a.+/-10%, 50Hz; * controled power: 60-500W (for resistent resistance); * isolation resistance: >15Mohm on 500V; * regolatione with
rotating command or swith with double function: longer pressure for continual regolation in increasement or decreasement, with electronic memory on release; fast touch for on/of funtion of the lamp on selected level of lighting
; * safety fuse; - jack chase in policarbonat self-extinguishing (UL94-V0) for click instalation and removal with tool, having punctures for screw instalation
with possibility of adjustment in the case of defectouse instalation; - bx closures or finishes with covering elements enabling following protection : * at least IP21 (where not specified)
with covers of type selected by D.L. fixed by pressure and removable with tools; * IP55 with closure doors with transparent elastic sheath in silicone gum or similar, resistant to
humidity and water jets, allowing secure functionality of control devices with closed doors; * IP67 with non movable cover and elastic membrain in elastomer anti-age resistant to atmosferic agents
(heat, solar light, low temperatures ecc.), salt e/o acide, alcals, mineral and plant oil, animal oil and fat, carburants and non fire materials, fixed on jack box with stainless steal screws
; - eventually transit boxes.In the case of light signal command aditional price shoud be quoted for equivalent light source. In case of dimmed command
aditional price shoul be quoted fordimmed light source having caracteristics indicated by type. The price should include interior jacks cabbling. Cabbling type should be prescribed by chapter and grafic tables.
Matrials composing control swittch should have caracteristics indicated in the specific chapter of the present study.
Visible switch or push button switch with rigid PVC pipe and cable - IP55
| OUTDOOR AREA - LIGHTING SYSTEM |  | 1
| Total amount |  | 1
M20.A30.A1 |  | n
EMERGENCY RELEASE PUSHBUTTON Emergency release pushbutton is composed by: - part of the quote for distribution box installed on the voltage tower (where required);; - conduits from pushbutton to release interuprot/s installed
on the main voltage squar or zone voltage square - box in lectro zink and collored in yellow complete by hinged cover, neoprene gasket
eoprene, key lock, glass breaking hammer with chain, breaking glass, sintetic,splinter proof, including release button 6A/380V; - instruction table indicating text as defined by D.L.
Emergency release pushbutton with PVC pipe and cable
| OUTDOOR AREA - LV TERMINAL DISTRIBUTION |  | 2
| Total amount |  | 2
M30.A10.B8 |  | n
POWER SUPPLY Power supply is composed by : - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks (quoted appart)
; - eventualy transit boxes and jack boxes. Type of cabbling should be prescribed by chapter and dimensioned on the basis of efective voltage
used by devices (motored door/tent, cabinets, etc.) . In the case of existing conduits just the price of cabbling shoud be indicated . In the case of supply and instalation
of only conduits and boxes price for preparaty works should be indicated. Used materials should be in line with specific chaapter of present study.
Visible wall installation power supply with PVC rigid pipe and 3x4 cable, IP44
| OUTDOOR AREA - LV TERMINAL DISTRIBUTION |  | 5
| Total amount |  | 5
TOTAL DISTRIBUTION TERMINAL AND ENERGY SUPPLY CONNECTION POINTS
09 - EARTHING AND PROTECTION AGAINST ATMOSFERIC SHOTS
O10.A21.A4 |  | n
INOX STEEL GROUND CROSS PILLAR in line with CEI 11-8(89) and subsequent variations. Caracteristics : - cross profile in heated zinc steal; - klema plate with
clamp for connection to round or flat conduits; - minimal dimensions: 50x50x5 mm.
Inox steel ground pillar D=20mm, L=3m
| OUTDOOR AREA - EARTHING AND LIGHTNING PLANT |  | 7
| Total amount |  | 7
O10.A60.A1 |  | n
COPPER BAR FOR EQUIPOTENTIAL SYSTEM of minimal section.200 mm2 of round edges, with holes for anchoring ground protection conduits trough fasteners fixed on walls of dispensors and supported by two isolators
Copper bar for connection of equipotential cables
| OUTDOOR AREA - EARTHING AND LIGHTNING PLANT |  | 7
| Total amount |  | 7
O20.A10.A14 |  | m
CYLINDER BARE COPPER CABLE in line with CEI 7-1 and subsequent variations; UNI 5649/1. Conductor: rope produced by elementar fibres (n.7 per section from 16 to 50 mmq and n.19 from 70 to 150 mmq of diameatr not
lower than1,8mm) with flat surface, cylindric, row copper or annealed copper type CU-ETP with Cu Ag 99,9%. Accessories: attest and derivation connections of mechanical type (pressure or fastening with screw
or aluminotermic sealing, identification table, eventual eventuali bands and fixing materials, dilatation end expansion joins.
Cylinder bare copper cable 50mm2
| OUTDOOR AREA - EARTHING AND LIGHTNING PLANT |  | 125
| Total amount |  | 125
TOTAL EARTHING AND PROTECTION AGAINST ATMOSFERIC SHOTS
10 - LIGHTING LUMINARIES
P500.A10.A6 |  | globally
LIGHTING LUMINAIRES LAYING Laying works of lighting luminaries (supply excluded) including instalation and other cocts related to complete instalation
Lighting luminaires laying (luminaires not included) on external areas
| OUTDOOR AREA - LIGHTING SYSTEM |  | 1
| Total amount |  | 1
TOTAL LIGHTING LUMINARIES
TOTAL ELECTRICAL - OUTDOOR AREAS
02 | ELECTRICAL PLANTS - UNDERGROUND
01 - CONDUITS, CABLES AND ACCESSORIES
A210.A20.A2 |  | m
H07Z1-K 450/750V CABLE type 2 450/750V IN LINE WITH: CEI 20-22/3, 20-38/1 AND SUBSEQUENT VARIATIONS. Nominal voltage : 450/750 V. Isolation: termoplastic mixture. Conduit: flexible red copper wire
. Fire reaction: - non propagating fire; - low emission of smoke, toxic and corrrosive gases
H07Z1-K 450/750V cable 1x2,5 mmq
| UNDERGROUND LEVEL - MV/LV CABLES |  | 190
| UNDERGROUND LEVEL - MV/LV CABLES - UNIVERSITY |  | 275
| Total amount |  | 465
A210.A20.A3 |  | m
H07Z1-K 450/750V CABLE type 2 450/750V IN LINE WITH: CEI 20-22/3, 20-38/1 AND SUBSEQUENT VARIATIONS. Nominal voltage : 450/750 V. Isolation: termoplastic mixture. Conduit: flexible red copper wire
. Fire reaction: - non propagating fire; - low emission of smoke, toxic and corrrosive gases
H07Z1-K 450/750V cable 1x4 mmq
| UNDERGROUND LEVEL - MV/LV CABLES |  | 35
| UNDERGROUND LEVEL - MV/LV CABLES - UNIVERSITY |  | 175
| Total amount |  | 210
A210.A20.A4 |  | m
H07Z1-K 450/750V CABLE type 2 450/750V IN LINE WITH: CEI 20-22/3, 20-38/1 AND SUBSEQUENT VARIATIONS. Nominal voltage : 450/750 V. Isolation: termoplastic mixture. Conduit: flexible red copper wire
. Fire reaction: - non propagating fire; - low emission of smoke, toxic and corrrosive gases
H07Z1-K 450/750V cable 1x6 mmq
| UNDERGROUND LEVEL - MV/LV CABLES - UNIVERSITY |  | 105
| Total amount |  | 105
A210.A20.A5 |  | m
H07Z1-K 450/750V CABLE type 2 450/750V IN LINE WITH: CEI 20-22/3, 20-38/1 AND SUBSEQUENT VARIATIONS. Nominal voltage : 450/750 V. Isolation: termoplastic mixture. Conduit: flexible red copper wire
. Fire reaction: - non propagating fire; - low emission of smoke, toxic and corrrosive gases
H07Z1-K 450/750V cable 1x10 mmq
| UNDERGROUND LEVEL - MV/LV CABLES |  | 10
| Total amount |  | 10
A210.A20.A6 |  | m
H07Z1-K 450/750V CABLE type 2 450/750V IN LINE WITH: CEI 20-22/3, 20-38/1 AND SUBSEQUENT VARIATIONS. Nominal voltage : 450/750 V. Isolation: termoplastic mixture. Conduit: flexible red copper wire
. Fire reaction: - non propagating fire; - low emission of smoke, toxic and corrrosive gases
H07Z1-K 450/750V cable 1x16 mmq
| UNDERGROUND LEVEL - MV/LV CABLES |  | 20
| Total amount |  | 20
A220.A20.A11 |  | m
FG7M1 0,6/1kV, FG7OM1 0,6/1kV CABLE CAVO FG7M1 0,6/1kV, FG7OM1 0,6/1kV In line with: CEI 20-13, 20-22/3 and subsequent variations. In line with tables : CEI-UNEL 35382, 35384. Nominal voltage: 600/1000 V. Isolation
: etilen-propilenic gum type G7. Sheath: special termoplastic polimer quality M1. Filler: non vulcanizzed gum. Conduit: flexible coated copper wire. Protection Cover (if required): coper wires network. Fire reaction
: - non propagating fire; - low emission of smoke, toxic and corrrosive gases
FG7M1 0,6/1kV cable 1x95 mmq
| UNDERGROUND LEVEL - MV/LV CABLES - UNIVERSITY |  | 30
| Total amount |  | 30
A220.A20.A31 |  | m
FG7M1 0,6/1kV, FG7OM1 0,6/1kV CABLE CAVO FG7M1 0,6/1kV, FG7OM1 0,6/1kV In line with: CEI 20-13, 20-22/3 and subsequent variations. In line with tables : CEI-UNEL 35382, 35384. Nominal voltage: 600/1000 V. Isolation
: etilen-propilenic gum type G7. Sheath: special termoplastic polimer quality M1. Filler: non vulcanizzed gum. Conduit: flexible coated copper wire. Protection Cover (if required): coper wires network. Fire reaction
: - non propagating fire; - low emission of smoke, toxic and corrrosive gases
FG7OM1 0,6/1kV cable 3x2,5 mmq
| UNDERGROUND LEVEL - MV/LV CABLES |  | 455
| Total amount |  | 455
A220.A20.A32 |  | m
FG7M1 0,6/1kV, FG7OM1 0,6/1kV CABLE CAVO FG7M1 0,6/1kV, FG7OM1 0,6/1kV In line with: CEI 20-13, 20-22/3 and subsequent variations. In line with tables : CEI-UNEL 35382, 35384. Nominal voltage: 600/1000 V. Isolation
: etilen-propilenic gum type G7. Sheath: special termoplastic polimer quality M1. Filler: non vulcanizzed gum. Conduit: flexible coated copper wire. Protection Cover (if required): coper wires network. Fire reaction
: - non propagating fire; - low emission of smoke, toxic and corrrosive gases
FG7OM1 0,6/1kV cable 3x4 mmq
| UNDERGROUND LEVEL - MV/LV CABLES |  | 775
| Total amount |  | 775
A220.A20.A33 |  | m
FG7M1 0,6/1kV, FG7OM1 0,6/1kV CABLE CAVO FG7M1 0,6/1kV, FG7OM1 0,6/1kV In line with: CEI 20-13, 20-22/3 and subsequent variations. In line with tables : CEI-UNEL 35382, 35384. Nominal voltage: 600/1000 V. Isolation
: etilen-propilenic gum type G7. Sheath: special termoplastic polimer quality M1. Filler: non vulcanizzed gum. Conduit: flexible coated copper wire. Protection Cover (if required): coper wires network. Fire reaction
: - non propagating fire; - low emission of smoke, toxic and corrrosive gases
FG7OM1 0,6/1kV cable 3x6 mmq
| UNDERGROUND LEVEL - MV/LV CABLES |  | 160
| Total amount |  | 160
A220.A20.A63 |  | m
FG7M1 0,6/1kV, FG7OM1 0,6/1kV CABLE CAVO FG7M1 0,6/1kV, FG7OM1 0,6/1kV In line with: CEI 20-13, 20-22/3 and subsequent variations. In line with tables : CEI-UNEL 35382, 35384. Nominal voltage: 600/1000 V. Isolation
: etilen-propilenic gum type G7. Sheath: special termoplastic polimer quality M1. Filler: non vulcanizzed gum. Conduit: flexible coated copper wire. Protection Cover (if required): coper wires network. Fire reaction
: - non propagating fire; - low emission of smoke, toxic and corrrosive gases
FG7OM1 0,6/1kV cable 5x6 mmq
| UNDERGROUND LEVEL - MV/LV CABLES |  | 200
| Total amount |  | 200
A220.A20.A65 |  | m
FG7M1 0,6/1kV, FG7OM1 0,6/1kV CABLE CAVO FG7M1 0,6/1kV, FG7OM1 0,6/1kV In line with: CEI 20-13, 20-22/3 and subsequent variations. In line with tables : CEI-UNEL 35382, 35384. Nominal voltage: 600/1000 V. Isolation
: etilen-propilenic gum type G7. Sheath: special termoplastic polimer quality M1. Filler: non vulcanizzed gum. Conduit: flexible coated copper wire. Protection Cover (if required): coper wires network. Fire reaction
: - non propagating fire; - low emission of smoke, toxic and corrrosive gases
FG7OM1 0,6/1kV cable 5x16 mmq
| UNDERGROUND LEVEL - MV/LV CABLES |  | 70
| Total amount |  | 70
A230.A10.A32 |  | m
FTG10M1 0,6/1kV CEI 20-45 FIRE RESISTANCE CABLE CAVO FTG10M1 0,6/1kV CEI 20-45, FTG10OM1 0,6/1kV CEI 20-45 In line with: CEI 20-22/3, 20-38, 20-45 and subsequent variations ; EN50200. Nominal voltage: 600/1000 V. Isolation
: etilenpropilenic gum mixture qualitay G10. Sheath : special termoplastic polimer quality M1. Filler: non toxic gum . Conduit: flexible wire of coated copper coated with fire resistance tape. Fire reaction:
non propagating fire; - low emission of smoke, toxic and corrrosive gases; - continuous work of minimum 180 minutes on the temperature 750°C in the presence of mechanical shock on every 5 min.
FTG10OM1 0,6/1kV CEI 20-45 fire resistance cable 3x2,5 mmq
| UNDERGROUND LEVEL - MV/LV CABLES |  | 725
| Total amount |  | 725
A230.A10.A33 |  | m
FTG10M1 0,6/1kV CEI 20-45 FIRE RESISTANCE CABLE CAVO FTG10M1 0,6/1kV CEI 20-45, FTG10OM1 0,6/1kV CEI 20-45 In line with: CEI 20-22/3, 20-38, 20-45 and subsequent variations ; EN50200. Nominal voltage: 600/1000 V. Isolation
: etilenpropilenic gum mixture qualitay G10. Sheath : special termoplastic polimer quality M1. Filler: non toxic gum . Conduit: flexible wire of coated copper coated with fire resistance tape. Fire reaction:
non propagating fire; - low emission of smoke, toxic and corrrosive gases; - continuous work of minimum 180 minutes on the temperature 750°C in the presence of mechanical shock on every 5 min.
FTG10OM1 0,6/1kV CEI 20-45 fire resistance cable 3x4 mmq
| UNDERGROUND LEVEL - MV/LV CABLES |  | 115
| Total amount |  | 115
A250.A10.A1 |  | m
BARE COPPER CABLE CORDA DI RAME In line with: CEI 7-1 and subsequent variations; UNI 5649/1. Conduit: Wire with basic fibres (n.7 for positions from 16 to 50 mmq and n.19 from 70 to 150 mmq with diameter non under
1,8mm) flat surface, cylindric, raw copper or annealed type CU-ETP with Cu Ag 99,9%.
Bare copper cable 16mmq
| UNDERGROUND LEVEL - MV/LV CABLES |  | 200
| Total amount |  | 200
TOTAL CONDUITS, CABLES AND ACCESSORIES
02 - CONDUITS
B10.A10.A2 |  | m
METAL TRUNKING IN CLOSED VERSION, ZINC PLATED PASSERELLA PORTACAVI IN ACCIAIO ZINCATO A CALDO PER IMMERSIONE DOPO LA LAVORAZIONE in line with: CEI 23-76, CEI 7-6 and subsequent variations . Shock resistance: > 1J on ambience temperature
(20°C ±5). Meccanical resistance: minimal acceptable load (values measured for maximal deformation curve of 1/200 of intermediate load, junction on 1/5 between suporters) measured in line with norms of the product : - closed channel with h. 75mm
, Light between two suporters 1,5m: * 145 kg/m for channel width 50-75 mm; * 149 kg/m for channel width 100 mm; * 158 kg/m for channel width 150 mm; * 165 kg/m for channel width 200 mm; * 204 kg/m for channel width 3
00 mm; * 208 kg/m for channel width 400 mm; * 214 kg/m for channel width 500-600 mm; - punctured channel with h. 75mm, light between two supporters 1,5m: * 145 kg/m for channel width 50-75 mm; * 156 kg/m for channel width 100 mm
; * 170 kg/m for channel width150 mm; * 190 kg/m for channel width 200-300 mm; * 201 kg/m for channel width 400 mm; * 208 kg/m for channel width 500 mm; * 217 kg/m for channel width 600 mm. Electrical caracteristics
: - electric Continuity garantita guaranteed by manufacturer with lectrical reistance (on 12V c.a. max 50Hz, 25A): =< 0,005 ohm per meter and e <= 0,05 ohm in proximity of junctio. Construction caracteristics: - chase composed by one piece of perfored sheet
closed depending on type, with boarded angles or anti cut reinforced produced by rolling and zinced on fire after production with zinc Zn A 99,90%; - thickeness of the sheet: min.0,8 mm (untill 150x75) and
1 mm and over (for bigger production); - medium thickeness of zinc surface: 57 micron +/-10% for single face ; - medium mass of zinc surface: 400 g/m2 +/-10% for single face; - cover (when required) in zinced steal
with same treatment and construction caracteristics s.d., click closure or trough connected grips. Protection level (in case of trunking with full bottom/closed with cover): min. IP30, for the entire system.
Zinc plated metal trunking, perforated base, size 100x75mm
| UNDERGROUND LEVEL - MV/LV RACEWAYS |  | 256
| Total amount |  | 256
B10.A10.A22 |  | m
METAL TRUNKING IN CLOSED VERSION, ZINC PLATED PASSERELLA PORTACAVI IN ACCIAIO ZINCATO A CALDO PER IMMERSIONE DOPO LA LAVORAZIONE in line with: CEI 23-76, CEI 7-6 and subsequent variations . Shock resistance: > 1J on ambience temperature
(20°C ±5). Meccanical resistance: minimal acceptable load (values measured for maximal deformation curve of 1/200 of intermediate load, junction on 1/5 between suporters) measured in line with norms of the product : - closed channel with h. 75mm
, Light between two suporters 1,5m: * 145 kg/m for channel width 50-75 mm; * 149 kg/m for channel width 100 mm; * 158 kg/m for channel width 150 mm; * 165 kg/m for channel width 200 mm; * 204 kg/m for channel width 3
00 mm; * 208 kg/m for channel width 400 mm; * 214 kg/m for channel width 500-600 mm; - punctured channel with h. 75mm, light between two supporters 1,5m: * 145 kg/m for channel width 50-75 mm; * 156 kg/m for channel width 100 mm
; * 170 kg/m for channel width150 mm; * 190 kg/m for channel width 200-300 mm; * 201 kg/m for channel width 400 mm; * 208 kg/m for channel width 500 mm; * 217 kg/m for channel width 600 mm. Electrical caracteristics
: - electric Continuity garantita guaranteed by manufacturer with lectrical reistance (on 12V c.a. max 50Hz, 25A): =< 0,005 ohm per meter and e <= 0,05 ohm in proximity of junctio. Construction caracteristics: - chase composed by one piece of perfored sheet
closed depending on type, with boarded angles or anti cut reinforced produced by rolling and zinced on fire after production with zinc Zn A 99,90%; - thickeness of the sheet: min.0,8 mm (untill 150x75) and
1 mm and over (for bigger production); - medium thickeness of zinc surface: 57 micron +/-10% for single face ; - medium mass of zinc surface: 400 g/m2 +/-10% for single face; - cover (when required) in zinced steal
with same treatment and construction caracteristics s.d., click closure or trough connected grips. Protection level (in case of trunking with full bottom/closed with cover): min. IP30, for the entire system.
Metal trunking cover 100 mm
| UNDERGROUND LEVEL - MV/LV RACEWAYS |  | 256
| Total amount |  | 256
B10.A10.A24 |  | m
METAL TRUNKING IN CLOSED VERSION, ZINC PLATED PASSERELLA PORTACAVI IN ACCIAIO ZINCATO A CALDO PER IMMERSIONE DOPO LA LAVORAZIONE in line with: CEI 23-76, CEI 7-6 and subsequent variations . Shock resistance: > 1J on ambience temperature
(20°C ±5). Meccanical resistance: minimal acceptable load (values measured for maximal deformation curve of 1/200 of intermediate load, junction on 1/5 between suporters) measured in line with norms of the product : - closed channel with h. 75mm
, Light between two suporters 1,5m: * 145 kg/m for channel width 50-75 mm; * 149 kg/m for channel width 100 mm; * 158 kg/m for channel width 150 mm; * 165 kg/m for channel width 200 mm; * 204 kg/m for channel width 3
00 mm; * 208 kg/m for channel width 400 mm; * 214 kg/m for channel width 500-600 mm; - punctured channel with h. 75mm, light between two supporters 1,5m: * 145 kg/m for channel width 50-75 mm; * 156 kg/m for channel width 100 mm
; * 170 kg/m for channel width150 mm; * 190 kg/m for channel width 200-300 mm; * 201 kg/m for channel width 400 mm; * 208 kg/m for channel width 500 mm; * 217 kg/m for channel width 600 mm. Electrical caracteristics
: - electric Continuity garantita guaranteed by manufacturer with lectrical reistance (on 12V c.a. max 50Hz, 25A): =< 0,005 ohm per meter and e <= 0,05 ohm in proximity of junctio. Construction caracteristics: - chase composed by one piece of perfored sheet
closed depending on type, with boarded angles or anti cut reinforced produced by rolling and zinced on fire after production with zinc Zn A 99,90%; - thickeness of the sheet: min.0,8 mm (untill 150x75) and
1 mm and over (for bigger production); - medium thickeness of zinc surface: 57 micron +/-10% for single face ; - medium mass of zinc surface: 400 g/m2 +/-10% for single face; - cover (when required) in zinced steal
with same treatment and construction caracteristics s.d., click closure or trough connected grips. Protection level (in case of trunking with full bottom/closed with cover): min. IP30, for the entire system.
Metal trunking cover 200 mm
| UNDERGROUND LEVEL - MV/LV RACEWAYS |  | 170
| Total amount |  | 170
B10.A10.A4 |  | m
METAL TRUNKING IN CLOSED VERSION, ZINC PLATED PASSERELLA PORTACAVI IN ACCIAIO ZINCATO A CALDO PER IMMERSIONE DOPO LA LAVORAZIONE in line with: CEI 23-76, CEI 7-6 and subsequent variations . Shock resistance: > 1J on ambience temperature
(20°C ±5). Meccanical resistance: minimal acceptable load (values measured for maximal deformation curve of 1/200 of intermediate load, junction on 1/5 between suporters) measured in line with norms of the product : - closed channel with h. 75mm
, Light between two suporters 1,5m: * 145 kg/m for channel width 50-75 mm; * 149 kg/m for channel width 100 mm; * 158 kg/m for channel width 150 mm; * 165 kg/m for channel width 200 mm; * 204 kg/m for channel width 3
00 mm; * 208 kg/m for channel width 400 mm; * 214 kg/m for channel width 500-600 mm; - punctured channel with h. 75mm, light between two supporters 1,5m: * 145 kg/m for channel width 50-75 mm; * 156 kg/m for channel width 100 mm
; * 170 kg/m for channel width150 mm; * 190 kg/m for channel width 200-300 mm; * 201 kg/m for channel width 400 mm; * 208 kg/m for channel width 500 mm; * 217 kg/m for channel width 600 mm. Electrical caracteristics
: - electric Continuity garantita guaranteed by manufacturer with lectrical reistance (on 12V c.a. max 50Hz, 25A): =< 0,005 ohm per meter and e <= 0,05 ohm in proximity of junctio. Construction caracteristics: - chase composed by one piece of perfored sheet
closed depending on type, with boarded angles or anti cut reinforced produced by rolling and zinced on fire after production with zinc Zn A 99,90%; - thickeness of the sheet: min.0,8 mm (untill 150x75) and
1 mm and over (for bigger production); - medium thickeness of zinc surface: 57 micron +/-10% for single face ; - medium mass of zinc surface: 400 g/m2 +/-10% for single face; - cover (when required) in zinced steal
with same treatment and construction caracteristics s.d., click closure or trough connected grips. Protection level (in case of trunking with full bottom/closed with cover): min. IP30, for the entire system.
Zinc plated metal trunking, perforated base, size 200x75mm
| UNDERGROUND LEVEL - MV/LV RACEWAYS |  | 170
| Total amount |  | 170
B10.A40.A14 |  | m
ZINC PLATED WIRE MESH PASSERELLA PORTACAVI A RETE IN FILO DI ACCIAIO ZINCATO A CALDO PER IMMERSIONE DOPO LA LAVORAZIONE
Compliance with standards: CEI 23-76, CEI 7-6 and subsequent variations.
Impact resistance: > 1J on room temperature (20°C ±5).
Mechanical resistance: minimum allowed load (values ​​measured for maximum arrow 1/200 medium capacity, the composition at 1/5 of the opening) measured in accordance with the appropriate performance standards:
_constructions with h. 50 mm, light between two brackets 1,5m;
* 18 kg/m for channels wide 50-100 mm;
* 27 kg/m for channels wide 150 mm;
* 33 kg/m for channels wide 200 mm;
* 63 kg/m for channels wide 300 mm;
* 104 kg/m for channels wide 400 mm;
* 120 kg/m for channels wide 500-600 mm;
constructions with h. 100mm, light between two supporters 1,5m:
* 37 kg/m for channels wide 100 mm;
* 53 kg/m for channels wide 150 mm;
* 73 kg/m for channels wide 200 mm;
* 104 kg/m for channels wide 300-400 mm; * 125 kg/m for channels wide 500-600 mm.
Electrical characteristics:
_ electric continuity guaranteed by the constructor with the electrical resistance (at 12V max ca 50Hz, 25A) = <0.005 ohm per meter <= 0.05 ohm nearby compound.
Structural characteristics:
_structure is made of welded steel wire, hot-dipped galvanized for drowning after treatment with prior degreasing and pickling, and the final painting (for types that are required) epoxy resin or polyester;
_ safety edge without parts that contain sharp edges;
_ minimum mass of zink layer: 330 g/m2 +/-10%;
_ average thickness of zink layer: 50 micron +/- 10%.
_ cover (when required) of galvanized steel with the same treatment and structural characteristics of s.d., with the closure with the latch, i.e. by hook that can not be lost.
Behavior on the fire collored (upon request) autoestingueting.
Zinc plated wire mesh, size 200x105mm
| UNDERGROUND LEVEL - MV/LV RACEWAYS |  | 20
| Total amount |  | 20
B10.A40.A15 |  | m
ZINC PLATED WIRE MESH PASSERELLA PORTACAVI A RETE IN FILO DI ACCIAIO ZINCATO A CALDO PER IMMERSIONE DOPO LA LAVORAZIONE
Compliance with standards: CEI 23-76, CEI 7-6 and subsequent variations.
Impact resistance: > 1J on room temperature (20°C ±5).
Mechanical resistance: minimum allowed load (values ​​measured for maximum arrow 1/200 medium capacity, the composition at 1/5 of the opening) measured in accordance with the appropriate performance standards:
_constructions with h. 50 mm, light between two brackets 1,5m;
* 18 kg/m for channels wide 50-100 mm;
* 27 kg/m for channels wide 150 mm;
* 33 kg/m for channels wide 200 mm;
* 63 kg/m for channels wide 300 mm;
* 104 kg/m for channels wide 400 mm;
* 120 kg/m for channels wide 500-600 mm;
constructions with h. 100mm, light between two supporters 1,5m:
* 37 kg/m for channels wide 100 mm;
* 53 kg/m for channels wide 150 mm;
* 73 kg/m for channels wide 200 mm;
* 104 kg/m for channels wide 300-400 mm; * 125 kg/m for channels wide 500-600 mm.
Electrical characteristics:
_ electric continuity guaranteed by the constructor with the electrical resistance (at 12V max ca 50Hz, 25A) = <0.005 ohm per meter <= 0.05 ohm nearby compound.
Structural characteristics:
_structure is made of welded steel wire, hot-dipped galvanized for drowning after treatment with prior degreasing and pickling, and the final painting (for types that are required) epoxy resin or polyester;
_ safety edge without parts that contain sharp edges;
_ minimum mass of zink layer: 330 g/m2 +/-10%;
_ average thickness of zink layer: 50 micron +/- 10%.
_ cover (when required) of galvanized steel with the same treatment and structural characteristics of s.d., with the closure with the latch, i.e. by hook that can not be lost.
Behavior on the fire collored (upon request) autoestingueting.
Zinc plated wire mesh, size 300x105mm
| UNDERGROUND LEVEL - MV/LV RACEWAYS |  | 20
| Total amount |  | 20
B10.A40.A2 |  | m
ZINC PLATED WIRE MESH PASSERELLA PORTACAVI A RETE IN FILO DI ACCIAIO ZINCATO A CALDO PER IMMERSIONE DOPO LA LAVORAZIONE
Compliance with standards: CEI 23-76, CEI 7-6 and subsequent variations.
Impact resistance: > 1J on room temperature (20°C ±5).
Mechanical resistance: minimum allowed load (values ​​measured for maximum arrow 1/200 medium capacity, the composition at 1/5 of the opening) measured in accordance with the appropriate performance standards:
_constructions with h. 50 mm, light between two brackets 1,5m;
* 18 kg/m for channels wide 50-100 mm;
* 27 kg/m for channels wide 150 mm;
* 33 kg/m for channels wide 200 mm;
* 63 kg/m for channels wide 300 mm;
* 104 kg/m for channels wide 400 mm;
* 120 kg/m for channels wide 500-600 mm;
constructions with h. 100mm, light between two supporters 1,5m:
* 37 kg/m for channels wide 100 mm;
* 53 kg/m for channels wide 150 mm;
* 73 kg/m for channels wide 200 mm;
* 104 kg/m for channels wide 300-400 mm; * 125 kg/m for channels wide 500-600 mm.
Electrical characteristics:
_ electric continuity guaranteed by the constructor with the electrical resistance (at 12V max ca 50Hz, 25A) = <0.005 ohm per meter <= 0.05 ohm nearby compound.
Structural characteristics:
_structure is made of welded steel wire, hot-dipped galvanized for drowning after treatment with prior degreasing and pickling, and the final painting (for types that are required) epoxy resin or polyester;
_ safety edge without parts that contain sharp edges;
_ minimum mass of zink layer: 330 g/m2 +/-10%;
_ average thickness of zink layer: 50 micron +/- 10%.
_ cover (when required) of galvanized steel with the same treatment and structural characteristics of s.d., with the closure with the latch, i.e. by hook that can not be lost.
Behavior on the fire collored (upon request) autoestingueting.
Zinc plated wire mesh, size 100x55mm
| UNDERGROUND LEVEL - MV/LV RACEWAYS |  | 15
| Total amount |  | 15
B10.A40.A4 |  | m
ZINC PLATED WIRE MESH PASSERELLA PORTACAVI A RETE IN FILO DI ACCIAIO ZINCATO A CALDO PER IMMERSIONE DOPO LA LAVORAZIONE
Compliance with standards: CEI 23-76, CEI 7-6 and subsequent variations.
Impact resistance: > 1J on room temperature (20°C ±5).
Mechanical resistance: minimum allowed load (values ​​measured for maximum arrow 1/200 medium capacity, the composition at 1/5 of the opening) measured in accordance with the appropriate performance standards:
_constructions with h. 50 mm, light between two brackets 1,5m;
* 18 kg/m for channels wide 50-100 mm;
* 27 kg/m for channels wide 150 mm;
* 33 kg/m for channels wide 200 mm;
* 63 kg/m for channels wide 300 mm;
* 104 kg/m for channels wide 400 mm;
* 120 kg/m for channels wide 500-600 mm;
constructions with h. 100mm, light between two supporters 1,5m:
* 37 kg/m for channels wide 100 mm;
* 53 kg/m for channels wide 150 mm;
* 73 kg/m for channels wide 200 mm;
* 104 kg/m for channels wide 300-400 mm; * 125 kg/m for channels wide 500-600 mm.
Electrical characteristics:
_ electric continuity guaranteed by the constructor with the electrical resistance (at 12V max ca 50Hz, 25A) = <0.005 ohm per meter <= 0.05 ohm nearby compound.
Structural characteristics:
_structure is made of welded steel wire, hot-dipped galvanized for drowning after treatment with prior degreasing and pickling, and the final painting (for types that are required) epoxy resin or polyester;
_ safety edge without parts that contain sharp edges;
_ minimum mass of zink layer: 330 g/m2 +/-10%;
_ average thickness of zink layer: 50 micron +/- 10%.
_ cover (when required) of galvanized steel with the same treatment and structural characteristics of s.d., with the closure with the latch, i.e. by hook that can not be lost.
Behavior on the fire collored (upon request) autoestingueting.
Zinc plated wire mesh, size 200x55mm
| UNDERGROUND LEVEL - MV/LV RACEWAYS |  | 3
| Total amount |  | 3
B20.A30.A17 |  | m
PVC WALL MOUNTING RACEWAY CANALE IN PVC PER POSA CAVI E PER CONTENIMENTO APPARECCHI TERMINALI (CANALE IN PVC ATTREZZATO) In line with: CEI 23-58, 23-32 and subsequent variations (wall mounting raceway canal for cables and devices), 23-19 and subsequent variations
(distribution system on wall protectors). Caracteristics: - el. density: >= 60 kV/mm; - surface resistance. 10 esp. 13 ohm. Protection level: non under IP40 if not diferently indicated by type. Construction caracteristics
: - PVC chase closed, produced with estrusion, one or more sections in order to have separation of different systems; - collor to be selected by DL; - click cover in PVC; - possibility to contain boxes in raceway
; - covers with indicated perforations of dimensions appropriate for devices. Type of instalation: on wall. Fire reaction: autoestingeting. Testing temparure on incandenscent wire
: >= 850°C. Price should include: - losses and scart; - accessories for: * junction; * closure of endings; * horizontal and vertical change of direction; * cables and sections fixing ; *
flange entrance in boxes; - cover and appropriate accessories; - screws, nails etc.. Price is not inclusive of : - section separators (quoted apart if required). .
Divider for PVC raceway, height 40 mm
| UNDERGROUND LEVEL - MV/LV RACEWAYS |  | 25.4
| Total amount |  | 25.4
B20.A30.A5 |  | m
PVC WALL MOUNTING RACEWAY CANALE IN PVC PER POSA CAVI E PER CONTENIMENTO APPARECCHI TERMINALI (CANALE IN PVC ATTREZZATO) In line with: CEI 23-58, 23-32 and subsequent variations (wall mounting raceway canal for cables and devices), 23-19 and subsequent variations
(distribution system on wall protectors). Caracteristics: - el. density: >= 60 kV/mm; - surface resistance. 10 esp. 13 ohm. Protection level: non under IP40 if not diferently indicated by type. Construction caracteristics
: - PVC chase closed, produced with estrusion, one or more sections in order to have separation of different systems; - collor to be selected by DL; - click cover in PVC; - possibility to contain boxes in raceway
; - covers with indicated perforations of dimensions appropriate for devices. Type of instalation: on wall. Fire reaction: autoestingeting. Testing temparure on incandenscent wire
: >= 850°C. Price should include: - losses and scart; - accessories for: * junction; * closure of endings; * horizontal and vertical change of direction; * cables and sections fixing ; *
flange entrance in boxes; - cover and appropriate accessories; - screws, nails etc.. Price is not inclusive of : - section separators (quoted apart if required). .
PVC wall mounting raceway to equip with sockets, size 100x40 mm
| UNDERGROUND LEVEL - MV/LV RACEWAYS |  | 25.4
| Total amount |  | 25.4
B30.A10.A3 |  | m
PVC FLEXIBLE PIPE TUBO PROTETTIVO PIEGHEVOLE - CORRUGATO IN PVC PER POSA SOTTO TRACCIA In line with : CEI 23-82, 23-39 and subsequent variations. Classification: non under 3321. Crush resistance: >= 750N.
shock resistance: >= 2J. Electrical isolation resistance: >= 100Mohm a 500V for 1 min. Dielectric densisty: >= 2kV/mm a 50Hz for 15 min. Fire reaction : non propagating fire. System protection level: min. IP4X.
PVC flexible pipe D=25mm
| UNDERGROUND LEVEL - MV/LV RACEWAYS |  | 291
| Total amount |  | 291
B30.A10.A5 |  | m
PVC FLEXIBLE PIPE TUBO PROTETTIVO PIEGHEVOLE - CORRUGATO IN PVC PER POSA SOTTO TRACCIA In line with : CEI 23-82, 23-39 and subsequent variations. Classification: non under 3321. Crush resistance: >= 750N.
shock resistance: >= 2J. Electrical isolation resistance: >= 100Mohm a 500V for 1 min. Dielectric densisty: >= 2kV/mm a 50Hz for 15 min. Fire reaction : non propagating fire. System protection level: min. IP4X.
PVC flexible pipe D=40mm
| UNDERGROUND LEVEL - MV/LV RACEWAYS |  | 20
| Total amount |  | 20
B30.A20.A25 |  | m
PVC RIGID PIPE TUBO PROTETTIVO RIGIDO MEDIO IN PVC PER POSA IN VISTA O SOTTOTRACCIA In line with: 23-51, 23-54 and subsequent variations. In line with tables: CEI-UNEL 37118, 37119, 37120. Classification: non under3321. Crush resistance
: >= 750N. Shock resistance: >= 2J. Electrical isolation resistance: >= 100Mohm a 500V for 1 min. Dielectrical density: >= 2kV/mm on 50Hz for 15 min. Fire reaction : non propagating fire; - low content of alogen gasses
(as by CEI 20-37). System protection level: indicated by type
PVC rigid pipe IP65 D=40mm
| UNDERGROUND LEVEL - MV/LV RACEWAYS |  | 422
| Total amount |  | 422
B50.A20.A8 |  | m
PEHD FLEXIBLE PIPE TO BURY TUBO PROTETTIVO PIEGHEVOLE IN POLIETILENE AD ALTA DENSITA' PER POSA INTERRATA In line with: CEI 23-39, 23-46 and subsequent variations. Classification: non under 3441. Crush resistance: >=
450N. Shock resistance: >= 6J. Electrical isolation resistance: >= 100Mohm. Dielectrical density: >= 20kV/mm. Resistance on chimical agents and microorganisms. Construction caractersitics: - polietilene tube with high density
(PEHD), with double flat wall entirely corrugated on exterior part; - more elements conjunction handle. System protection level: min. IP4X.
PEHD flexible pipe D=160mm
| UNDERGROUND LEVEL - MV/LV RACEWAYS |  | 1120
| UNDERGROUND LEVEL - MV/LV RACEWAYS - UNIVERSITY |  | 80
| Total amount |  | 1200
CE.A11.A4 |  | n
PREFABRICATED CONCRETE BOX PREFABRICATED CONCRETE BOX vibrated and armoured with thickeness 6-8 cm for pipes connection. Price is inclusive of: - costs related to holes opening and closing
; - forming of supporting slabs in concrete; - catchment backfilling. Following is excluded from price Sono esclusi dal prezzo: - seals; - excavation.
Prefabricated concrete box size 60x60x60cm
| UNDERGROUND LEVEL - MV/LV RACEWAYS |  | 14
| Total amount |  | 14
CE.A11.A8 |  | n
PREFABRICATED CONCRETE BOX PREFABRICATED CONCRETE BOX vibrated and armoured with thickeness 6-8 cm for pipes connection. Price is inclusive of: - costs related to holes opening and closing
; - forming of supporting slabs in concrete; - catchment backfilling. Following is excluded from price Sono esclusi dal prezzo: - seals; - excavation.
Prefabricated concrete box size 100x100x100cm
| UNDERGROUND LEVEL - MV/LV RACEWAYS |  | 2
| Total amount |  | 2
CE.C10.A45 |  | n
CAST IRON COVER Cast iron sferoic cover is composed by fixing chase and cover. In line withUNI EN 124 and tables UNI 4544. Resistance class (depending on type):
B125 with tension density >= 125 kN (12,5t) for sidewalk locations, pedestrian zones occasionaly open for traffic, parking zones and floor garage ; - C250 with tension density >= 250 kN
(25t) for instalation on street sides where lanes to 0,5 m and side walk to 0,2 m sui marciapiedi, quay sides and parking lots for heavy veichles; - D400 with tension density >= 400 kN (4
0t) for trafic lanes (state roads), parking areas for all types of veichels. Construction caracteristics: - quadrate chase form both for basis and extremities provided with: * alett
perimetric continuative exterior wing all over four sides, rounded on angles, non under 20 mm large in order to obtain better anchorage to the base ; * where required, U chase profile in order to limit penetrations
of liquids (hermetic type); * elastomer noise proof and tilt proof gasket, inserted in appropriate space; * fastener zipper blocking the cover in opening position 110^; * place
for positioning closing system; * anti slide shapes on the cover ; - quadrate form cover with: * anti slide shapes; * slot for the key ; *
closure with rotating key ; * supplement able to guarantee mobility of the frame and opening with possibility of cover extraction; * height : from 20 mm for resistance class B125
, 40 mm for resistance class C250, 60mm for D400. Works: - fixing of boxes with cement mortar of at least 2 cm and final sealing all over the chase perimeter; - bullone di messa a terra (se richiesto d
alla DL). Marks: covers shall have a legible and permanent mark which indicates: - compliance with norms UNI EN 124; - indication on the central part of the cover (es. PUBBLIC LIGHTS) to be defined by DL
; - resistance class; - standard and/or manufacter's label; - possible sign of compliance of third authority for certification
Cast iron cover for box 60x60cm, grade C250
| UNDERGROUND LEVEL - MV/LV RACEWAYS |  | 14
| Total amount |  | 14
CE.C10.C1 |  | n
CAST IRON COVER Cast iron sferoic cover is composed by fixing chase and cover. In line withUNI EN 124 and tables UNI 4544. Resistance class (depending on type):
B125 with tension density >= 125 kN (12,5t) for sidewalk locations, pedestrian zones occasionaly open for traffic, parking zones and floor garage ; - C250 with tension density >= 250 kN
(25t) for instalation on street sides where lanes to 0,5 m and side walk to 0,2 m sui marciapiedi, quay sides and parking lots for heavy veichles; - D400 with tension density >= 400 kN (4
0t) for trafic lanes (state roads), parking areas for all types of veichels. Construction caracteristics: - quadrate chase form both for basis and extremities provided with: * alett
perimetric continuative exterior wing all over four sides, rounded on angles, non under 20 mm large in order to obtain better anchorage to the base ; * where required, U chase profile in order to limit penetrations
of liquids (hermetic type); * elastomer noise proof and tilt proof gasket, inserted in appropriate space; * fastener zipper blocking the cover in opening position 110^; * place
for positioning closing system; * anti slide shapes on the cover ; - quadrate form cover with: * anti slide shapes; * slot for the key ; *
closure with rotating key ; * supplement able to guarantee mobility of the frame and opening with possibility of cover extraction; * height : from 20 mm for resistance class B125
, 40 mm for resistance class C250, 60mm for D400. Works: - fixing of boxes with cement mortar of at least 2 cm and final sealing all over the chase perimeter; - bullone di messa a terra (se richiesto d
alla DL). Marks: covers shall have a legible and permanent mark which indicates: - compliance with norms UNI EN 124; - indication on the central part of the cover (es. PUBBLIC LIGHTS) to be defined by DL
; - resistance class; - standard and/or manufacter's label; - possible sign of compliance of third authority for certification
Cast iron cover for box 100x100cm, grade C250
| UNDERGROUND LEVEL - MV/LV RACEWAYS |  | 2
| Total amount |  | 2
TOTAL CONDUITS
03 - DISTRIBUTION BOARDS
D40.A10.A1 |  | globally
METALLIC DISTRIBUTION BOARD In line with CEI 17-13/1(95) and subsequents variations. Caracteristics: - supporting modular structure composed by metalic chase in steal or pressed sheets of at least 20/10
, complete by fixing slotting, zippers, guides, supporting profiles for device fixing ; -floor fixing chase or for adjustments of profiles in steal steanless
twice basic colloring and surface solloring in black, complete by regolable feets with rusticated base and perforated in order to permit floor fixing
with dowels and ediante tasselli and glue (where required); - lateral and back covering pannels in bordered and collored sheets, equiped by flexible ground connection; - front pannels for diferent divisions in boarded sheets and collored
, zipper opening with special key with flexible ground connection; perforated pannels should be complete by gasket and perforation covers in order to close spaces not used; - boarded front door and collored, in trasnparent full plastic material,
(depending on prescribtions in grafic tables), zipper opening with handle, special key lock and flexible ground connection; - copper bar
marked in line with CEI-UNEL (oxidation junction phenomena indication should be included) ; - external protection level: as prescribed by grafic tables
, including bottom; - fron open pannels protection: non under IP20 guaranteed by appropriate headphones, covers, screens, protections, etc. for all devices and parts under voltage . Type of execution
(inside of the wall, out standing , on the wall or on the floor), one wire electric scheme, caracteristics and le caratteristiche and calibration of devices, accessories, tools, etc., are indicated in grafic tables . Prices are exclusive of
special devices such are lighting flux, comand bus devices, lighting flux regolation units, , etc., which will be quoted separatly.
Distribution board is compose by following elements and devices: - metal structure composed by two cabinets and one cabbling space with total dimensions (HxBxP): 2000x1850x350, protection level IP40; - n°1 manual main switcher in box with auxiliar contact 4x160A; - n°1 adjustable diferntial relay with toroid Id=0,3-10A; - n°1 voltage transmiter type 2 with auxiliar contact; - n°1 multimetar measurement instrument; - n°1 voltmetric measurament group 500V, class 1,5; - n°1 amperometric measurement group 50A, class 1,5; - n°1 modular fuse box 4x125A with fuses with auxiliar contact; - n°1 modular fuse box 4x63A with fuses with auxiliar contact; - n°2 modular fuse box 4x32A with fuses; - n°4 modular fuse box 2x20A with fuses; - n°2 manual main switcher 4x63A with auxiliar contact; - n°1 manual main switcher 4x40A with auxiliar contact; - n°1 modular commutator 4x40A;
- n°1magnetotermic differential modular automatic switcher 4x25A, Id=30mA with auxiliar contact; - n°1 magnetotermic differential modular automatic switcher 4x16A, Id=30mA with auxiliar contact; - n°4 magnetotermic differential modular automatic switcher 4x10A, Id=300mA with auxiliar contact; - n°2magnetotermic differential modular automatic switcher 1x25A+N, Id=30mA with auxiliar contact; - n°3 magnetotermic differential modular automatic switcher 1x16A+N, Id=30mA with auxiliar contact; - n°2 magnetotermic differential modular automatic switcher 1x10A+N, Id=300mA with auxiliar contact; - n°6 magnetotermic differential modular automatic switcher function of interventions B 1x10A+N, Id=30mA with auxiliar contact; - n°1 termo regolable differential automatic modular switcher 3x25A with auxiliar contact; - n°1 differential automatic modular switcher 4x25A, Id=300mA with auxiliar contact; - n°9 power modular contactor 3x12A AC3 with auxiliar contact; - n°1 power modular contactor 4x26A AC3 with auxiliar contact; - n°2 power modular contactor 3x26A AC3 with auxiliar contact; - n°1 trasformator 230/24V power 400VA; - n°3 modular selector on 3 positions; - signal lamp; - motor protection switch; - grounding bar inside distribution board.
DB_L-1/P1
| UNDERGROUND LEVEL - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 1
| Total amount |  | 1
D40.A10.A10 |  | globally
METALLIC DISTRIBUTION BOARD In line with CEI 17-13/1(95) and subsequents variations. Caracteristics: - supporting modular structure composed by metalic chase in steal or pressed sheets of at least 20/10
, complete by fixing slotting, zippers, guides, supporting profiles for device fixing ; -floor fixing chase or for adjustments of profiles in steal steanless
twice basic colloring and surface solloring in black, complete by regolable feets with rusticated base and perforated in order to permit floor fixing
with dowels and ediante tasselli and glue (where required); - lateral and back covering pannels in bordered and collored sheets, equiped by flexible ground connection; - front pannels for diferent divisions in boarded sheets and collored
, zipper opening with special key with flexible ground connection; perforated pannels should be complete by gasket and perforation covers in order to close spaces not used; - boarded front door and collored, in trasnparent full plastic material,
(depending on prescribtions in grafic tables), zipper opening with handle, special key lock and flexible ground connection; - copper bar
marked in line with CEI-UNEL (oxidation junction phenomena indication should be included) ; - external protection level: as prescribed by grafic tables
, including bottom; - fron open pannels protection: non under IP20 guaranteed by appropriate headphones, covers, screens, protections, etc. for all devices and parts under voltage . Type of execution
(inside of the wall, out standing , on the wall or on the floor), one wire electric scheme, caracteristics and le caratteristiche and calibration of devices, accessories, tools, etc., are indicated in grafic tables . Prices are exclusive of
special devices such are lighting flux, comand bus devices, lighting flux regolation units, , etc., which will be quoted separatly.
Distribution board is compose by following elements and devices: - metal structure composed by one wall cabinet total dimensions (HxBxP): 900x600x200, protection level IP40; - n°1 manual modular switch 2x32A with auxiliar contact; - n°1 voltage transmiter type 2 with auxiliar contact; - n°1 box modular fuses 2x32A complete by fuses; - n°5 magnetotermic differential modulare automatic switcher 1x10A+N, Id=300mA with auxiliar contact; - n°3 modular power contactor 3x12A AC3 with auxiliar contact; - signal lamp; - grounding bar inside distribution board.
DB_L-1/P1/EL
| UNDERGROUND LEVEL - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 1
| Total amount |  | 1
D40.A10.A11 |  | globally
METALLIC DISTRIBUTION BOARD In line with CEI 17-13/1(95) and subsequents variations. Caracteristics: - supporting modular structure composed by metalic chase in steal or pressed sheets of at least 20/10
, complete by fixing slotting, zippers, guides, supporting profiles for device fixing ; -floor fixing chase or for adjustments of profiles in steal steanless
twice basic colloring and surface solloring in black, complete by regolable feets with rusticated base and perforated in order to permit floor fixing
with dowels and ediante tasselli and glue (where required); - lateral and back covering pannels in bordered and collored sheets, equiped by flexible ground connection; - front pannels for diferent divisions in boarded sheets and collored
, zipper opening with special key with flexible ground connection; perforated pannels should be complete by gasket and perforation covers in order to close spaces not used; - boarded front door and collored, in trasnparent full plastic material,
(depending on prescribtions in grafic tables), zipper opening with handle, special key lock and flexible ground connection; - copper bar
marked in line with CEI-UNEL (oxidation junction phenomena indication should be included) ; - external protection level: as prescribed by grafic tables
, including bottom; - fron open pannels protection: non under IP20 guaranteed by appropriate headphones, covers, screens, protections, etc. for all devices and parts under voltage . Type of execution
(inside of the wall, out standing , on the wall or on the floor), one wire electric scheme, caracteristics and le caratteristiche and calibration of devices, accessories, tools, etc., are indicated in grafic tables . Prices are exclusive of
special devices such are lighting flux, comand bus devices, lighting flux regolation units, , etc., which will be quoted separatly.
Distribution board is compose by following elements and devices: - metal structure composed by one wall cabinet total dimensions(HxBxP): 900x600x200, protection level IP40; - n°1 manual modular switch 2x32A with auxiliar contact; - n°1 scaricatore di tensione type 2 with auxiliar contact; - n°1 box modular fuses 2x32A complete of fuses; - n°3 magnetotermic differential modulare automatic switcher1x10A+N, Id=300mA with auxiliar contact; - n°1 modular power contactor 3x12A AC3 with auxiliar contact; - signal lamp; - grounding bar inside distribution board.
DB_L-1/P2/EL
| UNDERGROUND LEVEL - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 1
| Total amount |  | 1
D40.A10.A2 |  | globally
METALLIC DISTRIBUTION BOARD In line with CEI 17-13/1(95) and subsequents variations. Caracteristics: - supporting modular structure composed by metalic chase in steal or pressed sheets of at least 20/10
, complete by fixing slotting, zippers, guides, supporting profiles for device fixing ; -floor fixing chase or for adjustments of profiles in steal steanless
twice basic colloring and surface solloring in black, complete by regolable feets with rusticated base and perforated in order to permit floor fixing
with dowels and ediante tasselli and glue (where required); - lateral and back covering pannels in bordered and collored sheets, equiped by flexible ground connection; - front pannels for diferent divisions in boarded sheets and collored
, zipper opening with special key with flexible ground connection; perforated pannels should be complete by gasket and perforation covers in order to close spaces not used; - boarded front door and collored, in trasnparent full plastic material,
(depending on prescribtions in grafic tables), zipper opening with handle, special key lock and flexible ground connection; - copper bar
marked in line with CEI-UNEL (oxidation junction phenomena indication should be included) ; - external protection level: as prescribed by grafic tables
, including bottom; - fron open pannels protection: non under IP20 guaranteed by appropriate headphones, covers, screens, protections, etc. for all devices and parts under voltage . Type of execution
(inside of the wall, out standing , on the wall or on the floor), one wire electric scheme, caracteristics and le caratteristiche and calibration of devices, accessories, tools, etc., are indicated in grafic tables . Prices are exclusive of
special devices such are lighting flux, comand bus devices, lighting flux regolation units, , etc., which will be quoted separatly.
Distribution board is compose by following elements and devices: - metal structure composed by two cabinets and one cabbling space with total dimensions (HxBxP): 2000x1850x350, protection level IP40; - n°1 manual main switcher in box with auxiliar contact 4x160A; - n°1 adjustable diferntial relay with toroid Id=0,3-10A; - n°1 voltage transmiter type 2 with auxiliar contact; - n°1 multimetar measurement instrument; - n°1 voltmetric measurament group 500V, class 1,5; - n°1 amperometric measurement group 50A, class 1,5; - n°1 modular fuse box 4x125A with fuses with auxiliar contact; - n°1 modular fuse box 4x63A with fuses with auxiliar contact; - n°2 modular fuse box 4x32A with fuses; - n°4 modular fuse box 2x20A with fuses; - n°2 manual main switcher 4x63A with auxiliar contact; - n°1 manual main switcher 4x40A with auxiliar contact; - n°1 modular commutator 4x40A;
- n°1magnetotermic differential modular automatic switcher 4x25A, Id=30mA with auxiliar contact; - n°1 magnetotermic differential modular automatic switcher 4x16A, Id=30mA with auxiliar contact; - n°4 magnetotermic differential modular automatic switcher 4x10A, Id=300mA with auxiliar contact; - n°2magnetotermic differential modular automatic switcher 1x25A+N, Id=30mA with auxiliar contact; - n°3 magnetotermic differential modular automatic switcher 1x16A+N, Id=30mA with auxiliar contact; - n°2 magnetotermic differential modular automatic switcher 1x10A+N, Id=300mA with auxiliar contact; - n°6 magnetotermic differential modular automatic switcher function of interventions B 1x10A+N, Id=30mA with auxiliar contact; - n°1 termo regolable differential automatic modular switcher 3x25A with auxiliar contact; - n°1 differential automatic modular switcher 4x25A, Id=300mA with auxiliar contact; - n°9 power modular contactor 3x12A AC3 with auxiliar contact; - n°1 power modular contactor 4x26A AC3 with auxiliar contact; - n°2 power modular contactor 3x26A AC3 with auxiliar contact; - n°1 trasformator 230/24V power 400VA; - n°3 modular selector on 3 positions; - signal lamp; - motor protection switch; - grounding bar inside distribution board.
DB_L-1/P2
| UNDERGROUND LEVEL - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 1
| Total amount |  | 1
D40.A10.A4 |  | globally
METALLIC DISTRIBUTION BOARD In line with CEI 17-13/1(95) and subsequents variations. Caracteristics: - supporting modular structure composed by metalic chase in steal or pressed sheets of at least 20/10
, complete by fixing slotting, zippers, guides, supporting profiles for device fixing ; -floor fixing chase or for adjustments of profiles in steal steanless
twice basic colloring and surface solloring in black, complete by regolable feets with rusticated base and perforated in order to permit floor fixing
with dowels and ediante tasselli and glue (where required); - lateral and back covering pannels in bordered and collored sheets, equiped by flexible ground connection; - front pannels for diferent divisions in boarded sheets and collored
, zipper opening with special key with flexible ground connection; perforated pannels should be complete by gasket and perforation covers in order to close spaces not used; - boarded front door and collored, in trasnparent full plastic material,
(depending on prescribtions in grafic tables), zipper opening with handle, special key lock and flexible ground connection; - copper bar
marked in line with CEI-UNEL (oxidation junction phenomena indication should be included) ; - external protection level: as prescribed by grafic tables
, including bottom; - fron open pannels protection: non under IP20 guaranteed by appropriate headphones, covers, screens, protections, etc. for all devices and parts under voltage . Type of execution
(inside of the wall, out standing , on the wall or on the floor), one wire electric scheme, caracteristics and le caratteristiche and calibration of devices, accessories, tools, etc., are indicated in grafic tables . Prices are exclusive of
special devices such are lighting flux, comand bus devices, lighting flux regolation units, , etc., which will be quoted separatly.
Distribution board is compose by following elements and devices: - Wall unit in termoplastic materila dimensions (HxBxP): 420x300x140, grado di protezione IP40; - n°1 automatic differential modular switch 4x63A, Id=30mA; - n°1 box modular fuses 4x32A box modular fuses; - n°2 box modular fuses 2x20A box modular fuses; - n°1 automatic magnetotermic modular switch 4x16A with auxiliar contact; - n°1 automatic magnetotermic modular switch1x25A+N with auxiliar contact; - n°1 automatic magnetotermic modular switch 1x16A+N with auxiliar contact; - n°2 automatic magnetotermic modular switch 1x10A+N with auxiliar contact; - signal lamp; - grounding bar inside distribution board.
DB_L-1/U
| UNDERGROUND LEVEL - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 1
| Total amount |  | 1
TOTAL DISTRIBUTION BOARDS
08 - DISTRIBUTION TERMINAL AND LIGHT SUPPLY
M10.A10.A1 |  | n
LIGHT SUPPLY EQUIVALENT Light supply composed by: - part of the quote for distribution box installed on the voltage tower, conduits passing from the distribution box to light device (priced appart)
connection box supplying light device (where required). In the case of two different lamps situated in one light device aditional price should be quoted (to equivalent light source) for doubled light source which includes modification or integration of cabbling.
In the case of dimmable light devices aditional price should be chargged (to equivalent light source) which includes modification or integration of cabbling (dimmable reactors and control point included).
Cabling typology should be prescribed by tables and grafics.
Materials forming points shouId have caracteristics indicated in the specific chapter of this study.
Light supply on wall with flexible PVC pipe and cable
| UNDERGROUND LEVEL - LIGHTING SYSTEM |  | 18
| UNDERGROUND LEVEL - LIGHTING SYSTEM - UNIVERSITY |  | 5
| Total amount |  | 23
M10.A10.A3 |  | n
LIGHT SUPPLY EQUIVALENT Light supply composed by: - part of the quote for distribution box installed on the voltage tower, conduits passing from the distribution box to light device (priced appart)
connection box supplying light device (where required). In the case of two different lamps situated in one light device aditional price should be quoted (to equivalent light source) for doubled light source which includes modification or integration of cabbling.
In the case of dimmable light devices aditional price should be chargged (to equivalent light source) which includes modification or integration of cabbling (dimmable reactors and control point included).
Cabling typology should be prescribed by tables and grafics.
Materials forming points shouId have caracteristics indicated in the specific chapter of this study.
Light supply on wall with flexible PVC pipe and fire resistence cable
| UNDERGROUND LEVEL - LIGHTING SYSTEM |  | 20
| Total amount |  | 20
M10.A10.A31 |  | n
LIGHT SUPPLY EQUIVALENT Light supply composed by: - part of the quote for distribution box installed on the voltage tower, conduits passing from the distribution box to light device (priced appart)
connection box supplying light device (where required). In the case of two different lamps situated in one light device aditional price should be quoted (to equivalent light source) for doubled light source which includes modification or integration of cabbling.
In the case of dimmable light devices aditional price should be chargged (to equivalent light source) which includes modification or integration of cabbling (dimmable reactors and control point included).
Cabling typology should be prescribed by tables and grafics.
Materials forming points shouId have caracteristics indicated in the specific chapter of this study.
Light supply on ceiling with cable
| UNDERGROUND LEVEL - LIGHTING SYSTEM |  | 21
| Total amount |  | 21
M10.A10.A8 |  | n
LIGHT SUPPLY EQUIVALENT Light supply composed by: - part of the quote for distribution box installed on the voltage tower, conduits passing from the distribution box to light device (priced appart)
connection box supplying light device (where required). In the case of two different lamps situated in one light device aditional price should be quoted (to equivalent light source) for doubled light source which includes modification or integration of cabbling.
In the case of dimmable light devices aditional price should be chargged (to equivalent light source) which includes modification or integration of cabbling (dimmable reactors and control point included).
Cabling typology should be prescribed by tables and grafics.
Materials forming points shouId have caracteristics indicated in the specific chapter of this study.
Visible light supply with rigid PVC pipe and cable, IP65
| UNDERGROUND LEVEL - LIGHTING SYSTEM |  | 205
| Total amount |  | 205
M10.A10.A9 |  | n
LIGHT SUPPLY EQUIVALENT Light supply composed by: - part of the quote for distribution box installed on the voltage tower, conduits passing from the distribution box to light device (priced appart)
connection box supplying light device (where required). In the case of two different lamps situated in one light device aditional price should be quoted (to equivalent light source) for doubled light source which includes modification or integration of cabbling.
In the case of dimmable light devices aditional price should be chargged (to equivalent light source) which includes modification or integration of cabbling (dimmable reactors and control point included).
Cabling typology should be prescribed by tables and grafics.
Materials forming points shouId have caracteristics indicated in the specific chapter of this study.
Visible light supply with rigid PVC pipe and fire resistance cable, IP65
| UNDERGROUND LEVEL - LIGHTING SYSTEM |  | 72
| Total amount |  | 72
M20.A10.A1 |  | n
LIGHT CONTROL SWITCH EQUIVALENT Control switch equivalent is composed by: - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks
; - jacks to be inserted in walls, completed, where required, by grips and conduits; - modular control jacks with following caracteristics: SWITCHES, DIVERTERS,
AND BUTTONS * in line with: CEI 23-9 and subsequent variants; * voltage and nominal frequency: 250V c.a., 50Hz; * nominal energy power : 10A for buttons and 16A for switches; * testing voltage: 2000V on 50Hz for 1 min.; *
interuption power: 200 opening and closing movements on 1,25 In, 275V c.a., cosfi'0,3; * functionality testing : 50000 movements on In, 250V c.a., cosfi'0,6; * isolation resistance: >15Mohm a 500V; * signal identification lamp
(where by type required); DIMMERS * voltage and nominal frequency: 230V c.a.+/-10%, 50Hz; * controled power: 60-500W (for resistent resistance); * isolation resistance: >15Mohm on 500V; * regolatione with
rotating command or swith with double function: longer pressure for continual regolation in increasement or decreasement, with electronic memory on release; fast touch for on/of funtion of the lamp on selected level of lighting
; * safety fuse; - jack chase in policarbonat self-extinguishing (UL94-V0) for click instalation and removal with tool, having punctures for screw instalation
with possibility of adjustment in the case of defectouse instalation; - box closures or finishes with covering elements enabling following protection : * at least IP21 (where not specified)
with covers of type selected by D.L. fixed by pressure and removable with tools; * IP55 with closure doors with transparent elastic sheath in silicone gum or similar, resistant to
humidity and water jets, allowing secure functionality of control devices with closed doors; * IP67 with non movable cover and elastic membrain in elastomer anti-age resistant to atmosferic agents
(heat, solar light, low temperatures ecc.), salt e/o acide, alcals, mineral and plant oil, animal oil and fat, carburants and non fire materials, fixed on jack box with stainless steal screws
; - eventually transit boxes.In the case of light signal command aditional price shoud be quoted for equivalent light source. In case of dimmed command
aditional price shoul be quoted fordimmed light source having caracteristics indicated by type. The price should include interior jacks cabbling. Cabbling type should be prescribed by chapter and grafic tables.
Matrials composing control swittch should have caracteristics indicated in the specific chapter of the present study.
Control switch equivalent is composed by: - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks
; - jacks to be inserted in walls, completed, where required, by grips and conduits; - modular control jacks with following caracteristics: SWITCHES, DIVERTERS,
AND BUTTONS * in line with: CEI 23-9 and subsequent variants; * voltage and nominal frequency: 250V c.a., 50Hz; * nominal energy power : 10A for buttons and 16A for switches; * testing voltage: 2000V on 50Hz for 1 min.; *
interuption power: 200 opening and closing movements on 1,25 In, 275V c.a., cosfi'0,3; * functionality testing : 50000 movements on In, 250V c.a., cosfi'0,6; * isolation resistance: >15Mohm a 500V; * signal identification lamp
(where by type required); DIMMERS * voltage and nominal frequency: 230V c.a.+/-10%, 50Hz; * controled power: 60-500W (for resistent resistance); * isolation resistance: >15Mohm on 500V; * regolatione with
rotating command or swith with double function: longer pressure for continual regolation in increasement or decreasement, with electronic memory on release; fast touch for on/of funtion of the lamp on selected level of lighting
; * safety fuse; - jack chase in policarbonat self-extinguishing (UL94-V0) for click instalation and removal with tool, having punctures for screw instalation
with possibility of adjustment in the case of defectouse instalation; - bx closures or finishes with covering elements enabling following protection : * at least IP21 (where not specified)
with covers of type selected by D.L. fixed by pressure and removable with tools; * IP55 with closure doors with transparent elastic sheath in silicone gum or similar, resistant to
humidity and water jets, allowing secure functionality of control devices with closed doors; * IP67 with non movable cover and elastic membrain in elastomer anti-age resistant to atmosferic agents
(heat, solar light, low temperatures ecc.), salt e/o acide, alcals, mineral and plant oil, animal oil and fat, carburants and non fire materials, fixed on jack box with stainless steal screws
; - eventually transit boxes.In the case of light signal command aditional price shoud be quoted for equivalent light source. In case of dimmed command
aditional price shoul be quoted fordimmed light source having caracteristics indicated by type. The price should include interior jacks cabbling. Cabbling type should be prescribed by chapter and grafic tables.
Matrials composing control swittch should have caracteristics indicated in the specific chapter of the present study.
Switch or push button switch on wall with flexible PVC pipe and cable
| UNDERGROUND LEVEL - LIGHTING SYSTEM |  | 10
| UNDERGROUND LEVEL - LIGHTING SYSTEM - UNIVERSITY |  | 5
| Total amount |  | 15
M20.A10.A32 |  | n
LIGHT CONTROL SWITCH EQUIVALENT Control switch equivalent is composed by: - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks
; - jacks to be inserted in walls, completed, where required, by grips and conduits; - modular control jacks with following caracteristics: SWITCHES, DIVERTERS,
AND BUTTONS * in line with: CEI 23-9 and subsequent variants; * voltage and nominal frequency: 250V c.a., 50Hz; * nominal energy power : 10A for buttons and 16A for switches; * testing voltage: 2000V on 50Hz for 1 min.; *
interuption power: 200 opening and closing movements on 1,25 In, 275V c.a., cosfi'0,3; * functionality testing : 50000 movements on In, 250V c.a., cosfi'0,6; * isolation resistance: >15Mohm a 500V; * signal identification lamp
(where by type required); DIMMERS * voltage and nominal frequency: 230V c.a.+/-10%, 50Hz; * controled power: 60-500W (for resistent resistance); * isolation resistance: >15Mohm on 500V; * regolatione with
rotating command or swith with double function: longer pressure for continual regolation in increasement or decreasement, with electronic memory on release; fast touch for on/of funtion of the lamp on selected level of lighting
; * safety fuse; - jack chase in policarbonat self-extinguishing (UL94-V0) for click instalation and removal with tool, having punctures for screw instalation
with possibility of adjustment in the case of defectouse instalation; - box closures or finishes with covering elements enabling following protection : * at least IP21 (where not specified)
with covers of type selected by D.L. fixed by pressure and removable with tools; * IP55 with closure doors with transparent elastic sheath in silicone gum or similar, resistant to
humidity and water jets, allowing secure functionality of control devices with closed doors; * IP67 with non movable cover and elastic membrain in elastomer anti-age resistant to atmosferic agents
(heat, solar light, low temperatures ecc.), salt e/o acide, alcals, mineral and plant oil, animal oil and fat, carburants and non fire materials, fixed on jack box with stainless steal screws
; - eventually transit boxes.In the case of light signal command aditional price shoud be quoted for equivalent light source. In case of dimmed command
aditional price shoul be quoted fordimmed light source having caracteristics indicated by type. The price should include interior jacks cabbling. Cabbling type should be prescribed by chapter and grafic tables.
Matrials composing control swittch should have caracteristics indicated in the specific chapter of the present study.
Control switch equivalent is composed by: - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks
; - jacks to be inserted in walls, completed, where required, by grips and conduits; - modular control jacks with following caracteristics: SWITCHES, DIVERTERS,
AND BUTTONS * in line with: CEI 23-9 and subsequent variants; * voltage and nominal frequency: 250V c.a., 50Hz; * nominal energy power : 10A for buttons and 16A for switches; * testing voltage: 2000V on 50Hz for 1 min.; *
interuption power: 200 opening and closing movements on 1,25 In, 275V c.a., cosfi'0,3; * functionality testing : 50000 movements on In, 250V c.a., cosfi'0,6; * isolation resistance: >15Mohm a 500V; * signal identification lamp
(where by type required); DIMMERS * voltage and nominal frequency: 230V c.a.+/-10%, 50Hz; * controled power: 60-500W (for resistent resistance); * isolation resistance: >15Mohm on 500V; * regolatione with
rotating command or swith with double function: longer pressure for continual regolation in increasement or decreasement, with electronic memory on release; fast touch for on/of funtion of the lamp on selected level of lighting
; * safety fuse; - jack chase in policarbonat self-extinguishing (UL94-V0) for click instalation and removal with tool, having punctures for screw instalation
with possibility of adjustment in the case of defectouse instalation; - bx closures or finishes with covering elements enabling following protection : * at least IP21 (where not specified)
with covers of type selected by D.L. fixed by pressure and removable with tools; * IP55 with closure doors with transparent elastic sheath in silicone gum or similar, resistant to
humidity and water jets, allowing secure functionality of control devices with closed doors; * IP67 with non movable cover and elastic membrain in elastomer anti-age resistant to atmosferic agents
(heat, solar light, low temperatures ecc.), salt e/o acide, alcals, mineral and plant oil, animal oil and fat, carburants and non fire materials, fixed on jack box with stainless steal screws
; - eventually transit boxes.In the case of light signal command aditional price shoud be quoted for equivalent light source. In case of dimmed command
aditional price shoul be quoted fordimmed light source having caracteristics indicated by type. The price should include interior jacks cabbling. Cabbling type should be prescribed by chapter and grafic tables.
Matrials composing control swittch should have caracteristics indicated in the specific chapter of the present study.
Visible switch or push button switch with rigid PVC pipe and cable - IP55
| UNDERGROUND LEVEL - LIGHTING SYSTEM |  | 31
| Total amount |  | 31
M20.A10.A61 |  | n
LIGHT CONTROL SWITCH EQUIVALENT Control switch equivalent is composed by: - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks
; - jacks to be inserted in walls, completed, where required, by grips and conduits; - modular control jacks with following caracteristics: SWITCHES, DIVERTERS,
AND BUTTONS * in line with: CEI 23-9 and subsequent variants; * voltage and nominal frequency: 250V c.a., 50Hz; * nominal energy power : 10A for buttons and 16A for switches; * testing voltage: 2000V on 50Hz for 1 min.; *
interuption power: 200 opening and closing movements on 1,25 In, 275V c.a., cosfi'0,3; * functionality testing : 50000 movements on In, 250V c.a., cosfi'0,6; * isolation resistance: >15Mohm a 500V; * signal identification lamp
(where by type required); DIMMERS * voltage and nominal frequency: 230V c.a.+/-10%, 50Hz; * controled power: 60-500W (for resistent resistance); * isolation resistance: >15Mohm on 500V; * regolatione with
rotating command or swith with double function: longer pressure for continual regolation in increasement or decreasement, with electronic memory on release; fast touch for on/of funtion of the lamp on selected level of lighting
; * safety fuse; - jack chase in policarbonat self-extinguishing (UL94-V0) for click instalation and removal with tool, having punctures for screw instalation
with possibility of adjustment in the case of defectouse instalation; - box closures or finishes with covering elements enabling following protection : * at least IP21 (where not specified)
with covers of type selected by D.L. fixed by pressure and removable with tools; * IP55 with closure doors with transparent elastic sheath in silicone gum or similar, resistant to
humidity and water jets, allowing secure functionality of control devices with closed doors; * IP67 with non movable cover and elastic membrain in elastomer anti-age resistant to atmosferic agents
(heat, solar light, low temperatures ecc.), salt e/o acide, alcals, mineral and plant oil, animal oil and fat, carburants and non fire materials, fixed on jack box with stainless steal screws
; - eventually transit boxes.In the case of light signal command aditional price shoud be quoted for equivalent light source. In case of dimmed command
aditional price shoul be quoted fordimmed light source having caracteristics indicated by type. The price should include interior jacks cabbling. Cabbling type should be prescribed by chapter and grafic tables.
Matrials composing control swittch should have caracteristics indicated in the specific chapter of the present study.
Control switch equivalent is composed by: - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks
; - jacks to be inserted in walls, completed, where required, by grips and conduits; - modular control jacks with following caracteristics: SWITCHES, DIVERTERS,
AND BUTTONS * in line with: CEI 23-9 and subsequent variants; * voltage and nominal frequency: 250V c.a., 50Hz; * nominal energy power : 10A for buttons and 16A for switches; * testing voltage: 2000V on 50Hz for 1 min.; *
interuption power: 200 opening and closing movements on 1,25 In, 275V c.a., cosfi'0,3; * functionality testing : 50000 movements on In, 250V c.a., cosfi'0,6; * isolation resistance: >15Mohm a 500V; * signal identification lamp
(where by type required); DIMMERS * voltage and nominal frequency: 230V c.a.+/-10%, 50Hz; * controled power: 60-500W (for resistent resistance); * isolation resistance: >15Mohm on 500V; * regolatione with
rotating command or swith with double function: longer pressure for continual regolation in increasement or decreasement, with electronic memory on release; fast touch for on/of funtion of the lamp on selected level of lighting
; * safety fuse; - jack chase in policarbonat self-extinguishing (UL94-V0) for click instalation and removal with tool, having punctures for screw instalation
with possibility of adjustment in the case of defectouse instalation; - bx closures or finishes with covering elements enabling following protection : * at least IP21 (where not specified)
with covers of type selected by D.L. fixed by pressure and removable with tools; * IP55 with closure doors with transparent elastic sheath in silicone gum or similar, resistant to
humidity and water jets, allowing secure functionality of control devices with closed doors; * IP67 with non movable cover and elastic membrain in elastomer anti-age resistant to atmosferic agents
(heat, solar light, low temperatures ecc.), salt e/o acide, alcals, mineral and plant oil, animal oil and fat, carburants and non fire materials, fixed on jack box with stainless steal screws
; - eventually transit boxes.In the case of light signal command aditional price shoud be quoted for equivalent light source. In case of dimmed command
aditional price shoul be quoted fordimmed light source having caracteristics indicated by type. The price should include interior jacks cabbling. Cabbling type should be prescribed by chapter and grafic tables.
Matrials composing control swittch should have caracteristics indicated in the specific chapter of the present study.
Surcharge for dimmable switch
| UNDERGROUND LEVEL - LIGHTING SYSTEM |  | 1
| Total amount |  | 1
M20.A30.A1 |  | n
EMERGENCY RELEASE PUSHBUTTON Emergency release pushbutton is composed by: - part of the quote for distribution box installed on the voltage tower (where required);; - conduits from pushbutton to release interuprot/s installed
on the main voltage squar or zone voltage square - box in lectro zink and collored in yellow complete by hinged cover, neoprene gasket
eoprene, key lock, glass breaking hammer with chain, breaking glass, sintetic,splinter proof, including release button 6A/380V; - instruction table indicating text as defined by D.L.
Emergency release pushbutton with PVC pipe and cable
| UNDERGROUND LEVEL - LV TERMINAL DISTRIBUTION |  | 3
| Total amount |  | 3
M20.A50.A1 |  | n
SURCHARGE FOR INFRARED AUTOMATIC COMMAND POINT Infrared automatic command light point in presence of people trough volumetric with following caracteristics: - nominal voltage frequence
: 230V c.a. +/-10%, 50Hz; - nominal power: at least 2200 VA; - detection angle : at least 100^ horizontal and 30^ on vertical type of walls; 360^ with basic conus d.7,5m on h=2,5 for the ceiling type ; -
radius of action: front type at least 4 m for the wall type; at least 7m for the ceiling type. - detection density of at least 14 incidents segments trough fresnel lens; - regolation of brightness trashold from 5 to 1000 lux at least with possibility of exclusion
; - commutation time regolation min.: from 5 sec to 10 min; - protection leve;: min. IP44 (frontal) IP20 on ceiling; - o where required MAN/0/AUT selector in order to inhibit or mainain commutaded comand contact
; - chase in ABS composed by: * (wall type) fixed part having electronic componenets , regolation screws , grip and fixing accessories for chase fixing or out standing trough junction to max. angle of
l80^; * (ceiling type) fixing nail for detector positioning; - reley with contacts for lamp command incandescence and fluoroscent; - attesting grip with screws; - instalation:
in wall or on wall depending on type. Where required by type, detection system should be executed with more divices where the principal one with master function and secondaries (limited number) with slave function which will send detected signal to the master one;
master will have at least n.2 different contacts. Materials forming the point should have caracteristics indicated in the specific chapter of the present study.
quotation should be understood as aditional price to be added to command equivalent point
Surcharge for command point on wall with infrared sensor
| UNDERGROUND LEVEL - LIGHTING SYSTEM |  | 10
| UNDERGROUND LEVEL - LIGHTING SYSTEM - UNIVERSITY |  | 1
| Total amount |  | 11
M20.A50.A2 |  | n
SURCHARGE FOR INFRARED AUTOMATIC COMMAND POINT Infrared automatic command light point in presence of people trough volumetric with following caracteristics: - nominal voltage frequence
: 230V c.a. +/-10%, 50Hz; - nominal power: at least 2200 VA; - detection angle : at least 100^ horizontal and 30^ on vertical type of walls; 360^ with basic conus d.7,5m on h=2,5 for the ceiling type ; -
radius of action: front type at least 4 m for the wall type; at least 7m for the ceiling type. - detection density of at least 14 incidents segments trough fresnel lens; - regolation of brightness trashold from 5 to 1000 lux at least with possibility of exclusion
; - commutation time regolation min.: from 5 sec to 10 min; - protection leve;: min. IP44 (frontal) IP20 on ceiling; - o where required MAN/0/AUT selector in order to inhibit or mainain commutaded comand contact
; - chase in ABS composed by: * (wall type) fixed part having electronic componenets , regolation screws , grip and fixing accessories for chase fixing or out standing trough junction to max. angle of
l80^; * (ceiling type) fixing nail for detector positioning; - reley with contacts for lamp command incandescence and fluoroscent; - attesting grip with screws; - instalation:
in wall or on wall depending on type. Where required by type, detection system should be executed with more divices where the principal one with master function and secondaries (limited number) with slave function which will send detected signal to the master one;
master will have at least n.2 different contacts. Materials forming the point should have caracteristics indicated in the specific chapter of the present study.
quotation should be understood as aditional price to be added to command equivalent point
Surcharge for visible command point with infrared sensor
| UNDERGROUND LEVEL - LIGHTING SYSTEM |  | 16
| Total amount |  | 16
M30.A10.A7 |  | n
POWER SUPPLY POINTS Power supply is composed by : - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks (quoted appart)
; - eventualy transit boxes and jack boxes. Type of cabbling should be prescribed by chapter and dimensioned on the basis of efective voltage
used by devices (motored door/tent, cabinets, etc.) . In the case of existing conduits just the price of cabbling shoud be indicated . In the case of supply and instalation
of only conduits and boxes price for preparaty works should be indicated. Used materials should be in line with specific chaapter of present study.
Wall embedded power with PVC flexible pipe and 3x2.5 cable
| UNDERGROUND LEVEL - LV TERMINAL DISTRIBUTION |  | 22
| Total amount |  | 22
M30.A10.A8 |  | n
POWER SUPPLY POINTS Power supply is composed by : - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks (quoted appart)
; - eventualy transit boxes and jack boxes. Type of cabbling should be prescribed by chapter and dimensioned on the basis of efective voltage
used by devices (motored door/tent, cabinets, etc.) . In the case of existing conduits just the price of cabbling shoud be indicated . In the case of supply and instalation
of only conduits and boxes price for preparaty works should be indicated. Used materials should be in line with specific chaapter of present study.
Wall embedded power with PVC flexible pipe and 3x4 cable
| UNDERGROUND LEVEL - LV TERMINAL DISTRIBUTION |  | 6
| Total amount |  | 6
M30.A10.B18 |  | n
POWER SUPPLY POINTS Power supply is composed by : - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks (quoted appart)
; - eventualy transit boxes and jack boxes. Type of cabbling should be prescribed by chapter and dimensioned on the basis of efective voltage
used by devices (motored door/tent, cabinets, etc.) . In the case of existing conduits just the price of cabbling shoud be indicated . In the case of supply and instalation
of only conduits and boxes price for preparaty works should be indicated. Used materials should be in line with specific chaapter of present study.
Visible wall installation power supply with PVC rigid pipe and 5x4 cable, IP44
| UNDERGROUND LEVEL - LV TERMINAL DISTRIBUTION |  | 23
| UNDERGROUND LEVEL - LV TERMINAL DISTRIBUTION - UNIVERSITY |  | 3
| Total amount |  | 26
M30.A10.B7 |  | n
POWER SUPPLY POINTS Power supply is composed by : - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks (quoted appart)
; - eventualy transit boxes and jack boxes. Type of cabbling should be prescribed by chapter and dimensioned on the basis of efective voltage
used by devices (motored door/tent, cabinets, etc.) . In the case of existing conduits just the price of cabbling shoud be indicated . In the case of supply and instalation
of only conduits and boxes price for preparaty works should be indicated. Used materials should be in line with specific chaapter of present study.
Visible wall installation power supply with PVC rigid pipe and 3x2.5 cable, IP44
| UNDERGROUND LEVEL - LV TERMINAL DISTRIBUTION |  | 37
| UNDERGROUND LEVEL - LV TERMINAL DISTRIBUTION - UNIVERSITY |  | 6
| Total amount |  | 43
M30.A10.B8 |  | n
POWER SUPPLY POINTS Power supply is composed by : - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks (quoted appart)
; - eventualy transit boxes and jack boxes. Type of cabbling should be prescribed by chapter and dimensioned on the basis of efective voltage
used by devices (motored door/tent, cabinets, etc.) . In the case of existing conduits just the price of cabbling shoud be indicated . In the case of supply and instalation
of only conduits and boxes price for preparaty works should be indicated. Used materials should be in line with specific chaapter of present study.
Visible wall installation power supply with PVC rigid pipe and 3x4 cable, IP44
| UNDERGROUND LEVEL - LV TERMINAL DISTRIBUTION |  | 7
| UNDERGROUND LEVEL - LV TERMINAL DISTRIBUTION - UNIVERSITY |  | 1
| Total amount |  | 8
N10.A10.A13 |  | n
DOMESTIC SOCKET POINT AND PROTECTION DEVICE OR SIMILAR Socket point composed by: Punto presa composto da: - modular sockets with following caracteristics: DOMESTIC SOCKETS OR SIMILAR : * in line with
: CEI 23-5, 23-16 and subsequent variations; * in line with tables: CEI-UNEL 47158, 47 V3. * voltage and nominal frequency : 230V c.a. +/-10%, 50Hz; * nominal energy supply: as described by types; * level of protection: min. IP21; * testing voltage
i: 2000V on 50Hz for 1 min.; * interruption power: min. 100 movements of in/out and extraction of jack on 275V c.a., cosfi' 0,6, with testing power 1,25 In (for socket 10A) e 2,0 In (for socket 16A); * isolation resistance
o: > 15Mohm on 500V; * click fixing removal with tool; PROTECTION SWITCH (magnetotermic and magnetotermic differential, depending on type): * in line with : CEI 23-3 and subsequent variations
; * nominal frequence and voltage: 230V c.a. +/-10%, 50Hz; *nominal energy supply: as described by types; * interruption power: 3000A; * differential energy (eventualy): 10mA; * isolation resistance: > 15Mohm a 500V; * fixing on chase with tool removal
; FUSE BOX AND FUSES * in line with: CEI 32-1, 32-4, 32-5 and subsequent variation; * voltage and nominal frequency: 230V c.a. +/-10%, 50Hz; * nominal energy: as decribed by type
; * interruption power: 100kA with cosfi' 0,2; ISOLATION TRANSFORMATOR (shaving socket): * in line with: CEI 14-6 and subsequent variations; * primary voltage: 230V c.a. +/-10%; * nominal frequency: 50Hz; * secondary voltage
: double coil on 110V connectable in series (230V) or parallel (110V) trough commutator; * nominal power: 20VA; * microinterruptor for transormator insertion only for grafted; * over power protection
; - socket chase in autoestingueting policarbonat (UL94-V0) with slotted holes for screw fixing in order to permit adjustments in case of defected instalation ; - closing and finishing of domestic socket
, with covering elements in order to guarantee following protection: * IP21 with cover selected by D.L.fixed by pressure or screwed to be removed with tool
; * IP 44 min. with doors with transparent elastic sheath in silicone gum or similar or doors in termoplastic material, resistent to humidity and water jets on closed position.
POWER SUPPLY POINTS Power supply is composed by : - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to sockets (quoted appart)
; - eventualy transit boxes and sockets. Type of cabbling should be prescribed by chapter and dimensioned on the basis of specific chapter of the study "Disciplinare descrittivo e pr
estazionale degli elementi tecnici". Price should be inclusive of cabbling between sockets. Materials must be with caracteristics indicated in the specific chapter of the present study.
Socket outlet 2x16 A+E
| UNDERGROUND LEVEL - LV TERMINAL DISTRIBUTION |  | 18
| Total amount |  | 18
N10.A10.A3 |  | n
DOMESTIC SOCKET POINT AND PROTECTION DEVICE OR SIMILAR Socket point composed by: Punto presa composto da: - modular sockets with following caracteristics: DOMESTIC SOCKETS OR SIMILAR : * in line with
: CEI 23-5, 23-16 and subsequent variations; * in line with tables: CEI-UNEL 47158, 47 V3. * voltage and nominal frequency : 230V c.a. +/-10%, 50Hz; * nominal energy supply: as described by types; * level of protection: min. IP21; * testing voltage
i: 2000V on 50Hz for 1 min.; * interruption power: min. 100 movements of in/out and extraction of jack on 275V c.a., cosfi' 0,6, with testing power 1,25 In (for socket 10A) e 2,0 In (for socket 16A); * isolation resistance
o: > 15Mohm on 500V; * click fixing removal with tool; PROTECTION SWITCH (magnetotermic and magnetotermic differential, depending on type): * in line with : CEI 23-3 and subsequent variations
; * nominal frequence and voltage: 230V c.a. +/-10%, 50Hz; *nominal energy supply: as described by types; * interruption power: 3000A; * differential energy (eventualy): 10mA; * isolation resistance: > 15Mohm a 500V; * fixing on chase with tool removal
; FUSE BOX AND FUSES * in line with: CEI 32-1, 32-4, 32-5 and subsequent variation; * voltage and nominal frequency: 230V c.a. +/-10%, 50Hz; * nominal energy: as decribed by type
; * interruption power: 100kA with cosfi' 0,2; ISOLATION TRANSFORMATOR (shaving socket): * in line with: CEI 14-6 and subsequent variations; * primary voltage: 230V c.a. +/-10%; * nominal frequency: 50Hz; * secondary voltage
: double coil on 110V connectable in series (230V) or parallel (110V) trough commutator; * nominal power: 20VA; * microinterruptor for transormator insertion only for grafted; * over power protection
; - socket chase in autoestingueting policarbonat (UL94-V0) with slotted holes for screw fixing in order to permit adjustments in case of defected instalation ; - closing and finishing of domestic socket
, with covering elements in order to guarantee following protection: * IP21 with cover selected by D.L.fixed by pressure or screwed to be removed with tool
; * IP 44 min. with doors with transparent elastic sheath in silicone gum or similar or doors in termoplastic material, resistent to humidity and water jets on closed position.
POWER SUPPLY POINTS Power supply is composed by : - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to sockets (quoted appart)
; - eventualy transit boxes and sockets. Type of cabbling should be prescribed by chapter and dimensioned on the basis of specific chapter of the study "Disciplinare descrittivo e pr
estazionale degli elementi tecnici". Price should be inclusive of cabbling between sockets. Materials must be with caracteristics indicated in the specific chapter of the present study.
Socket outlet 2x10/16 A+E
| UNDERGROUND LEVEL - LV TERMINAL DISTRIBUTION |  | 18
| Total amount |  | 18
N10.A10.A5 |  | n
DOMESTIC SOCKET POINT AND PROTECTION DEVICE OR SIMILAR Socket point composed by: Punto presa composto da: - modular sockets with following caracteristics: DOMESTIC SOCKETS OR SIMILAR : * in line with
: CEI 23-5, 23-16 and subsequent variations; * in line with tables: CEI-UNEL 47158, 47 V3. * voltage and nominal frequency : 230V c.a. +/-10%, 50Hz; * nominal energy supply: as described by types; * level of protection: min. IP21; * testing voltage
i: 2000V on 50Hz for 1 min.; * interruption power: min. 100 movements of in/out and extraction of jack on 275V c.a., cosfi' 0,6, with testing power 1,25 In (for socket 10A) e 2,0 In (for socket 16A); * isolation resistance
o: > 15Mohm on 500V; * click fixing removal with tool; PROTECTION SWITCH (magnetotermic and magnetotermic differential, depending on type): * in line with : CEI 23-3 and subsequent variations
; * nominal frequence and voltage: 230V c.a. +/-10%, 50Hz; *nominal energy supply: as described by types; * interruption power: 3000A; * differential energy (eventualy): 10mA; * isolation resistance: > 15Mohm a 500V; * fixing on chase with tool removal
; FUSE BOX AND FUSES * in line with: CEI 32-1, 32-4, 32-5 and subsequent variation; * voltage and nominal frequency: 230V c.a. +/-10%, 50Hz; * nominal energy: as decribed by type
; * interruption power: 100kA with cosfi' 0,2; ISOLATION TRANSFORMATOR (shaving socket): * in line with: CEI 14-6 and subsequent variations; * primary voltage: 230V c.a. +/-10%; * nominal frequency: 50Hz; * secondary voltage
: double coil on 110V connectable in series (230V) or parallel (110V) trough commutator; * nominal power: 20VA; * microinterruptor for transormator insertion only for grafted; * over power protection
; - socket chase in autoestingueting policarbonat (UL94-V0) with slotted holes for screw fixing in order to permit adjustments in case of defected instalation ; - closing and finishing of domestic socket
, with covering elements in order to guarantee following protection: * IP21 with cover selected by D.L.fixed by pressure or screwed to be removed with tool
; * IP 44 min. with doors with transparent elastic sheath in silicone gum or similar or doors in termoplastic material, resistent to humidity and water jets on closed position.
POWER SUPPLY POINTS Power supply is composed by : - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to sockets (quoted appart)
; - eventualy transit boxes and sockets. Type of cabbling should be prescribed by chapter and dimensioned on the basis of specific chapter of the study "Disciplinare descrittivo e pr
estazionale degli elementi tecnici". Price should be inclusive of cabbling between sockets. Materials must be with caracteristics indicated in the specific chapter of the present study.
Socket outlet 2x16 A+E with interblock switch
| UNDERGROUND LEVEL - LV TERMINAL DISTRIBUTION |  | 5
| UNDERGROUND LEVEL - LV TERMINAL DISTRIBUTION - UNIVERSITY |  | 1
| Total amount |  | 6
N10.A10.A65 |  | n
DOMESTIC SOCKET POINT AND PROTECTION DEVICE OR SIMILAR Socket point composed by: Punto presa composto da: - modular sockets with following caracteristics: DOMESTIC SOCKETS OR SIMILAR : * in line with
: CEI 23-5, 23-16 and subsequent variations; * in line with tables: CEI-UNEL 47158, 47 V3. * voltage and nominal frequency : 230V c.a. +/-10%, 50Hz; * nominal energy supply: as described by types; * level of protection: min. IP21; * testing voltage
i: 2000V on 50Hz for 1 min.; * interruption power: min. 100 movements of in/out and extraction of jack on 275V c.a., cosfi' 0,6, with testing power 1,25 In (for socket 10A) e 2,0 In (for socket 16A); * isolation resistance
o: > 15Mohm on 500V; * click fixing removal with tool; PROTECTION SWITCH (magnetotermic and magnetotermic differential, depending on type): * in line with : CEI 23-3 and subsequent variations
; * nominal frequence and voltage: 230V c.a. +/-10%, 50Hz; *nominal energy supply: as described by types; * interruption power: 3000A; * differential energy (eventualy): 10mA; * isolation resistance: > 15Mohm a 500V; * fixing on chase with tool removal
; FUSE BOX AND FUSES * in line with: CEI 32-1, 32-4, 32-5 and subsequent variation; * voltage and nominal frequency: 230V c.a. +/-10%, 50Hz; * nominal energy: as decribed by type
; * interruption power: 100kA with cosfi' 0,2; ISOLATION TRANSFORMATOR (shaving socket): * in line with: CEI 14-6 and subsequent variations; * primary voltage: 230V c.a. +/-10%; * nominal frequency: 50Hz; * secondary voltage
: double coil on 110V connectable in series (230V) or parallel (110V) trough commutator; * nominal power: 20VA; * microinterruptor for transormator insertion only for grafted; * over power protection
; - socket chase in autoestingueting policarbonat (UL94-V0) with slotted holes for screw fixing in order to permit adjustments in case of defected instalation ; - closing and finishing of domestic socket
, with covering elements in order to guarantee following protection: * IP21 with cover selected by D.L.fixed by pressure or screwed to be removed with tool
; * IP 44 min. with doors with transparent elastic sheath in silicone gum or similar or doors in termoplastic material, resistent to humidity and water jets on closed position.
POWER SUPPLY POINTS Power supply is composed by : - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to sockets (quoted appart)
; - eventualy transit boxes and sockets. Type of cabbling should be prescribed by chapter and dimensioned on the basis of specific chapter of the study "Disciplinare descrittivo e pr
estazionale degli elementi tecnici". Price should be inclusive of cabbling between sockets. Materials must be with caracteristics indicated in the specific chapter of the present study.
Socket outlet 2x16 A+E with interblock switch, IP44
| UNDERGROUND LEVEL - LV TERMINAL DISTRIBUTION |  | 19
| UNDERGROUND LEVEL - LV TERMINAL DISTRIBUTION - UNIVERSITY |  | 4
| Total amount |  | 23
N10.A20.A50 |  | n
INDUSTRIAL SOCKET OUTLET In line with: CEI 23-12(92) and subsequent variations; UL94-V1. In line with tables : CEI-UNEL 47173, 47174, 47175, 47176. Nominal voltage: 230/400V c.a. +/-10%.
Niminal frequence: 50Hz; Nominal energy: as described by type. Ptotection level :as described by type. Caracteristics: - modular chase box in wall or on wall scatola in termo poliestere resine,
autoestingueting, reinforced by glass fiber or in pressofused alloy heat collored with epossidic resine with previous resine chromatization treatment depending on type ; cover with same caracteristics as the box, connected to the box complete with screws in steal stainless and elestomer age proof gasket
; signed holes complete of connections to supply conduits; - bayonet connection for closed switch manual blockage
; ferulle and protection watertight cover in termoplastic material with stainless steal closing spring ; - selector switcher rotation type with reef with contact disc intermoindurent isolation material
, autoestingueting, electric arc proof and two interuption points silver contacts; manual blocking in order to prevent, closed switche, jack extraction, opening of cover and access tu fuses and, if cover open, closure of the swither
; - where required by type, fuse box froup in ceramic material or in termpolastic material, autoestiguiting, complete by fusible cartridge of dimensions in line with international standards,
; - owhere required by type, security transformator (norm CEI 14-6) voltage at least 160VA for jack supply in lowest security voltage (SELV); interblocking switcher composed by switcher situated on the primary transformator,
, activated by jack instertion; protection of the primery and secondary by fuses.
Industrial visible socket outlet with mechanical interblock and fuses, 2x16 A+E, IP55
| UNDERGROUND LEVEL - LV TERMINAL DISTRIBUTION |  | 20
| UNDERGROUND LEVEL - LV TERMINAL DISTRIBUTION - UNIVERSITY |  | 3
| Total amount |  | 23
N10.A20.A56 |  | n
INDUSTRIAL SOCKET OUTLET In line with: CEI 23-12(92) and subsequent variations; UL94-V1. In line with tables : CEI-UNEL 47173, 47174, 47175, 47176. Nominal voltage: 230/400V c.a. +/-10%.
Niminal frequence: 50Hz; Nominal energy: as described by type. Ptotection level :as described by type. Caracteristics: - modular chase box in wall or on wall ,
autoestingueting, reinforced by glass fiber or in pressofused alloy heat collored with epossidic resine with previous resine chromatization treatment depending on type ; cover with same caracteristics as the box, connected to the box complete with screws in steal stainless and elestomer age proof gasket
; signed holes complete of connections to supply conduits; - bayonet connection for closed switch manual blockage
; ferulle and protection watertight cover in termoplastic material with stainless steal closing spring ; - selector switcher rotation type with reef with contact disc intermoindurent isolation material
, autoestingueting, electric arc proof and two interuption points silver contacts; manual blocking in order to prevent, closed switche, jack extraction, opening of cover and access tu fuses and, if cover open, closure of the swither
; - where required by type, fuse box froup in ceramic material or in termpolastic material, autoestiguiting, complete by fusible cartridge of dimensions in line with international standards,
; - Where required by type, security transformator (norm CEI 14-6) voltage at least 160VA for jack supply in lowest security voltage (SELV); interblocking switcher composed by switcher situated on the primary transformator,
, activated by jack instertion; protection of the primery and secondary by fuses.
Industrial visible socket outlet with mechanical interblock and fuses, 3x16 A+N+E, IP55
| UNDERGROUND LEVEL - LV TERMINAL DISTRIBUTION |  | 20
| UNDERGROUND LEVEL - LV TERMINAL DISTRIBUTION - UNIVERSITY |  | 3
| Total amount |  | 23
TOTAL DISTRIBUTION TERMINALS AND SUPPLY POINTS
09 - EARTHING AND PROTECTION AGAINST ATMOSFERIC SHOTS
O10.A80.A1 |  | n
CONNECTION TO BUILDING METAL ELEMENTS EQUIVALENT CONNECTION POINT composed by : - round and flat conduit up to 150 mm2 di of zinc steal section or up to 100 mm2 of copper section for the connection of dispesor ring and building metal
; - collegamento equipotential connection between all armour metals and dispesor realized in alluminotermic welding or grip joints
Connection to building metal elements by mechanical joint (clamping)
| UNDERGROUND LEVEL - EARTHING AND LIGHTNING PLANT |  | 55
| Total amount |  | 55
TOTAL IMP. TERRA E PROTEZ. CONTRO SCARICHE ATMOSF.
10 - APPARECCHI ILLUMINANTI
P300.A120.A1 |  | n
SELF POWERING KIT FOR EMERGENCY LIGHTING WITH FLUORESCENT LIGHTS Group of supply-reactor and battery Ni-Cd hermetic appropriate for linear and compact fluoroscent light emergency supply
, instalation in the allready cabbled lighting device . In light with: CEI 34-21, 34-22 and subsequent variations . Technical and lighting caracteritics: - voltage and nominal frequency: 230V c.a. +/-20%, 50H
z; - charging time: max. 24h; Electromeccanical caracteristics: - isolation level: class II; - protection level min: IP20; - fire resistance: 750° C. Construction caracteristic: - battery
Ni-Cd with capacity appropriate for the power of the lamp having following authonomy min: * fully charged as decsribed by type ; * at least one hour after 12 hours of charge; - slipcase in plastic material autoestinguiting ; - possibility for supply of fluoroscent lamp from
18 a 58W with minimal authonomy as decsribed per type ; - minimal percentage of emergency percentuale minima of transition of emergency of the lamp respectively to nominal as indicated del: * authonomy 1h: 35% for lamps from 18W, 20% for 36W and 1
5% for lamps 58W; * authonomy 3h: 25% for lamp of 18W, 15% for 36W and 10% for lamp 58W; - protection switch for batery total empty; - network protection fuses; - battery activity network presence LED
; - constant activity possibility SA (lamps allways on) or just emergency SE (just without voltage in network); - connection grips from comand line and emergency
. - electronic circuit contolling minimal level of voltage and of automatic charge ; - connection grips for command line conection and emergency ; - (where required by type) diagnostic circuit capable to perform test on internal circuit, on the lamp
and on batteries trough centralized system.
Self powering kit for fluorescent light up to 58W, aut. 1h
| UNDERGROUND LEVEL - LIGHTING SYSTEM |  | 9
| UNDERGROUND LEVEL - LIGHTING SYSTEM - UNIVERSITY |  | 9
| Total amount |  | 18
P500.A10.A1 |  | globally
LIGHTING LUMINAIRES LAYING Instalation of lighting devices (exclusive of supply) including assembly of parts and all relevant costs in order to perform the work.
completa e funzionante
Lighting luminaires laying (luminaires not included) on basement level
| UNDERGROUND LEVEL - LIGHTING SYSTEM |  | 1
| Total amount |  | 1
TOTAL LIGHTING DEVICES
TOTAL ELECTRICAL - UNDERGROUND
-
03 | ELECTRICAL PLANTS - GROUND FLOOR AND UPPER FLOOR LEVELS
01 - CONDUCTORS, CABLES AND ACCESSORIES
A210.A20.A2 |  | m
H07Z1-K 450/750V CABLE H07Z1-K type 2 450/750V in line with: CEI 20-22/3, 20-38/1 and subsequent variations. Nominal voltage: 450/750 V. Isolation: Termoplastica mixture. Conductor: copper wire of flexible red copper
Fire reaction: - non propagating fire; - law gas emission, toxic and corrosive gasses
H07Z1-K 450/750V cable 1x2,5 mmq
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 125
| FIRST FLOOR LEVEL - MV/LV CABLES |  | 100
| SECOND FLOOR LEVEL - MV/LV CABLES |  | 110
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 40
| Total amount |  | 375
A210.A20.A3 |  | m
H07Z1-K 450/750V CABLE H07Z1-K type 2 450/750V in line with: CEI 20-22/3, 20-38/1 and subsequent variations. Nominal voltage: 450/750 V. Isolation: Termoplastica mixture. Conductor: copper wire of flexible red copper
Fire reaction: - non propagating fire; - law gas emission, toxic and corrosive gasses
H07Z1-K 450/750V cable 1x4 mmq
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 250
| FIRST FLOOR LEVEL - MV/LV CABLES |  | 120
| SECOND FLOOR LEVEL - MV/LV CABLES |  | 90
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 50
| Total amount |  | 510
A210.A20.A5 |  | m
H07Z1-K 450/750V CABLE H07Z1-K type 2 450/750V in line with: CEI 20-22/3, 20-38/1 and subsequent variations. Nominal voltage: 450/750 V. Isolation: Termoplastica mixture. Conductor: copper wire of flexible red copper
Fire reaction: - non propagating fire; - law gas emission, toxic and corrosive gasses
H07Z1-K 450/750V cable 1x10 mmq
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 5
| FIRST FLOOR LEVEL - MV/LV CABLES |  | 5
| SECOND FLOOR LEVEL - MV/LV CABLES |  | 5
| Total amount |  | 15
A210.A20.A6 |  | m
H07Z1-K 450/750V CABLE H07Z1-K type 2 450/750V in line with: CEI 20-22/3, 20-38/1 and subsequent variations. Nominal voltage: 450/750 V. Isolation: Termoplastica mixture. Conductor: copper wire of flexible red copper
Fire reaction: - non propagating fire; - law gas emission, toxic and corrosive gasses
H07Z1-K 450/750V cable 1x16 mmq
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 15
| FIRST FLOOR LEVEL - MV/LV CABLES |  | 10
| SECOND FLOOR LEVEL - MV/LV CABLES |  | 5
| Total amount |  | 30
A210.A20.A7 |  | m
H07Z1-K 450/750V CABLE H07Z1-K type 2 450/750V in line with: CEI 20-22/3, 20-38/1 and subsequent variations. Nominal voltage: 450/750 V. Isolation: Termoplastica mixture. Conductor: copper wire of flexible red copper
Fire reaction: - non propagating fire; - law gas emission, toxic and corrosive gasses
H07Z1-K 450/750V cable 1x25 mmq
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 5
| Total amount |  | 5
A220.A20.A18 |  | m
FG7M1 0,6/1kV, FG7OM1 0,6/1kV CABLE FG7M1 0,6/1kV, FG7OM1 0,6/1kV in line with: CEI 20-13, 20-22/3 and subsequent variations. In line with tables: CEI-UNEL 35382, 35384. Nominal voltage: 600/1000 V. Isolation
: etilen-propilenic tipo G7 gum. Sheath: special termoplastic polimer quality M1. Filler: non vulcanized gum . Conductor: heated copperflexible wire. Protection (if required): copper wire braid. Fire reaction: non propagating fire; - law gas emission, toxic and corrosive gasses.
FG7OM1 0,6/1kV cable 2x2,5 mmq
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 140
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 255
| Total amount |  | 395
A220.A20.A31 |  | m
FG7M1 0,6/1kV, FG7OM1 0,6/1kV CABLE FG7M1 0,6/1kV, FG7OM1 0,6/1kV in line with: CEI 20-13, 20-22/3 and subsequent variations. In line with tables: CEI-UNEL 35382, 35384. Nominal voltage: 600/1000 V. Isolation
: etilen-propilenic tipo G7 gum. Sheath: special termoplastic polimer quality M1. Filler: non vulcanized gum . Conductor: heated copperflexible wire. Protection (if required): copper wire braid. Fire reaction: non propagating fire; - law gas emission, toxic and corrosive gasses.
FG7OM1 0,6/1kV cable 3x2,5 mmq
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 560
| FIRST FLOOR LEVEL - MV/LV CABLES |  | 660
| SECOND FLOOR LEVEL - MV/LV CABLES |  | 815
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 405
| Total amount |  | 2440
A220.A20.A32 |  | m
FG7M1 0,6/1kV, FG7OM1 0,6/1kV CABLE FG7M1 0,6/1kV, FG7OM1 0,6/1kV in line with: CEI 20-13, 20-22/3 and subsequent variations. In line with tables: CEI-UNEL 35382, 35384. Nominal voltage: 600/1000 V. Isolation
: etilen-propilenic tipo G7 gum. Sheath: special termoplastic polimer quality M1. Filler: non vulcanized gum . Conductor: heated copperflexible wire. Protection (if required): copper wire braid. Fire reaction: non propagating fire; - law gas emission, toxic and corrosive gasses.
FG7OM1 0,6/1kV cable 3x4 mmq
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 535
| FIRST FLOOR LEVEL - MV/LV CABLES |  | 1060
| SECOND FLOOR LEVEL - MV/LV CABLES |  | 1015
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 505
| Total amount |  | 3115
A220.A20.A33 |  | m
FG7M1 0,6/1kV, FG7OM1 0,6/1kV CABLE FG7M1 0,6/1kV, FG7OM1 0,6/1kV in line with: CEI 20-13, 20-22/3 and subsequent variations. In line with tables: CEI-UNEL 35382, 35384. Nominal voltage: 600/1000 V. Isolation
: etilen-propilenic tipo G7 gum. Sheath: special termoplastic polimer quality M1. Filler: non vulcanized gum . Conductor: heated copperflexible wire. Protection (if required): copper wire braid. Fire reaction: non propagating fire; - law gas emission, toxic and corrosive gasses.
FG7OM1 0,6/1kV cable 3x6 mmq
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 220
| FIRST FLOOR LEVEL - MV/LV CABLES |  | 35
| SECOND FLOOR LEVEL - MV/LV CABLES |  | 150
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 90
| Total amount |  | 495
A220.A20.A47 |  | m
FG7M1 0,6/1kV, FG7OM1 0,6/1kV CABLE FG7M1 0,6/1kV, FG7OM1 0,6/1kV in line with: CEI 20-13, 20-22/3 and subsequent variations. In line with tables: CEI-UNEL 35382, 35384. Nominal voltage: 600/1000 V. Isolation
: etilen-propilenic tipo G7 gum. Sheath: special termoplastic polimer quality M1. Filler: non vulcanized gum . Conductor: heated copperflexible wire. Protection (if required): copper wire braid. Fire reaction: non propagating fire; - law gas emission, toxic and corrosive gasses.
FG7OM1 0,6/1kV cable 4x4 mmq
| SECOND FLOOR LEVEL - MV/LV CABLES |  | 120
| Total amount |  | 120
A220.A20.A50 |  | m
FG7M1 0,6/1kV, FG7OM1 0,6/1kV CABLE FG7M1 0,6/1kV, FG7OM1 0,6/1kV in line with: CEI 20-13, 20-22/3 and subsequent variations. In line with tables: CEI-UNEL 35382, 35384. Nominal voltage: 600/1000 V. Isolation
: etilen-propilenic tipo G7 gum. Sheath: special termoplastic polimer quality M1. Filler: non vulcanized gum . Conductor: heated copperflexible wire. Protection (if required): copper wire braid. Fire reaction: non propagating fire; - law gas emission, toxic and corrosive gasses.
FG7OM1 0,6/1kV cable 4x16 mmq
| SECOND FLOOR LEVEL - MV/LV CABLES |  | 70
| Total amount |  | 70
A220.A20.A51 |  | m
FG7M1 0,6/1kV, FG7OM1 0,6/1kV CABLE FG7M1 0,6/1kV, FG7OM1 0,6/1kV in line with: CEI 20-13, 20-22/3 and subsequent variations. In line with tables: CEI-UNEL 35382, 35384. Nominal voltage: 600/1000 V. Isolation
: etilen-propilenic tipo G7 gum. Sheath: special termoplastic polimer quality M1. Filler: non vulcanized gum . Conductor: heated copperflexible wire. Protection (if required): copper wire braid. Fire reaction: non propagating fire; - law gas emission, toxic and corrosive gasses.
FG7OM1 0,6/1kV cable 4x25 mmq
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 80
| Total amount |  | 80
A220.A20.A61 |  | m
FG7M1 0,6/1kV, FG7OM1 0,6/1kV CABLE FG7M1 0,6/1kV, FG7OM1 0,6/1kV in line with: CEI 20-13, 20-22/3 and subsequent variations. In line with tables: CEI-UNEL 35382, 35384. Nominal voltage: 600/1000 V. Isolation
: etilen-propilenic tipo G7 gum. Sheath: special termoplastic polimer quality M1. Filler: non vulcanized gum . Conductor: heated copperflexible wire. Protection (if required): copper wire braid. Fire reaction: non propagating fire; - law gas emission, toxic and corrosive gasses.
FG7OM1 0,6/1kV cable 5x2,5 mmq
| FIRST FLOOR LEVEL - MV/LV CABLES |  | 100
| SECOND FLOOR LEVEL - MV/LV CABLES |  | 35
| Total amount |  | 135
A220.A20.A62 |  | m
FG7M1 0,6/1kV, FG7OM1 0,6/1kV CABLE FG7M1 0,6/1kV, FG7OM1 0,6/1kV in line with: CEI 20-13, 20-22/3 and subsequent variations. In line with tables: CEI-UNEL 35382, 35384. Nominal voltage: 600/1000 V. Isolation
: etilen-propilenic tipo G7 gum. Sheath: special termoplastic polimer quality M1. Filler: non vulcanized gum . Conductor: heated copperflexible wire. Protection (if required): copper wire braid. Fire reaction: non propagating fire; - law gas emission, toxic and corrosive gasses.
FG7OM1 0,6/1kV cable 5x4 mmq
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 10
| FIRST FLOOR LEVEL - MV/LV CABLES |  | 1510
| Total amount |  | 1520
A220.A20.A63 |  | m
FG7M1 0,6/1kV, FG7OM1 0,6/1kV CABLE FG7M1 0,6/1kV, FG7OM1 0,6/1kV in line with: CEI 20-13, 20-22/3 and subsequent variations. In line with tables: CEI-UNEL 35382, 35384. Nominal voltage: 600/1000 V. Isolation
: etilen-propilenic tipo G7 gum. Sheath: special termoplastic polimer quality M1. Filler: non vulcanized gum . Conductor: heated copperflexible wire. Protection (if required): copper wire braid. Fire reaction: non propagating fire; - law gas emission, toxic and corrosive gasses.
FG7OM1 0,6/1kV cable 5x6 mmq
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 30
| FIRST FLOOR LEVEL - MV/LV CABLES |  | 505
| SECOND FLOOR LEVEL - MV/LV CABLES |  | 100
| Total amount |  | 635
A220.A20.A66 |  | m
FG7M1 0,6/1kV, FG7OM1 0,6/1kV CABLE FG7M1 0,6/1kV, FG7OM1 0,6/1kV in line with: CEI 20-13, 20-22/3 and subsequent variations. In line with tables: CEI-UNEL 35382, 35384. Nominal voltage: 600/1000 V. Isolation
: etilen-propilenic tipo G7 gum. Sheath: special termoplastic polimer quality M1. Filler: non vulcanized gum . Conductor: heated copperflexible wire. Protection (if required): copper wire braid. Fire reaction: non propagating fire; - law gas emission, toxic and corrosive gasses.
FG7OM1 0,6/1kV cable 5x25 mmq
| SECOND FLOOR LEVEL - MV/LV CABLES |  | 70
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 120
| Total amount |  | 190
A220.A20.A7 |  | m
FG7M1 0,6/1kV, FG7OM1 0,6/1kV CABLE FG7M1 0,6/1kV, FG7OM1 0,6/1kV in line with: CEI 20-13, 20-22/3 and subsequent variations. In line with tables: CEI-UNEL 35382, 35384. Nominal voltage: 600/1000 V. Isolation
: etilen-propilenic tipo G7 gum. Sheath: special termoplastic polimer quality M1. Filler: non vulcanized gum . Conductor: heated copperflexible wire. Protection (if required): copper wire braid. Fire reaction: non propagating fire; - law gas emission, toxic and corrosive gasses.
FG7M1 0,6/1kV cable 1x25 mmq
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 50
| Total amount |  | 50
A220.A20.A9 |  | m
FG7M1 0,6/1kV, FG7OM1 0,6/1kV CABLE FG7M1 0,6/1kV, FG7OM1 0,6/1kV in line with: CEI 20-13, 20-22/3 and subsequent variations. In line with tables: CEI-UNEL 35382, 35384. Nominal voltage: 600/1000 V. Isolation
: etilen-propilenic tipo G7 gum. Sheath: special termoplastic polimer quality M1. Filler: non vulcanized gum . Conductor: heated copperflexible wire. Protection (if required): copper wire braid. Fire reaction: non propagating fire; - law gas emission, toxic and corrosive gasses.
FG7M1 0,6/1kV cable 1x50 mmq
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 75
| Total amount |  | 75
A230.A10.A32 |  | m
FTG10M1 0,6/1kV CEI 20-45 FIRE RESISTANCE CABLE FTG10M1 0,6/1kV CEI 20-45, FTG10OM1 0,6/1kV CEI 20-45 In line with: CEI 20-22/3, 20-38, 20-45 and subsequent variations; EN50200. Nominal voltage: 600/1000 V. Isolation
etilenpropilenic mixture gum of quality G10. Sheath: special termoplastic polimer of quality M1. Filler: non toxic gum. Conductor: flexible tinned copper covered by isolation tape. non propagating fire; - law gas emission, toxic and corrosive gasses.
- continuation of at least 180 min a 750°C of mecchanical shock on 5 min.
FTG10OM1 0,6/1kV CEI 20-45 fire resistance cable 3x2,5 mmq
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 260
| FIRST FLOOR LEVEL - MV/LV CABLES |  | 1155
| SECOND FLOOR LEVEL - MV/LV CABLES |  | 505
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 45
| Total amount |  | 1965
A230.A10.A55 |  | m
FTG10M1 0,6/1kV CEI 20-45 FIRE RESISTANCE CABLE FTG10M1 0,6/1kV CEI 20-45, FTG10OM1 0,6/1kV CEI 20-45 In line with: CEI 20-22/3, 20-38, 20-45 and subsequent variations; EN50200. Nominal voltage: 600/1000 V. Isolation
etilenpropilenic mixture gum of quality G10. Sheath: special termoplastic polimer of quality M1. Filler: non toxic gum. Conductor: flexible tinned copper covered by isolation tape. non propagating fire; - law gas emission, toxic and corrosive gasses.
- continuation of at least 180 min a 750°C of mecchanical shock on 5 min.
FTG10M1 0,6/1kV CEI 20-45 fire resistance cable 5x10 mmq
| SECOND FLOOR LEVEL - MV/LV CABLES |  | 5
| Total amount |  | 5
A250.A10.A1 |  | m
BARE COPPER CABLE In line with: CEI 7-1 and subsequent variations; UNI 5649/1. Conductor: bare with elementar wires (n.7 per section from 16 to 50 mmq and n.19 from 70 to 150 mmq of diametre non under
1,8mm) flat surface, cylindric, regular of raw copper or heated type CU-ETP with percentage of Cu Ag 99,9%.
Bare copper cable 16mmq
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 90
| FIRST FLOOR LEVEL - MV/LV CABLES |  | 220
| SECOND FLOOR LEVEL - MV/LV CABLES |  | 80
| GROUND FLOOR LEVEL - MV/LV CABLES |  | 50
| Total amount |  | 440
TOTAL CONDUCTORS, CABLES AND ACCESSORIES
02 - CONDUITS
B10.A10.A2 |  | m
METAL TRUNKING IN CLOSED VERSION, ZINC PLATED PASSERELLA PORTACAVI IN ACCIAIO ZINCATO A CALDO PER IMMERSIONE DOPO LA LAVORAZIONE in line with: CEI 23-76, CEI 7-6 and subsequent variations . Shock resistance: > 1J on ambience temperature
(20°C ±5). Meccanical resistance: minimal acceptable load (values measured for maximal deformation curve of 1/200 of intermediate load, junction on 1/5 between suporters) measured in line with norms of the product : - closed channel with h. 75mm
, Light between two suporters 1,5m: * 145 kg/m for channel width 50-75 mm; * 149 kg/m for channel width 100 mm; * 158 kg/m for channel width 150 mm; * 165 kg/m for channel width 200 mm; * 204 kg/m for channel width 3
00 mm; * 208 kg/m for channel width 400 mm; * 214 kg/m for channel width 500-600 mm; - punctured channel with h. 75mm, light between two supporters 1,5m: * 145 kg/m for channel width 50-75 mm; * 156 kg/m for channel width 100 mm
; * 170 kg/m for channel width150 mm; * 190 kg/m for channel width 200-300 mm; * 201 kg/m for channel width 400 mm; * 208 kg/m for channel width 500 mm; * 217 kg/m for channel width 600 mm. Electrical caracteristics
: - electric Continuity garantita guaranteed by manufacturer with lectrical reistance (on 12V c.a. max 50Hz, 25A): =< 0,005 ohm per meter and e <= 0,05 ohm in proximity of junctio. Construction caracteristics: - chase composed by one piece of perfored sheet
closed depending on type, with boarded angles or anti cut reinforced produced by rolling and zinced on fire after production with zinc Zn A 99,90%; - thickeness of the sheet: min.0,8 mm (untill 150x75) and
1 mm and over (for bigger production); - medium thickeness of zinc surface: 57 micron +/-10% for single face ; - medium mass of zinc surface: 400 g/m2 +/-10% for single face; - cover (when required) in zinced steal
with same treatment and construction caracteristics s.d., click closure or trough connected grips. Protection level (in case of trunking with full bottom/closed with cover): min. IP30, for the entire system.
Zinc plated metal trunking, perforated base, size 100x75mm
| SECOND FLOOR LEVEL - MV/LV RACEWAYS |  | 43
| ROOF LEVEL - MV/LV RACEWAYS |  | 84
| Total amount |  | 127
B10.A10.A22 |  | m
METAL TRUNKING IN CLOSED VERSION, ZINC PLATED PASSERELLA PORTACAVI IN ACCIAIO ZINCATO A CALDO PER IMMERSIONE DOPO LA LAVORAZIONE in line with: CEI 23-76, CEI 7-6 and subsequent variations . Shock resistance: > 1J on ambience temperature
(20°C ±5). Meccanical resistance: minimal acceptable load (values measured for maximal deformation curve of 1/200 of intermediate load, junction on 1/5 between suporters) measured in line with norms of the product : - closed channel with h. 75mm
, Light between two suporters 1,5m: * 145 kg/m for channel width 50-75 mm; * 149 kg/m for channel width 100 mm; * 158 kg/m for channel width 150 mm; * 165 kg/m for channel width 200 mm; * 204 kg/m for channel width 3
00 mm; * 208 kg/m for channel width 400 mm; * 214 kg/m for channel width 500-600 mm; - punctured channel with h. 75mm, light between two supporters 1,5m: * 145 kg/m for channel width 50-75 mm; * 156 kg/m for channel width 100 mm
; * 170 kg/m for channel width150 mm; * 190 kg/m for channel width 200-300 mm; * 201 kg/m for channel width 400 mm; * 208 kg/m for channel width 500 mm; * 217 kg/m for channel width 600 mm. Electrical caracteristics
: - electric Continuity garantita guaranteed by manufacturer with lectrical reistance (on 12V c.a. max 50Hz, 25A): =< 0,005 ohm per meter and e <= 0,05 ohm in proximity of junctio. Construction caracteristics: - chase composed by one piece of perfored sheet
closed depending on type, with boarded angles or anti cut reinforced produced by rolling and zinced on fire after production with zinc Zn A 99,90%; - thickeness of the sheet: min.0,8 mm (untill 150x75) and
1 mm and over (for bigger production); - medium thickeness of zinc surface: 57 micron +/-10% for single face ; - medium mass of zinc surface: 400 g/m2 +/-10% for single face; - cover (when required) in zinced steal
with same treatment and construction caracteristics s.d., click closure or trough connected grips. Protection level (in case of trunking with full bottom/closed with cover): min. IP30, for the entire system.
Metal trunking cover 100 mm
| SECOND FLOOR LEVEL - MV/LV RACEWAYS |  | 43
| ROOF LEVEL - MV/LV RACEWAYS |  | 88
| Total amount |  | 131
B10.A10.A24 |  | m
METAL TRUNKING IN CLOSED VERSION, ZINC PLATED PASSERELLA PORTACAVI IN ACCIAIO ZINCATO A CALDO PER IMMERSIONE DOPO LA LAVORAZIONE in line with: CEI 23-76, CEI 7-6 and subsequent variations . Shock resistance: > 1J on ambience temperature
(20°C ±5). Meccanical resistance: minimal acceptable load (values measured for maximal deformation curve of 1/200 of intermediate load, junction on 1/5 between suporters) measured in line with norms of the product : - closed channel with h. 75mm
, Light between two suporters 1,5m: * 145 kg/m for channel width 50-75 mm; * 149 kg/m for channel width 100 mm; * 158 kg/m for channel width 150 mm; * 165 kg/m for channel width 200 mm; * 204 kg/m for channel width 3
00 mm; * 208 kg/m for channel width 400 mm; * 214 kg/m for channel width 500-600 mm; - punctured channel with h. 75mm, light between two supporters 1,5m: * 145 kg/m for channel width 50-75 mm; * 156 kg/m for channel width 100 mm
; * 170 kg/m for channel width150 mm; * 190 kg/m for channel width 200-300 mm; * 201 kg/m for channel width 400 mm; * 208 kg/m for channel width 500 mm; * 217 kg/m for channel width 600 mm. Electrical caracteristics
: - electric Continuity garantita guaranteed by manufacturer with lectrical reistance (on 12V c.a. max 50Hz, 25A): =< 0,005 ohm per meter and e <= 0,05 ohm in proximity of junctio. Construction caracteristics: - chase composed by one piece of perfored sheet
closed depending on type, with boarded angles or anti cut reinforced produced by rolling and zinced on fire after production with zinc Zn A 99,90%; - thickeness of the sheet: min.0,8 mm (untill 150x75) and
1 mm and over (for bigger production); - medium thickeness of zinc surface: 57 micron +/-10% for single face ; - medium mass of zinc surface: 400 g/m2 +/-10% for single face; - cover (when required) in zinced steal
with same treatment and construction caracteristics s.d., click closure or trough connected grips. Protection level (in case of trunking with full bottom/closed with cover): min. IP30, for the entire system.
Metal trunking cover 200 mm
| SECOND FLOOR LEVEL - MV/LV RACEWAYS |  | 42
| Total amount |  | 42
B10.A10.A4 |  | m
METAL TRUNKING IN CLOSED VERSION, ZINC PLATED PASSERELLA PORTACAVI IN ACCIAIO ZINCATO A CALDO PER IMMERSIONE DOPO LA LAVORAZIONE in line with: CEI 23-76, CEI 7-6 and subsequent variations . Shock resistance: > 1J on ambience temperature
(20°C ±5). Meccanical resistance: minimal acceptable load (values measured for maximal deformation curve of 1/200 of intermediate load, junction on 1/5 between supporters) measured in line with norms of the product : - closed channel with h. 75mm
, Light between two suporters 1,5m: * 145 kg/m for channel width 50-75 mm; * 149 kg/m for channel width 100 mm; * 158 kg/m for channel width 150 mm; * 165 kg/m for channel width 200 mm; * 204 kg/m for channel width 3
00 mm; * 208 kg/m for channel width 400 mm; * 214 kg/m for channel width 500-600 mm; - punctured channel with h. 75mm, light between two supporters 1,5m: * 145 kg/m for channel width 50-75 mm; * 156 kg/m for channel width 100 mm
; * 170 kg/m for channel width150 mm; * 190 kg/m for channel width 200-300 mm; * 201 kg/m for channel width 400 mm; * 208 kg/m for channel width 500 mm; * 217 kg/m for channel width 600 mm. Electrical caracteristics
: - electric continuity guaranteed by manufacturer with electrical reistance (on 12V c.a. max 50Hz, 25A): =< 0,005 ohm per meter and <= 0,05 ohm in proximity of junction. Construction caracteristics: - chase composed by one piece of perfored sheet
closed depending on type, with boarded angles or anti cut reinforced produced by rolling and zinced on fire after production with zinc Zn A 99,90%; - thickeness of the sheet: min.0,8 mm (untill 150x75) and
1 mm and over (for bigger production); - medium thickeness of zinc surface: 57 micron +/-10% for single face ; - medium mass of zinc surface: 400 g/m2 +/-10% for single face; - cover (when required) in zinced steal
with same treatment and construction caracteristics s.d., click closure or trough connected grips. Protection level (in case of trunking with full bottom/closed with cover): min. IP30, for the entire system.
Zinc plated metal trunking, perforated base, size 200x75mm
| SECOND FLOOR LEVEL - MV/LV RACEWAYS |  | 42
| Total amount |  | 42
B10.A40.A1 |  | m
ZINC PLATED WIRE MESH PASSERELLA PORTACAVI A RETE IN FILO DI ACCIAIO ZINCATO A CALDO PER IMMERSIONE DOPO LA LAVORAZIONE In line with: CEI 23-76, CEI 7-6 and subsequent variations. Shock resistance: > 1 J on ambience tempereture (20°+/-
5). Meccanical resistance: minimal acceptable load (values measured for maximal deformation curve of 1/200 of intermediate load, junction on 1/5 between supporters) measured in line with norms of the product: - supporters h. 50mm, Light between two suporters
1,5m: * 18 kg/m for channel width 50-100 mm; * 27 kg/m for channel width 150 mm; * 33 kg/m per for channel width200 mm; * 63 kg/m for channel width 300 mm; * 104 kg/m for channel width400 mm; * 12
0 kg/m for channel width 500-600 mm; - passerelle con h. 100mm, Light between two suporters 1,5m: * 37 kg/m for channel width100 mm; * 53 kg/m for channel width 150 mm; * 73 kg/m for channel width 200 mm; * 104 kg/m
for channel width 300-400 mm; * 125 kg/m for channel width 500-600 mm. Electric caracteristics: - electric continuity guaranteed by manufacturer with electrical reistance (a 12V c.a. max 50Hz, 25A): =< 0,005 ohm per meter and <= 0,05 ohm in
proximity of junction. Construction caracteristics: - channel realised in welded steal wire, heat galvanized after production, previousely cleanned and degreased, final colloration (where required by type)
with epossidich and poliester resin; - security border absent of live angles; - zinc surface minimal soil mass: 330 g/m2 +/-10%; - medium zinc soil: 50 micron +/- 10%. - cover
(when required) in steal with same treatment and caracteristics as the chase , closure with click or connected grips . Fire reaction: collor (when required) autoestingueting.
Zinc plated wire mesh, size 50x55mm
| ROOF LEVEL - MV/LV RACEWAYS |  | 16
| Total amount |  | 16
B10.A40.A2 |  | m
ZINC PLATED WIRE MESH PASSERELLA PORTACAVI A RETE IN FILO DI ACCIAIO ZINCATO A CALDO PER IMMERSIONE DOPO LA LAVORAZIONE In line with: CEI 23-76, CEI 7-6 and subsequent variations. Shock resistance: > 1 J on ambience tempereture (20°+/-
5). Meccanical resistance: minimal acceptable load (values measured for maximal deformation curve of 1/200 of intermediate load, junction on 1/5 between supporters) measured in line with norms of the product: - supporters h. 50mm, Light between two suporters
1,5m: * 18 kg/m for channel width 50-100 mm; * 27 kg/m for channel width 150 mm; * 33 kg/m per for channel width200 mm; * 63 kg/m for channel width 300 mm; * 104 kg/m for channel width400 mm; * 12
0 kg/m for channel width 500-600 mm; - passerelle con h. 100mm, Light between two suporters 1,5m: * 37 kg/m for channel width100 mm; * 53 kg/m for channel width 150 mm; * 73 kg/m for channel width 200 mm; * 104 kg/m
for channel width 300-400 mm; * 125 kg/m for channel width 500-600 mm. Electric caracteristics: - electric continuity guaranteed by manufacturer with electrical reistance (a 12V c.a. max 50Hz, 25A): =< 0,005 ohm per meter and <= 0,05 ohm in
proximity of junction. Construction caracteristics: - channel realised in welded steal wire, heat galvanized after production, previousely cleanned and degreased, final colloration (where required by type)
with epossidich and poliester resin; - security border absent of live angles; - zinc surface minimal soil mass: 330 g/m2 +/-10%; - medium zinc soil: 50 micron +/- 10%. - cover
(when required) in steal with same treatment and caracteristics as the chase , closure with click or connected grips . Fire reaction: collor (when required) autoestingueting.
Zinc plated wire mesh, size 100x55mm
| GROUND FLOOR LEVEL - MV/LV RACEWAYS |  | 94
| FIRST FLOOR LEVEL - MV/LV RACEWAYS |  | 384
| SECOND FLOOR LEVEL - MV/LV RACEWAYS |  | 144
| ROOF LEVEL - MV/LV RACEWAYS |  | 20
| GROUND FLOOR LEVEL - MV/LV RACEWAYS |  | 13
| Total amount |  | 655
B10.A40.A4 |  | m
ZINC PLATED WIRE MESH PASSERELLA PORTACAVI A RETE IN FILO DI ACCIAIO ZINCATO A CALDO PER IMMERSIONE DOPO LA LAVORAZIONE In line with: CEI 23-76, CEI 7-6 and subsequent variations. Shock resistance: > 1 J on ambience tempereture (20°+/-
5). Meccanical resistance: minimal acceptable load (values measured for maximal deformation curve of 1/200 of intermediate load, junction on 1/5 between supporters) measured in line with norms of the product: - supporters h. 50mm, Light between two suporters
1,5m: * 18 kg/m for channel width 50-100 mm; * 27 kg/m for channel width 150 mm; * 33 kg/m per for channel width200 mm; * 63 kg/m for channel width 300 mm; * 104 kg/m for channel width400 mm; * 12
0 kg/m for channel width 500-600 mm; - passerelle con h. 100mm, Light between two suporters 1,5m: * 37 kg/m for channel width100 mm; * 53 kg/m for channel width 150 mm; * 73 kg/m for channel width 200 mm; * 104 kg/m
for channel width 300-400 mm; * 125 kg/m for channel width 500-600 mm. Electric caracteristics: - electric continuity guaranteed by manufacturer with electrical reistance (a 12V c.a. max 50Hz, 25A): =< 0,005 ohm per meter and <= 0,05 ohm in
proximity of junction. Construction caracteristics: - channel realised in welded steal wire, heat galvanized after production, previousely cleanned and degreased, final colloration (where required by type)
with epossidich and poliester resin; - security border absent of live angles; - zinc surface minimal soil mass: 330 g/m2 +/-10%; - medium zinc soil: 50 micron +/- 10%. - cover
(when required) in steal with same treatment and caracteristics as the chase , closure with click or connected grips . Fire reaction: collor (when required) autoestingueting.
Zinc plated wire mesh, size 200x55mm
| GROUND FLOOR LEVEL - MV/LV RACEWAYS |  | 113
| FIRST FLOOR LEVEL - MV/LV RACEWAYS |  | 170
| SECOND FLOOR LEVEL - MV/LV RACEWAYS |  | 88
| GROUND FLOOR LEVEL - MV/LV RACEWAYS |  | 48
| Total amount |  | 419
B10.A40.A5 |  | m
ZINC PLATED WIRE MESH PASSERELLA PORTACAVI A RETE IN FILO DI ACCIAIO ZINCATO A CALDO PER IMMERSIONE DOPO LA LAVORAZIONE In line with: CEI 23-76, CEI 7-6 and subsequent variations. Shock resistance: > 1 J on ambience tempereture (20°+/-
5). Meccanical resistance: minimal acceptable load (values measured for maximal deformation curve of 1/200 of intermediate load, junction on 1/5 between supporters) measured in line with norms of the product: - supporters h. 50mm, Light between two suporters
1,5m: * 18 kg/m for channel width 50-100 mm; * 27 kg/m for channel width 150 mm; * 33 kg/m per for channel width200 mm; * 63 kg/m for channel width 300 mm; * 104 kg/m for channel width400 mm; * 12
0 kg/m for channel width 500-600 mm; - passerelle con h. 100mm, Light between two suporters 1,5m: * 37 kg/m for channel width100 mm; * 53 kg/m for channel width 150 mm; * 73 kg/m for channel width 200 mm; * 104 kg/m
for channel width 300-400 mm; * 125 kg/m for channel width 500-600 mm. Electric caracteristics: - electric continuity guaranteed by manufacturer with electrical reistance (a 12V c.a. max 50Hz, 25A): =< 0,005 ohm per meter and <= 0,05 ohm in
proximity of junction. Construction caracteristics: - channel realised in welded steal wire, heat galvanized after production, previousely cleanned and degreased, final colloration (where required by type)
with epossidich and poliester resin; - security border absent of live angles; - zinc surface minimal soil mass: 330 g/m2 +/-10%; - medium zinc soil: 50 micron +/- 10%. - cover
(when required) in steal with same treatment and caracteristics as the chase , closure with click or connected grips . Fire reaction: collor (when required) autoestingueting.
Zinc plated wire mesh, size 300x55mm
| FIRST FLOOR LEVEL - MV/LV RACEWAYS |  | 294
| SECOND FLOOR LEVEL - MV/LV RACEWAYS |  | 92
| Total amount |  | 386
B10.A40.A6 |  | m
ZINC PLATED WIRE MESH PASSERELLA PORTACAVI A RETE IN FILO DI ACCIAIO ZINCATO A CALDO PER IMMERSIONE DOPO LA LAVORAZIONE In line with: CEI 23-76, CEI 7-6 and subsequent variations. Shock resistance: > 1 J on ambience tempereture (20°+/-
5). Meccanical resistance: minimal acceptable load (values measured for maximal deformation curve of 1/200 of intermediate load, junction on 1/5 between supporters) measured in line with norms of the product: - supporters h. 50mm, Light between two suporters
1,5m: * 18 kg/m for channel width 50-100 mm; * 27 kg/m for channel width 150 mm; * 33 kg/m per for channel width200 mm; * 63 kg/m for channel width 300 mm; * 104 kg/m for channel width400 mm; * 12
0 kg/m for channel width 500-600 mm; - passerelle con h. 100mm, Light between two suporters 1,5m: * 37 kg/m for channel width100 mm; * 53 kg/m for channel width 150 mm; * 73 kg/m for channel width 200 mm; * 104 kg/m
for channel width 300-400 mm; * 125 kg/m for channel width 500-600 mm. Electric caracteristics: - electric continuity guaranteed by manufacturer with electrical reistance (a 12V c.a. max 50Hz, 25A): =< 0,005 ohm per meter and <= 0,05 ohm in
proximity of junction. Construction caracteristics: - channel realised in welded steal wire, heat galvanized after production, previousely cleanned and degreased, final colloration (where required by type)
with epossidich and poliester resin; - security border absent of live angles; - zinc surface minimal soil mass: 330 g/m2 +/-10%; - medium zinc soil: 50 micron +/- 10%. - cover
(when required) in steal with same treatment and caracteristics as the chase , closure with click or connected grips . Fire reaction: collor (when required) autoestingueting.
Zinc plated wire mesh, size 400x55mm
| SECOND FLOOR LEVEL - MV/LV RACEWAYS |  | 17
| Total amount |  | 17
B30.A10.A3 |  | m
PVC FLEXIBLE PIPE TUBO PROTETTIVO PIEGHEVOLE - CORRUGATO IN PVC PER POSA SOTTO TRACCIA In line with: CEI 23-82, 23-39 and subsequent variations. Classification: non under 3321. Crush resistance: >= 750N.
Shock resistance: >= 2J. Electric isolation reistance: >= 100Mohm on 500V for 1 min. Dielectric strenght: >= 2kV/mm on 50Hz for 15 min. Fire reaction: non propagating fire. System protection level: min. IP4X.
PVC flexible pipe D=25mm
| GROUND FLOOR LEVEL - MV/LV RACEWAYS |  | 10
| Total amount |  | 10
B30.A20.A25 |  | m
PVC RIGID PIPE TUBO PROTETTIVO RIGIDO MEDIO IN PVC PER POSA IN VISTA O SOTTOTRACCIA In line with: 23-51, 23-54 and subsequent variation. In line with tables: CEI-UNEL 37118, 37119, 37120. Classification: non under 3321.
Crush resistance: >= 750N. Shock resistance: >= 2J. Electric isolation reistance: >= 100Mohm a 500V per 1 min. Dielectric strenght: >= 2kV/mm a 50Hz per 15 min. Fire reaction: non propagating fire; -
low composition of alogen gasses (in line with CEI 20-37). System protection level: indicated by tape
PVC rigid pipe IP65 D=40mm
| GROUND FLOOR LEVEL - MV/LV RACEWAYS |  | 486
| GROUND FLOOR LEVEL - MV/LV RACEWAYS |  | 156
| Total amount |  | 642
B40.A10.A6 |  | m
ZINC PLATED METAL PIPE TUBO PROTETTIVO RIGIDO FILETTABILE IN ACCIAIO ZINCATO ELETTROSALDATO Conformita' alle norme: 23-39, 23-54 e successive varianti; UL94 V-1. Classificazione: non inferiore a 5557. Crush resistance: >= 4000N.
Shock resistance: >= 6,8J. Electrical resistence: < 5mohm/m. Construction caracteristics: - rigid tube profiled by steal zinc sheets with Sendzimir method, welded with zinc on welding points, cold flexible;
junctions and connections with other elements with ISO metric thread as guarantee of metallic as well as required protection level. - color (if required by type) based on epossidic resine
. System protection level: min. IP4X. Fire reaction: color (if), autoestingueting.
Zinc plated metal pipe D=50mm
| ROOF LEVEL - MV/LV RACEWAYS |  | 39
| Total amount |  | 39
B70.A21.A1 |  | dm2
FLAME-FRINGE BARRIER WITH REMOVABLE BAGS BARRIERA FRANGI-FIAMMA A SACCHETTI AMOVIBILI Flame-fringe barrier composed by tamponage bags longitudinal disposed on cables wall route or cement channel In line with Minsitry of interiors regulation
n.91 del 14.09.61. Construction caracteristics : - tamponage bags in glass fiber sacchetti di contenimento in tessuto di fibra di vetro fitted plot, filled with tissotropic mixture having tickeness and width capable to be easely positioned on order to guarantee tamponage of interstices
and having length appropriate to realize barrier rage which will guarantee required fire resistance ; Minimal tickeness of the barrier: appprox. 200 mm equal to bag width
Fire reaction: untill resistance class REI 180.
Flame-fringe barrier with removable bags REI 180
| GROUND FLOOR LEVEL - MV/LV RACEWAYS |  | 10
| FIRST FLOOR LEVEL - MV/LV RACEWAYS |  | 20
| SECOND FLOOR LEVEL - MV/LV RACEWAYS |  | 25
| Total amount |  | 55
C20.A30.A7 |  | n
METALLIC BOX FOR INDOOR CASSETTA MODULARE IN LEGA LEGGERA COMPONIBILE IN BATTERIE Caracteristics: - chase and cover in light cromatised alloy and collored in furnace ; - gasket in age proof elastomer guarnizione; - wall windows provided by eccessories fixing screws and for coupling with other boxes in stainless steal
; - covers, closed or with zipper, fixed by screws in stainless steal; - fixing of boxes with feets ; - accessories: flat or screwed flanges
, blind or with unions, multi arms connection points, repulsive or with angle flanges. Level of protection: min.IP55.
Metallic box for indoor IP55, size 370x370x160mm
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 3
| Total amount |  | 3
C30.A61.A1 |  | n
FLOOR BOX TORRETTA A SCOMPARSA MULTIUTENZA concealed socket-holder tower for floating floors appropriate for instalation of FM utilities, telephone and data transmittion . In line with: CEI 23-73 and subsequent variations. Caracteristics
: - box dimension of at least 300x300x110 in termoplastic materiall , anti shock and autoestingueting (UL 94-V0) divided in n. 8 divisions separeted between tham, located all over the perimeter ; - socket moldings having same caracteristics as boxes
, click instalable in aposit chase; - cover in termoplastic autoestingieting material (UL 94 V-1) with external surface in rugged stainless steal, completed by elastic zipper with opening up to
180^, protection of wires, strap protection or excessive zipper openning, automatic closure of the cover and cable floor exit; - cable cover frame with treated angles; - positioning possibility of one box on at least two laterals of the cassett for the instalation of modular switches with load up to
3x16A for ptotection of BT utilities; - positioning of socket in vertical position or inlined of at least 45^ respectively to the vertical
; protection doors for eventual command sockets in horizontal position; - cable tubes positioned on exit doors in order to avoid over positioning of cables and closure of cover ; - walls of departments and connection boxes
perfored for clamps or cable press. Protection level: IP4X on the cover bord and between floor and frame ; IP2X in proximity of cable exit from the cover.
Floor box with inox cover, size 300x300mm
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 10
| FIRST FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 216
| SECOND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 30
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 21
| Total amount |  | 277
TOTAL CONDUITS
03 - DISTRIBUTION BOARDS
D30.A30.A1 |  | globally
INSULATED SUB-DISTRIBUTION BOARD CENTRALINO MODULARE ISOLANTE In line with: CEI 17-13/3 and subsequents variations. Caracteristics: - device chase, in wall or on wall, in termoplastic autoestingueting material
, provided with perforations for tubes and isolated holes for chase fixing and adjustment ; - device chase with one or more DIN conductor ; - phase, neutro and gound connections
; - attested connections for line in departure and arrival ; - zipped closing door full or transparent type ; - cover covering device with one or more windows
; - perforation cover for non used spaces closure. One wire electric scheme, caracteristics and calibration of devices, auxiliars, tools, etc., are indicated in grafic tables. Special devices such are bus command systems, light regulation units, centralized system command are not included in the price, and will be separately quoted.
Distribution board is compose by following elements and devices: - central unit in termoplastic material installed in the wall of total dimensions (HxBxP): 420x300x85, protection level IP40; - n°2 automatic differential modular switch 2x63A, Id=30mA; - n°2 modular fuses box 2x32A complete of fuses; - n°2 signal lamp; - n°1 magnetotermic modular automatic switch1x20A+N; - n°5 magnetotermic modular automatic switch 1x16A+N; - n°3 magnetotermic modular automatic switch1x10A+N; - n°1 contactor 1x20A with auxiliar contact and selector 3 positions; - n°1 modular fuses box 1x20A+N complete of fuses; - grounding bar inside distribution board.
DB_L0/U/...
| GROUND FLOOR LEVEL - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 5
| Total amount |  | 5
D30.A30.A10 |  | globally
INSULATED SUB-DISTRIBUTION BOARD CENTRALINO MODULARE ISOLANTE In line with: CEI 17-13/3 and subsequents variations. Caracteristics: - device chase, in wall or on wall, in termoplastic autoestingueting material
, provided with perforations for tubes and isolated holes for chase fixing and adjustment ; - device chase with one or more DIN conductor ; - phase, neutro and gound connections
; - attested connections for line in departure and arrival ; - zipped closing door full or transparent type ; - cover covering device with one or more windows
; - perforation cover for non used spaces closure. One wire electric scheme, caracteristics and calibration of devices, auxiliars, tools, etc., are indicated in grafic tables. Special devices such are bus command systems, light regulation units, centralized system command are not included in the price, and will be separately quoted.
Distribution board is compose by following elements and devices: - central unit in termoplastic material installed on the wall of total dimensions (HxBxP): 420x330x140, protection level IP40; - n°1 automatic differential modular switch 2x63A, Id=30mA; - n°1 automatic differential modular switch 2x50A, Id=30mA; - n°2 modular fuses box 2x32A complete of fuses; - n°2 signal lamp; - n°1 magnetotermic modular automatic switch 1x25A+N; - n°5 magnetotermic modular automatic switch 1x16A+N; - n°1 magnetotermic modular automatic switch1x10A+N; - n°1 contactor 2x12A AC3 with auxiliar switch; - n°1 contactor 3x20A AC3 with auxiliar contact and selector 3 positions; - grounding bar inside distribution board.
SDB_L2/1
| SECOND FLOOR LEVEL - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 1
| Total amount |  | 1
D30.A30.A11 |  | globally
INSULATED SUB-DISTRIBUTION BOARD CENTRALINO MODULARE ISOLANTE In line with: CEI 17-13/3 and subsequents variations. Caracteristics: - device chase, in wall or on wall, in termoplastic autoestingueting material
, provided with perforations for tubes and isolated holes for chase fixing and adjustment ; - device chase with one or more DIN conductor ; - phase, neutro and gound connections
; - attested connections for line in departure and arrival ; - zipped closing door full or transparent type ; - cover covering device with one or more windows
; - perforation cover for non used spaces closure. One wire electric scheme, caracteristics and calibration of devices, auxiliars, tools, etc., are indicated in grafic tables. Special devices such are bus command systems, light regulation units, centralized system command are not included in the price, and will be separately quoted.
Distribution board is compose by following elements and devices: - central unit in termoplastic material installed on the wall of total dimensions (HxBxP): 420x330x140, protection level IP40; - n°1 automatic differential modular switch 2x63A, Id=30mA; - n°1 automatic differential modular switch 2x50A, Id=30mA; - n°2 modular fuses box 2x32A complete of fuses; - n°2 signal lamp; - n°1 magnetotermic modular automatic switch 1x25A+N; - n°5 magnetotermic modular automatic switch 1x16A+N; - n°1 magnetotermic modular automatic switch1x10A+N; - n°1 contactor 2x12A AC3 with auxiliar switch; - n°1 contactor 3x20A AC3 with auxiliar contact and selector 3 positions; - grounding bar inside distribution board.
SDB_L2/2
| SECOND FLOOR LEVEL - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 1
| Total amount |  | 1
D30.A30.A12 |  | globally
INSULATED SUB-DISTRIBUTION BOARD CENTRALINO MODULARE ISOLANTE In line with: CEI 17-13/3 and subsequents variations. Caracteristics: - device chase, in wall or on wall, in termoplastic autoestingueting material
, provided with perforations for tubes and isolated holes for chase fixing and adjustment ; - device chase with one or more DIN conductor ; - phase, neutro and gound connections
; - attested connections for line in departure and arrival ; - zipped closing door full or transparent type ; - cover covering device with one or more windows
; - perforation cover for non used spaces closure. One wire electric scheme, caracteristics and calibration of devices, auxiliars, tools, etc., are indicated in grafic tables. Special devices such are bus command systems, light regulation units, centralized system command are not included in the price, and will be separately quoted.
Distribution board is compose by following elements and devices: - central unit in termoplastic material installed on the wall of total dimensions (HxBxP): 950x700x200, protection level IP40; - n°1 manual modular selector switch 4x63A; - n°3 manual modular selector switch 4x50A; - n°2 modular fuses box 4x32A complete of fuses; - n°6 signal lamp; - n°1 magnetotermic modular automatic differential switch 4x25A, Id=30mA; - n°1 magnetotermic modular automatic differential switch 4x10A, Id=300mA;
- n°7 magnetotermic modular automatic differential switch 1x16A+N, Id=30mA; - n°7 magnetotermic modular automatic differential switch 1x10A+N, Id=300mA; - n°4 contactor 3x12A AC3 with auxiliar contacts; - n°1 contactor 3x20A AC3 with auxiliar contacts and selector 3 positions; - n°2 modular fuses box 2x20A complete of fuses; - n°1 transformator 230/24V voltage 150VA; - grounding bar inside distribution board.
SDB_L2/3
| SECOND FLOOR LEVEL - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 1
| Total amount |  | 1
D30.A30.A13 |  | globally
INSULATED SUB-DISTRIBUTION BOARD CENTRALINO MODULARE ISOLANTE In line with: CEI 17-13/3 and subsequents variations. Caracteristics: - device chase, in wall or on wall, in termoplastic autoestingueting material
, provided with perforations for tubes and isolated holes for chase fixing and adjustment ; - device chase with one or more DIN conductor ; - phase, neutro and gound connections
; - attested connections for line in departure and arrival ; - zipped closing door full or transparent type ; - cover covering device with one or more windows
; - perforation cover for non used spaces closure. One wire electric scheme, caracteristics and calibration of devices, auxiliars, tools, etc., are indicated in grafic tables. Special devices such are bus command systems, light regulation units, centralized system command are not included in the price, and will be separately quoted.
Distribution board is compose by following elements and devices: - central unit in termoplastic material installed on the wall of total dimensions (HxBxP): 420x330x140, protection level IP40; - n°1 automatic differentiale modular switch 2x63A, Id=30mA; - n°1 automatic differentiale modular switch 2x50A, Id=30mA; - n°2 modular fuses box 2x32A complete of fuses; - n°2 signal lamp; - n°1 magnetotermic automatic modular switch 1x25A+N; - n°5 magnetotermic automatic modular switch 1x16A+N; - n°1 magnetotermic automatic modular switch 1x10A+N; - n°1 contactor 2x12A AC3 with auxiliar contact; - n°1 contactor 3x20A AC3 with auxiliar contact and selector 3 positions; - grounding bar inside distribution board.
SDB_L2/4
| SECOND FLOOR LEVEL - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 1
| Total amount |  | 1
D30.A30.A17 |  | globally
INSULATED SUB-DISTRIBUTION BOARD CENTRALINO MODULARE ISOLANTE In line with: CEI 17-13/3 and subsequents variations. Caracteristics: - device chase, in wall or on wall, in termoplastic autoestingueting material
, provided with perforations for tubes and isolated holes for chase fixing and adjustment ; - device chase with one or more DIN conductor ; - phase, neutro and gound connections
; - attested connections for line in departure and arrival ; - zipped closing door full or transparent type ; - cover covering device with one or more windows
; - perforation cover for non used spaces closure. One wire electric scheme, caracteristics and calibration of devices, auxiliars, tools, etc., are indicated in grafic tables. Special devices such are bus command systems, light regulation units, centralized system command are not included in the price, and will be separately quoted.
Distribution board is compose by following elements and devices: - central unit in termoplastic material installed on the wall of total dimensions (HxBxP): 550x460x260, Protection level IP40; - n°1 manual modular selector switch 4x63A; - n°2 contactor 4x26A AC3 with auxiliar contact and signal lamp; - n°2 telerutor 2x20A; - n°2 modular fuse box 4x32A complete of fuses; - n°6 signal lamp; - grounding bar inside distribution board.
DB_L2/M/LIFT
| SECOND FLOOR LEVEL - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 1
| Total amount |  | 1
D40.A10.A21 |  | globally
METALLIC DISTRIBUTION BOARD QUADRO DI DISTRIBUZIONE SECONDARIA DI TIPO METALLICO In line with CEI 17-13/1(95) and subsequents variations. Caracteristics: - supporting modular structure composed by metalic chase in steal or pressed sheets of at least 20/10
, complete by fixing slotting, zippers, guides, supporting profiles for device fixing ; -floor fixing chase or for adjustments of profiles in steal steanless
twice basic colloring and surface solloring in black, complete by regolable feets with rusticated base and perforated in order to permit floor fixing
with dowels and and glue (where required); - lateral and back covering pannels in bordered and collored sheets, equiped by flexible ground connection; - front pannels for diferent divisions in boarded sheets and collored
, zipper opening with special key with flexible ground connection; perforated pannels should be complete by gasket and perforation covers in order to close spaces not used; - boarded front door and collored, in trasnparent full plastic material,
(depending on prescribtions in grafic tables), zipper opening with handle, special key lock and flexible ground connection; - copper bar
marked in line with CEI-UNEL (oxidation junction phenomena indication should be included) ; - external protection level: as prescribed by grafic tables
, including bottom; - fron open pannels protection: non under IP20 guaranteed by appropriate headphones, covers, screens, protections, etc. for all devices and parts under voltage . Type of execution
(inside of the wall, out standing , on the wall or on the floor), one wire electric scheme, caracteristics and le caratteristiche and calibration of devices, accessories, tools, etc., are indicated in grafic tables . Prices are exclusive of
special devices such are lighting flux, comand bus devices, lighting flux regolation units, , etc., which will be quoted separatly.
Distribution board is compose by following elements and devices: - metal structure composed by two cabinets and one cabbling space with total dimensions (HxBxP): 2000x1100x250, protection level IP40; - n°1 manual main switcher, motor interruptor, with auxiliar contact and signal lamp 4x160A; - n°1 adjustable diferential relay with toroid Id=0,3-10A; - n°1 voltage transmiter type 2 with auxiliar contact; - n°2 voltmetric measurament group 500V, class 1,5; - n°2 amperometric measurement group 50A, class 1,5; - n°1 modular fuse box 4x125A complete of fuses and auxiliar contact; - n°1 modular fuse box 4x32A complete of fuses and auxiliar contact; - n°2 modular fuse box 4x32A complete of fuses; - n°1 modular fuse box 1x20A+N complete of fuses; - n°2 modular fuse box 2x20A complete of fuses and auxiliar contact;
- n°2 manual modular selector switch 4x63A with auxiliar contact; - n°1 manual modular selector switch4x32A with auxiliar contact; - n°1 modular commutator 4x32A with auxiliar contact and signal lamp; - n°3 modular automatico magnetotermic differential switch 4x16A, Id=30mA with auxiliar contact; - n°5 modular automatico magnetotermic differential switch 1x16A+N, Id=30mA with auxiliar contact; - n°1 modular automatico magnetotermic differential switch 1x10A+N, Id=300mA with auxiliar contact;
- n°1 modular automatico magnetotermic differential switch intervention curve B 4x10A, Id=30mA with auxiliar contact; - n°4 modular automatico magnetotermic differential switch intervention curve B 1x16A+N, Id=30mA with auxiliar contact; - n°2 modular automatico magnetotermic differential switch intervention curve B 1x10A+N, Id=30mA with auxiliar contact; - n°2 voltage modular contactor 3x17A AC3 with auxiliar contact; - n°1 transformator 230/24V voltage 400VA; - n°2 modular selector 3 positions; - grounding bar inside distribution board.
DB_L0/MDR
| GROUND FLOOR LEVEL - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 1
| Total amount |  | 1
D40.A10.A22 |  | globally
METALLIC DISTRIBUTION BOARD QUADRO DI DISTRIBUZIONE SECONDARIA DI TIPO METALLICO In line with CEI 17-13/1(95) and subsequents variations. Caracteristics: - supporting modular structure composed by metalic chase in steal or pressed sheets of at least 20/10
, complete by fixing slotting, zippers, guides, supporting profiles for device fixing ; -floor fixing chase or for adjustments of profiles in steal steanless
twice basic colloring and surface solloring in black, complete by regolable feets with rusticated base and perforated in order to permit floor fixing
with dowels and and glue (where required); - lateral and back covering pannels in bordered and collored sheets, equiped by flexible ground connection; - front pannels for diferent divisions in boarded sheets and collored
, zipper opening with special key with flexible ground connection; perforated pannels should be complete by gasket and perforation covers in order to close spaces not used; - boarded front door and collored, in trasnparent full plastic material,
(depending on prescribtions in grafic tables), zipper opening with handle, special key lock and flexible ground connection; - copper bar
marked in line with CEI-UNEL (oxidation junction phenomena indication should be included) ; - external protection level: as prescribed by grafic tables
, including bottom; - fron open pannels protection: non under IP20 guaranteed by appropriate headphones, covers, screens, protections, etc. for all devices and parts under voltage . Type of execution
(inside of the wall, out standing , on the wall or on the floor), one wire electric scheme, caracteristics and le caratteristiche and calibration of devices, accessories, tools, etc., are indicated in grafic tables . Prices are exclusive of
special devices such are lighting flux, comand bus devices, lighting flux regolation units, , etc., which will be quoted separatly.
Distribution board is compose by following elements and devices: - metal structure composed by two cabinets and one cabbling space with total dimensions (HxBxP): 1700x1350x250, protection level IP40 IP40; - n°1 manual main switcher, motor interruptor, with auxiliar contact and signal lamp 4x160A; - n°1 adjustable diferential relay with toroid Id=0,3-10A; - n°1 voltage transmiter type 2 with auxiliar contact; - n°1 voltmetric measurament group 500V, class 1,5; - n°1 amperometric measurement group 50A, class 1,5; - n°1 modular fuse box 4x125A complete of fuses and auxiliar contact; - n°1 modular fuse box 4x32A complete of fuses; - n°7 modular fuse box 1x20A+N complete of fuses and auxiliar contact;
- n°2 manual modular selector switch 4x32A with auxiliar contact; - n°2 modular automatic magnetotermic differential switch 4x16A, Id=30mA with auxiliar contact; - n°2 modular automatic magnetotermic differential switch 1x25A+N, Id=300mA with auxiliar contact;
- n°10 modular automatic magnetotermic differential switch 1x16A+N, Id=30mA with auxiliar contact; - n°2modular automatic magnetotermic differential switch 1x10A+N, Id=300mA with auxiliar contact; - n°1 modular voltage contactor 3x17A AC3 with auxiliar contact and selector 3 positions; - n°1 transformator 230/24V voltage 400VA; - grounding bar inside distribution board.
DB_L0/BR
| GROUND FLOOR LEVEL - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 1
| Total amount |  | 1
D40.A10.A23 |  | globally
METALLIC DISTRIBUTION BOARD QUADRO DI DISTRIBUZIONE SECONDARIA DI TIPO METALLICO In line with CEI 17-13/1(95) and subsequents variations. Caracteristics: - supporting modular structure composed by metalic chase in steal or pressed sheets of at least 20/10
, complete by fixing slotting, zippers, guides, supporting profiles for device fixing ; -floor fixing chase or for adjustments of profiles in steal steanless
twice basic colloring and surface solloring in black, complete by regolable feets with rusticated base and perforated in order to permit floor fixing
with dowels and and glue (where required); - lateral and back covering pannels in bordered and collored sheets, equiped by flexible ground connection; - front pannels for diferent divisions in boarded sheets and collored
, zipper opening with special key with flexible ground connection; perforated pannels should be complete by gasket and perforation covers in order to close spaces not used; - boarded front door and collored, in trasnparent full plastic material,
(depending on prescribtions in grafic tables), zipper opening with handle, special key lock and flexible ground connection; - copper bar
marked in line with CEI-UNEL (oxidation junction phenomena indication should be included) ; - external protection level: as prescribed by grafic tables
, including bottom; - fron open pannels protection: non under IP20 guaranteed by appropriate headphones, covers, screens, protections, etc. for all devices and parts under voltage . Type of execution
(inside of the wall, out standing , on the wall or on the floor), one wire electric scheme, caracteristics and le caratteristiche and calibration of devices, accessories, tools, etc., are indicated in grafic tables . Prices are exclusive of
special devices such are lighting flux, comand bus devices, lighting flux regolation units, , etc., which will be quoted separatly.
Distribution board is compose by following elements and devices: - metal structure composed by two cabinets and one cabbling space with total dimensions (HxBxP): 2000x1850x350, protection level IP40 IP40; - n°1 manual main switcher, motor interruptor, with auxiliar contact and signal lamp 4x160A; - n°1 adjustable diferential relay with toroid Id=0,3-10A; - n°1 voltage transmiter type 2 with auxiliar contact; - n°1 voltmetric measurament group 500V, class 1,5; - n°1 amperometric measurement group 50A, class 1,5; - n°1 modular fuse box 4x125A complete of fuses and auxiliar contact; - n°1 modular fuse box 4x40A complete of fuses and auxiliar contact; - n°2 modular fuse box 4x32A complete of fuses; - n°1 modular fuse box 1x20A+N complete of fuses; - n°2 modular fuse box2x20A complete of fuses and auxiliar contact;
- n°2 manual modular selector switch 4x63A with auxiliar contact; - n°1 manual modular selector switch 4x40A with auxiliar contact and signal lamp; - n°1 modulare capt 4x32A with auxiliar contact and signal lamp; - n°1 modular automatic magnetotermic differential switch 4x25A, Id=30mA with auxiliar contact; - n°2 modular automatic magnetotermic differential switch 4x16A, Id=30mA with auxiliar contact; - n°3 modular automatic magnetotermic differential switch 1x25A+N, Id=30mA with auxiliar contact; - n°6 modular automatic magnetotermic differential switch 1x16A+N, Id=30mA with auxiliar contact; - n°10 modular automatic magnetotermic differential switch1x10A+N, Id=300mA with auxiliar contact;
- n°8 modular automatic magnetotermic differential switch intervention curve B 1x16A+N, Id=30mA with auxiliar contact; - n°2 modular automatic magnetotermic differential switch intervention curve B 1x10A+N, Id=30mA with auxiliar contact; - n°4 modular voltage contactor 3x12A AC3 with auxiliar contact; - n°1 modular voltage contacto 3x17A AC3 with auxiliar contact and selector 3 positions; - n°1 transformator 230/24V voltage 400VA; - grounding bar inside distribution board.
DB_L0/M
| GROUND FLOOR LEVEL - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 1
| Total amount |  | 1
D40.A10.A24 |  | globally
METALLIC DISTRIBUTION BOARD QUADRO DI DISTRIBUZIONE SECONDARIA DI TIPO METALLICO In line with CEI 17-13/1(95) and subsequents variations. Caracteristics: - supporting modular structure composed by metalic chase in steal or pressed sheets of at least 20/10
, complete by fixing slotting, zippers, guides, supporting profiles for device fixing ; -floor fixing chase or for adjustments of profiles in steal steanless
twice basic colloring and surface solloring in black, complete by regolable feets with rusticated base and perforated in order to permit floor fixing
with dowels and and glue (where required); - lateral and back covering pannels in bordered and collored sheets, equiped by flexible ground connection; - front pannels for diferent divisions in boarded sheets and collored
, zipper opening with special key with flexible ground connection; perforated pannels should be complete by gasket and perforation covers in order to close spaces not used; - boarded front door and collored, in trasnparent full plastic material,
(depending on prescribtions in grafic tables), zipper opening with handle, special key lock and flexible ground connection; - copper bar
marked in line with CEI-UNEL (oxidation junction phenomena indication should be included) ; - external protection level: as prescribed by grafic tables
, including bottom; - fron open pannels protection: non under IP20 guaranteed by appropriate headphones, covers, screens, protections, etc. for all devices and parts under voltage . Type of execution
(inside of the wall, out standing , on the wall or on the floor), one wire electric scheme, caracteristics and le caratteristiche and calibration of devices, accessories, tools, etc., are indicated in grafic tables . Prices are exclusive of
special devices such are lighting flux, comand bus devices, lighting flux regolation units, , etc., which will be quoted separatly.
Distribution board is compose by following elements and devices: - metal structure composed by one cabinet on the wall total dimensions (HxBxP): 900x600x200, Protection level IP40; - n°1 manual modular selector switch 2x32A with auxiliar contact and signal lamp; - n°1 voltage transmiter type 2 with auxiliar contact; - n°1 modular fuses box 1x20A+N complete by fuses; - n°1 signal lamp; - n°6 modular automatic magnetotermic differential switch 1x10A+N, Id=300mA with auxiliar contact; - n°4 modular voltage contactor 3x12A AC3 with auxiliar contact; - grounding bar inside distribution board.
DB_L0/M/EL
| GROUND FLOOR LEVEL - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 1
| Total amount |  | 1
D40.A10.A25 |  | globally
METALLIC DISTRIBUTION BOARD QUADRO DI DISTRIBUZIONE SECONDARIA DI TIPO METALLICO In line with CEI 17-13/1(95) and subsequents variations. Caracteristics: - supporting modular structure composed by metalic chase in steal or pressed sheets of at least 20/10
, complete by fixing slotting, zippers, guides, supporting profiles for device fixing ; -floor fixing chase or for adjustments of profiles in steal steanless
twice basic colloring and surface solloring in black, complete by regolable feets with rusticated base and perforated in order to permit floor fixing
with dowels and and glue (where required); - lateral and back covering pannels in bordered and collored sheets, equiped by flexible ground connection; - front pannels for diferent divisions in boarded sheets and collored
, zipper opening with special key with flexible ground connection; perforated pannels should be complete by gasket and perforation covers in order to close spaces not used; - boarded front door and collored, in trasnparent full plastic material,
(depending on prescribtions in grafic tables), zipper opening with handle, special key lock and flexible ground connection; - copper bar
marked in line with CEI-UNEL (oxidation junction phenomena indication should be included) ; - external protection level: as prescribed by grafic tables
, including bottom; - fron open pannels protection: non under IP20 guaranteed by appropriate headphones, covers, screens, protections, etc. for all devices and parts under voltage . Type of execution
(inside of the wall, out standing , on the wall or on the floor), one wire electric scheme, caracteristics and le caratteristiche and calibration of devices, accessories, tools, etc., are indicated in grafic tables . Prices are exclusive of
special devices such are lighting flux, comand bus devices, lighting flux regolation units, , etc., which will be quoted separatly.
Distribution board is compose by following elements and devices: - metal structure composed by two cabinets and two cabbling space with total dimensions (HxBxP): 2000x2400x350, protection level IP40; - n°1 manual main switcher, motor interruptor, with auxiliar contact and signal lamp 4x160A; - n°1 adjustable diferential relay with toroid Id=0,3-10A; - n°1 voltage transmiter type 2 with auxiliar contact; - n°1 voltmetric measurament group 500V, class 1,5; - n°1 amperometric measurement group 50A, class 1,5; - n°1 modular fuse box 4x125A complete of fuses and auxiliar contact; - n°1 modular fuse box 4x63A complete of fuses and auxiliar contact; - n°2 modular fuse box 4x32Acomplete of fuses; - n°9 modular fuse box 1x20A+N complete of fuses; - n°2 modular fuse box 2x20A complete of fuses and auxiliar contact;
- n°2 manual modular selector switch 4x100A with auxiliar contact; - n°1 manual modular selector switch 4x63A with auxiliar contact and signal lamp; - n°1 modulare capt 4x63A with auxiliar contact and signal lamp; - n°2 modular automatic magnetotermic differential switch 4x160A, with auxiliar contact; - n°1 modular automatic magnetotermic differential switch 4x32A, Id=300mA with auxiliar contact; - n°2modular automatic magnetotermic differential switch 4x16A, Id=30mA with auxiliar contact; - n°1 modular automatic magnetotermic differential switch1x32A+N, Id=30mA with auxiliar contact; - n°2 modular automatic magnetotermic differential switch 1x25A+N, Id=30mA with auxiliar contact; - n°10 modular automatic magnetotermic differential switch 1x16A+N, Id=30mA with auxiliar contact; - n°12 modular automatic magnetotermic differential switch 1x10A+N, Id=300mA with auxiliar contact;
- n°2 modular automatic magnetotermic differential switch intervention curve B 4x63A with auxiliar contact; - n°1 modular automatic magnetotermic differential switch intervention curve B 4x16A, Id=30mA with auxiliar contact; - n°8 modular automatic magnetotermic differential switch intervention curveB 1x16A+N, Id=30mA with auxiliar contact; - n°2 modular automatic magnetotermic differential switch intervention curve B 1x10A+N, Id=30mA with auxiliar contact; - n°2 modulare voltage contactor 3x17A AC3 with auxiliar contact and selector 3 positions; - n°1 transformator 230/24V voltage 400VA; - grounding bar inside distribution board.
U_LV_SB
| GROUND FLOOR LEVEL - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 1
| Total amount |  | 1
D40.A10.A40 |  | globally
METALLIC DISTRIBUTION BOARD QUADRO DI DISTRIBUZIONE SECONDARIA DI TIPO METALLICO In line with CEI 17-13/1(95) and subsequents variations. Caracteristics: - supporting modular structure composed by metalic chase in steal or pressed sheets of at least 20/10
, complete by fixing slotting, zippers, guides, supporting profiles for device fixing ; -floor fixing chase or for adjustments of profiles in steal steanless
twice basic colloring and surface solloring in black, complete by regolable feets with rusticated base and perforated in order to permit floor fixing
with dowels and and glue (where required); - lateral and back covering pannels in bordered and collored sheets, equiped by flexible ground connection; - front pannels for diferent divisions in boarded sheets and collored
, zipper opening with special key with flexible ground connection; perforated pannels should be complete by gasket and perforation covers in order to close spaces not used; - boarded front door and collored, in trasnparent full plastic material,
(depending on prescribtions in grafic tables), zipper opening with handle, special key lock and flexible ground connection; - copper bar
marked in line with CEI-UNEL (oxidation junction phenomena indication should be included) ; - external protection level: as prescribed by grafic tables
, including bottom; - fron open pannels protection: non under IP20 guaranteed by appropriate headphones, covers, screens, protections, etc. for all devices and parts under voltage . Type of execution
(inside of the wall, out standing , on the wall or on the floor), one wire electric scheme, caracteristics and le caratteristiche and calibration of devices, accessories, tools, etc., are indicated in grafic tables . Prices are exclusive of
special devices such are lighting flux, comand bus devices, lighting flux regolation units, , etc., which will be quoted separatly.
Distribution board is compose by following elements and devices: - metal structure composed by two cabinets and one cabbling space with total dimensions (HxBxP): 2000x1850x350, Protection level IP40; - n°1manual main switcher, motor interruptor, with auxiliar contact and signal lamp 4x160A ; - n°1 adjustable diferential relay with toroid Id=0,3-10A; - n°1 voltage transmiter type 2 with auxiliar contact; - n°1 voltmetric measurament group 500V, class 1,5; - n°1 amperometric measurement group 50A, class 1,5; - n°1 modular fuse box 4x125A complete of fuses and auxiliar contact; - n°1 modular fuse box 4x63A complete of fuses and auxiliar contact; - n°2 modular fuse box 4x32A complete of fuses ; - n°1 modular fuse box 1x20A+N complete of fuses ; - n°2 modular fuse box 2x20A complete of fuses and auxiliar contact;
- n°2 manual modular selector switch 4x63A with auxiliar contact; - n°1manual modular selector switch 4x63A with auxiliar contact and signal lamp; - n°1 modulare capt 4x63A with auxiliar contact and signal lamp; - n°4 modular automatic magnetotermic differential switch 4x25A, Id=30mA with auxiliar contact; - n°9 modular automatic magnetotermic differential switch4x16A, Id=30mA with auxiliar contact; - n°3 modular automatic magnetotermic differential switch 4x10A, Id=300mA with auxiliar contact; - n°1 modular automatic magnetotermic differential switch1x25A+N, Id=30mA with auxiliar contact; - n°7modular automatic magnetotermic differential switch1x16A+N, Id=30mA with auxiliar contact; - n°8modular automatic magnetotermic differential switch 1x10A+N, Id=300mA with auxiliar contact;
- n°6 modular automatic magnetotermic differential switch intervention curve B 4x16A, Id=30mA with auxiliar contact; - n°1 modular automatic magnetotermic differential switch intervention curve B 4x10A, Id=30mA with auxiliar contact; - n°2 modular automatic magnetotermic differential switch intervention curve B 1x16A+N, Id=30mA with auxiliar contact; - n°5 modular automatic magnetotermic differential switch intervention curve B 1x10A+N, Id=30mA with auxiliar contact; - n°3 modulare voltage contactor 3x12A AC3with auxiliar contact; - n°3 modulare voltage contactor 3x17A AC3 with auxiliar contact and selector 3 positions; - n°1 transformator230/24V voltage 400VA; - grounding bar inside distribution board.
DB_L1/M/1
| FIRST FLOOR LEVEL - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 1
| Total amount |  | 1
D40.A10.A41 |  | globally
METALLIC DISTRIBUTION BOARD QUADRO DI DISTRIBUZIONE SECONDARIA DI TIPO METALLICO In line with CEI 17-13/1(95) and subsequents variations. Caracteristics: - supporting modular structure composed by metalic chase in steal or pressed sheets of at least 20/10
, complete by fixing slotting, zippers, guides, supporting profiles for device fixing ; -floor fixing chase or for adjustments of profiles in steal steanless
twice basic colloring and surface solloring in black, complete by regolable feets with rusticated base and perforated in order to permit floor fixing
with dowels and and glue (where required); - lateral and back covering pannels in bordered and collored sheets, equiped by flexible ground connection; - front pannels for diferent divisions in boarded sheets and collored
, zipper opening with special key with flexible ground connection; perforated pannels should be complete by gasket and perforation covers in order to close spaces not used; - boarded front door and collored, in trasnparent full plastic material,
(depending on prescribtions in grafic tables), zipper opening with handle, special key lock and flexible ground connection; - copper bar
marked in line with CEI-UNEL (oxidation junction phenomena indication should be included) ; - external protection level: as prescribed by grafic tables
, including bottom; - fron open pannels protection: non under IP20 guaranteed by appropriate headphones, covers, screens, protections, etc. for all devices and parts under voltage . Type of execution
(inside of the wall, out standing , on the wall or on the floor), one wire electric scheme, caracteristics and le caratteristiche and calibration of devices, accessories, tools, etc., are indicated in grafic tables . Prices are exclusive of
special devices such are lighting flux, comand bus devices, lighting flux regolation units, , etc., which will be quoted separatly.
Distribution board is compose by following elements and devices: - metal structure composed by two cabinets and one cabbling space with total dimensions (HxBxP): 2000x2100x350, Protection level IP40; - n°1 manual main switcher, motor interruptor, with auxiliar contact and signal lamp 4x160A ; - n°1 adjustable diferential relay with toroid Id=0,3-10A; - n°1 voltage transmiter type 2 with auxiliar contact; - n°1 voltmetric measurament group 500V, class 1,5; - n°1 amperometric measurement group 50A, class 1,5; - n°1 modular fuse box 4x125A complete of fuses and auxiliar contact; - n°1 modular fuse box 4x63A complete of fuses and auxiliar contact; - n°2 modular fuse box 4x32A complete of fuses; - n°1 modular fuse box 1x20A+N complete of fuses; - n°2 modular fuse box 2x20A complete of fuses and auxiliar contact;
- n°2 manual modular selector switch 4x63A with auxiliar contact; - n°1 manual modular selector switch 4x63A with auxiliar contact and signal lamp; - n°1 modulare capt 4x63A with auxiliar contact and signal lamp; - n°6 modular automatic magnetotermic differential switch4x25A, Id=30mA with auxiliar contact; - n°11 modular automatic magnetotermic differential switch 4x16A, Id=30mA with auxiliar contact; - n°1 modular automatic magnetotermic differential switch 4x10A, Id=300mA with auxiliar contact; - n°2 modular automatic magnetotermic differential switch 1x16A+N, Id=30mA with auxiliar contact; - n°12modular automatic magnetotermic differential switch 1x10A+N, Id=300mA with auxiliar contact;
- n°10 modular automatic magnetotermic differential switch intervention curve B 4x16A, Id=30mA with auxiliar contact; - n°1 modular automatic magnetotermic differential switch intervention curve B 1x16A+N, Id=30mA with auxiliar contact; - n°2 modular automatic magnetotermic differential switch intervention curve B 1x10A+N, Id=30mA with auxiliar contact; - n°3 modulare voltage contactor 3x12A AC3with auxiliar contact; - n°3 modulare voltage contactor 3x17A AC3 with auxiliar contact and selector 3 positions; - n°1 transformator 230/24V Voltage 400VA; - grounding bar inside distribution board.
DB_L1/M/2
| FIRST FLOOR LEVEL - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 1
| Total amount |  | 1
D40.A10.A42 |  | globally
METALLIC DISTRIBUTION BOARD QUADRO DI DISTRIBUZIONE SECONDARIA DI TIPO METALLICO In line with CEI 17-13/1(95) and subsequents variations. Caracteristics: - supporting modular structure composed by metalic chase in steal or pressed sheets of at least 20/10
, complete by fixing slotting, zippers, guides, supporting profiles for device fixing ; -floor fixing chase or for adjustments of profiles in steal steanless
twice basic colloring and surface solloring in black, complete by regolable feets with rusticated base and perforated in order to permit floor fixing
with dowels and and glue (where required); - lateral and back covering pannels in bordered and collored sheets, equiped by flexible ground connection; - front pannels for diferent divisions in boarded sheets and collored
, zipper opening with special key with flexible ground connection; perforated pannels should be complete by gasket and perforation covers in order to close spaces not used; - boarded front door and collored, in trasnparent full plastic material,
(depending on prescribtions in grafic tables), zipper opening with handle, special key lock and flexible ground connection; - copper bar
marked in line with CEI-UNEL (oxidation junction phenomena indication should be included) ; - external protection level: as prescribed by grafic tables
, including bottom; - fron open pannels protection: non under IP20 guaranteed by appropriate headphones, covers, screens, protections, etc. for all devices and parts under voltage . Type of execution
(inside of the wall, out standing , on the wall or on the floor), one wire electric scheme, caracteristics and le caratteristiche and calibration of devices, accessories, tools, etc., are indicated in grafic tables . Prices are exclusive of
special devices such are lighting flux, comand bus devices, lighting flux regolation units, , etc., which will be quoted separatly.
Distribution board is compose by following elements and devices: - metal structure composed by one cabinet and one cabbling space with total dimensions(HxBxP): 1700x1100x250, grado di protezione IP40; - n°1 manual modular main switcher 4x32A with auxiliar contact and signal lamp; - n°1 voltage transmiter type 2 with auxiliar contact; - n°1 modular fuse box 4x32A complete of fuses; - n°3 signal lamp; - n°20 modular magnotermic automatic differential switch 1x10A+N, Id=300mA with auxiliar contact; - n°18 modular voltage contactor 3x12A AC3 with auxiliar contact; - grounding bar inside distribution board.
DB_L1/M/EL
| FIRST FLOOR LEVEL - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 1
| Total amount |  | 1
D40.A10.A50 |  | globally
METALLIC DISTRIBUTION BOARD QUADRO DI DISTRIBUZIONE SECONDARIA DI TIPO METALLICO In line with CEI 17-13/1(95) and subsequents variations. Caracteristics: - supporting modular structure composed by metalic chase in steal or pressed sheets of at least 20/10
, complete by fixing slotting, zippers, guides, supporting profiles for device fixing ; -floor fixing chase or for adjustments of profiles in steal steanless
twice basic colloring and surface solloring in black, complete by regolable feets with rusticated base and perforated in order to permit floor fixing
with dowels and and glue (where required); - lateral and back covering pannels in bordered and collored sheets, equiped by flexible ground connection; - front pannels for diferent divisions in boarded sheets and collored
, zipper opening with special key with flexible ground connection; perforated pannels should be complete by gasket and perforation covers in order to close spaces not used; - boarded front door and collored, in trasnparent full plastic material,
(depending on prescribtions in grafic tables), zipper opening with handle, special key lock and flexible ground connection; - copper bar
marked in line with CEI-UNEL (oxidation junction phenomena indication should be included) ; - external protection level: as prescribed by grafic tables
, including bottom; - fron open pannels protection: non under IP20 guaranteed by appropriate headphones, covers, screens, protections, etc. for all devices and parts under voltage . Type of execution
(inside of the wall, out standing , on the wall or on the floor), one wire electric scheme, caracteristics and le caratteristiche and calibration of devices, accessories, tools, etc., are indicated in grafic tables . Prices are exclusive of
special devices such are lighting flux, comand bus devices, lighting flux regolation units, , etc., which will be quoted separatly.
Distribution board is compose by following elements and devices: - metal structure composed by two cabinets and one cabbling space with total dimensions (HxBxP): 2000x2350x350, Protection level IP40; - n°1 manual main switcher, motor interruptor, with auxiliar contact and signal lamp 4x160A ; - n°1 adjustable diferential relay with toroid Id=0,3-10A; - n°1 voltage transmiter type 2 with auxiliar contact; - n°1 voltmetric measurament group 500V, class 1,5; - n°1 amperometric measurement group 50A, class 1,5; - n°1 modular fuse box 4x125A complete of fuses and auxiliar contact; - n°1 modular fuse box 4x63A complete of fuses and auxiliar contact; - n°2 modular fuse box 4x32A complete of fuses; - n°1 modular fuse box 1x20A+N complete of fuses; - n°2 modular fuse box 2x20A complete of fuses and auxiliar contact;
- n°2 manual modular selector switch 4x63A with auxiliar contact; - n°1 manual modular selector switch 4x63A with auxiliar contact and signal lamp; - n°1 modulare capt 4x63A with auxiliar contact and signal lamp; - n°2 automatic magnetotermic cassette switch 4x160A, with auxiliar contact; - n°2 modular automatic magnetotermic differential switch 4x25A, Id=30mA with auxiliar contact; - n°2 modular automatic magnetotermic differential switch 4x16A, Id=30mA with auxiliar contact; - n°3 modular automatic magnetotermic differential switch 1x25A+N, Id=30mA with auxiliar contact; - n°11 modular automatic magnetotermic differential switch1x16A+N, Id=30mA with auxiliar contact; - n°13 modular automatic magnetotermic differential switch 1x10A+N, Id=300mA with auxiliar contact; - n°4 automatic termo regolable modular switch 3x25A, with auxiliar contact;
- n°4 modular automatic differential switch 4x25A, Id=30mA with auxiliar contact; - n°3 modular automatic magnetotermic differential switch intervention curve B 4x50A, Id=1mA selective, with auxiliar contact; - n°4 modular automatic magnetotermic differential switch intervention curve B 1x16A+N, Id=30mA with auxiliar contact; - n°7 modular automatic magnetotermic differential switch intervention curve B 1x10A+N, Id=30mA with auxiliar contact; - n°3 modulare voltage contactor 3x12A AC3 with auxiliar contact; - n°7 modulare voltage contactor 3x17A AC3 with auxiliar contact and selector 3 positions; - n°1 transformator 230/24V voltage 400VA; - grounding bar inside distribution board.
DB_L2/M
| SECOND FLOOR LEVEL - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 1
| Total amount |  | 1
D40.A10.A51 |  | globally
METALLIC DISTRIBUTION BOARD QUADRO DI DISTRIBUZIONE SECONDARIA DI TIPO METALLICO In line with CEI 17-13/1(95) and subsequents variations. Caracteristics: - supporting modular structure composed by metalic chase in steal or pressed sheets of at least 20/10
, complete by fixing slotting, zippers, guides, supporting profiles for device fixing ; -floor fixing chase or for adjustments of profiles in steal steanless
twice basic colloring and surface solloring in black, complete by regolable feets with rusticated base and perforated in order to permit floor fixing
with dowels and and glue (where required); - lateral and back covering pannels in bordered and collored sheets, equiped by flexible ground connection; - front pannels for diferent divisions in boarded sheets and collored
, zipper opening with special key with flexible ground connection; perforated pannels should be complete by gasket and perforation covers in order to close spaces not used; - boarded front door and collored, in trasnparent full plastic material,
(depending on prescribtions in grafic tables), zipper opening with handle, special key lock and flexible ground connection; - copper bar
marked in line with CEI-UNEL (oxidation junction phenomena indication should be included) ; - external protection level: as prescribed by grafic tables
, including bottom; - fron open pannels protection: non under IP20 guaranteed by appropriate headphones, covers, screens, protections, etc. for all devices and parts under voltage . Type of execution
(inside of the wall, out standing , on the wall or on the floor), one wire electric scheme, caracteristics and le caratteristiche and calibration of devices, accessories, tools, etc., are indicated in grafic tables . Prices are exclusive of
special devices such are lighting flux, comand bus devices, lighting flux regolation units, , etc., which will be quoted separatly.
Distribution board is compose by following elements and devices: - metal structure composed by one cabinet and one cabbling space with total dimensions(HxBxP): 1700x1100x250, grado di protezione IP40; - n°1 manual modular main switcher 4x32A with auxiliar contact and signal lamp; - n°1 voltage transmiter type 2 with auxiliar contact; - n°1 modular fuse box 4x32A complete of fuses; - n°3 signal lamp; - n°15 modular magnotermic automatic differential switch 1x10A+N, Id=300mA with auxiliar contact; - n°13 modular voltage contactor 3x12A AC3 with auxiliar contact; - grounding bar inside distribution board.
DB_L2/M/EL
| SECOND FLOOR LEVEL - SWITCHBOARDS AND DISTRIBUTION BOARDS |  | 1
| Total amount |  | 1
TOTAL DISTRIBUTION BOARDS
04 - RESERVE AND EMERGENCY SYSTEMS
L40.A10.A2 |  | n
UPS ABSOLUT CONTINUITY SISTEM absolut continuity system is composed by one static group. . In line with: CEI 21-39, 21-47, 21-48, 22-7, 22-26, 22-27, 22-29, 22-24, 74-2. supply should be composed by
: - rectifier -inverter cabinet and isolation transforamator on the by pass lateral; - protection devices, switchers, etc.; - hermetic plomb batteries, aappropriate for , fast charge, assembled in cabinets assembled in cabinet
(separately quoted), autonomy as prescribed by type; - modular magnetototermic automatic switcher of appropriate capacity; - cable connection between batteries and rectifier; - (eventualy) supporting chase in collored welded steal profile
. The price should include supply, instalation and and starting of each group.
Ups Rp=10kVA, Rv=400V, autonomy 15'
| GROUND FLOOR LEVEL - UPS AND EMERGENCY GENERATOR |  | 1
| Total amount |  | 1
TOTAL RESERVE AND EMERGENCY SYSTEMS
08 - DISTRIBUTION TERMINAL AND LIGHT SUPPLY
M10.A10.A1 |  | n
LIGHT SUPPLY EQUIVALENT POINT Light supply composed by: - part of the quote for distribution box installed on the voltage tower, conduits passing from the distribution box to light device (priced appart)
connection box supplying light device (where required). In the case of two different lamps situated in one light device aditional price should be quoted (to equivalent light source) for doubled light source which includes modification or integration of cabbling.
| In the case of dimmable light devices aditional price should be chargged (to equivalent light source) which includes modification or integration of cabbling (dimmable reactors and control point included). |  | 25
| Cabling typology should be prescribed by tables and grafics. |  | 30
| Materials forming points shouId have caracteristics indicated in the specific chapter of this study. |  | 54
| GROUND FLOOR LEVEL - LIGHTING SYSTEM |  | 15
| Total amount |  | 124
M10.A10.A3 |  | n
LIGHT SUPPLY EQUIVALENT POINT Light supply composed by: - part of the quote for distribution box installed on the voltage tower, conduits passing from the distribution box to light device (priced appart)
connection box supplying light device (where required). In the case of two different lamps situated in one light device aditional price should be quoted (to equivalent light source) for doubled light source which includes modification or integration of cabbling.
In the case of dimmable light devices aditional price should be chargged (to equivalent light source) which includes modification or integration of cabbling (dimmable reactors and control point included).
Cabling typology should be prescribed by tables and grafics.
Materials forming points shouId have caracteristics indicated in the specific chapter of this study.
Light supply on wall with flexible PVC pipe and fire resistence cable
| GROUND FLOOR LEVEL - LIGHTING SYSTEM |  | 18
| FIRST FLOOR LEVEL - LIGHTING SYSTEM |  | 12
| SECOND FLOOR LEVEL - LIGHTING SYSTEM |  | 13
| Total amount |  | 43
M10.A10.A31 |  | n
LIGHT SUPPLY EQUIVALENT POINT Light supply composed by: - part of the quote for distribution box installed on the voltage tower, conduits passing from the distribution box to light device (priced appart)
connection box supplying light device (where required). In the case of two different lamps situated in one light device aditional price should be quoted (to equivalent light source) for doubled light source which includes modification or integration of cabbling.
In the case of dimmable light devices aditional price should be chargged (to equivalent light source) which includes modification or integration of cabbling (dimmable reactors and control point included).
Cabling typology should be prescribed by tables and grafics.
Materials forming points shouId have caracteristics indicated in the specific chapter of this study.
Light supply on ceiling with cable
| GROUND FLOOR LEVEL - LIGHTING SYSTEM |  | 63
| FIRST FLOOR LEVEL - LIGHTING SYSTEM |  | 244
| SECOND FLOOR LEVEL - LIGHTING SYSTEM |  | 118
| GROUND FLOOR LEVEL - LIGHTING SYSTEM |  | 83
| Total amount |  | 508
M10.A10.A32 |  | n
LIGHT SUPPLY EQUIVALENT POINT Light supply composed by: - part of the quote for distribution box installed on the voltage tower, conduits passing from the distribution box to light device (priced appart)
connection box supplying light device (where required). In the case of two different lamps situated in one light device aditional price should be quoted (to equivalent light source) for doubled light source which includes modification or integration of cabbling.
In the case of dimmable light devices aditional price should be chargged (to equivalent light source) which includes modification or integration of cabbling (dimmable reactors and control point included).
Cabling typology should be prescribed by tables and grafics.
Materials forming points shouId have caracteristics indicated in the specific chapter of this study.
Light supply on ceiling with fire resistance cable
| GROUND FLOOR LEVEL - LIGHTING SYSTEM |  | 11
| FIRST FLOOR LEVEL - LIGHTING SYSTEM |  | 123
| SECOND FLOOR LEVEL - LIGHTING SYSTEM |  | 57
| Total amount |  | 191
M10.A10.A8 |  | n
LIGHT SUPPLY EQUIVALENT POINT Light supply composed by: - part of the quote for distribution box installed on the voltage tower, conduits passing from the distribution box to light device (priced appart)
connection box supplying light device (where required). In the case of two different lamps situated in one light device aditional price should be quoted (to equivalent light source) for doubled light source which includes modification or integration of cabbling.
In the case of dimmable light devices aditional price should be chargged (to equivalent light source) which includes modification or integration of cabbling (dimmable reactors and control point included).
Cabling typology should be prescribed by tables and grafics.
Materials forming points shouId have caracteristics indicated in the specific chapter of this study.
Visible light supply with rigid PVC pipe and cable, IP65
| GROUND FLOOR LEVEL - LIGHTING SYSTEM |  | 10
| FIRST FLOOR LEVEL - LIGHTING SYSTEM |  | 6
| SECOND FLOOR LEVEL - LIGHTING SYSTEM |  | 137
| GROUND FLOOR LEVEL - LIGHTING SYSTEM |  | 2
| Total amount |  | 155
M20.A10.A1 |  | n
LIGHT CONTROL SWITCH EQUIVALENT Control switch equivalent is composed by: - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks
; - jacks to be inserted in walls, completed, where required, by grips and conduits; - modular control jacks with following caracteristics: SWITCHES, DIVERTERS,
AND BUTTONS * in line with: CEI 23-9 and subsequent variants; * voltage and nominal frequency: 250V c.a., 50Hz; * nominal energy power : 10A for buttons and 16A for switches; * testing voltage: 2000V on 50Hz for 1 min.; *
interuption power: 200 opening and closing movements on 1,25 In, 275V c.a., cosfi'0,3; * functionality testing : 50000 movements on In, 250V c.a., cosfi'0,6; * isolation resistance: >15Mohm a 500V; * signal identification lamp
(where by type required); DIMMERS * voltage and nominal frequency: 230V c.a.+/-10%, 50Hz; * controled power: 60-500W (for resistent resistance); * isolation resistance: >15Mohm on 500V; * regolatione with
rotating command or swith with double function: longer pressure for continual regolation in increasement or decreasement, with electronic memory on release; fast touch for on/of funtion of the lamp on selected level of lighting
; * safety fuse; - jack chase in policarbonat self-extinguishing (UL94-V0) for click instalation and removal with tool, having punctures for screw instalation
with possibility of adjustment in the case of defectouse instalation; - box closures or finishes with covering elements enabling following protection : * at least IP21 (where not specified)
with covers of type selected by D.L. fixed by pressure and removable with tools; * IP55 with closure doors with transparent elastic sheath in silicone gum or similar, resistant to
humidity and water jets, allowing secure functionality of control devices with closed doors; * IP67 with non movable cover and elastic membrain in elastomer anti-age resistant to atmosferic agents
(heat, solar light, low temperatures ecc.), salt e/o acide, alcals, mineral and plant oil, animal oil and fat, carburants and non fire materials, fixed on jack box with stainless steal screws
; - eventually transit boxes.In the case of light signal command aditional price shoud be quoted for equivalent light source. In case of dimmed command
aditional price shoul be quoted fordimmed light source having caracteristics indicated by type. The price should include interior jacks cabbling. Cabbling type should be prescribed by chapter and grafic tables.
Matrials composing control swittch should have caracteristics indicated in the specific chapter of the present study.
Control switch equivalent is composed by: - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks
; - jacks to be inserted in walls, completed, where required, by grips and conduits; - modular control jacks with following caracteristics: SWITCHES, DIVERTERS,
AND BUTTONS * in line with: CEI 23-9 and subsequent variants; * voltage and nominal frequency: 250V c.a., 50Hz; * nominal energy power : 10A for buttons and 16A for switches; * testing voltage: 2000V on 50Hz for 1 min.; *
interuption power: 200 opening and closing movements on 1,25 In, 275V c.a., cosfi'0,3; * functionality testing : 50000 movements on In, 250V c.a., cosfi'0,6; * isolation resistance: >15Mohm a 500V; * signal identification lamp
(where by type required); DIMMERS * voltage and nominal frequency: 230V c.a.+/-10%, 50Hz; * controled power: 60-500W (for resistent resistance); * isolation resistance: >15Mohm on 500V; * regolatione with
rotating command or swith with double function: longer pressure for continual regolation in increasement or decreasement, with electronic memory on release; fast touch for on/of funtion of the lamp on selected level of lighting
; * safety fuse; - jack chase in policarbonat self-extinguishing (UL94-V0) for click instalation and removal with tool, having punctures for screw instalation
with possibility of adjustment in the case of defectouse instalation; - bx closures or finishes with covering elements enabling following protection : * at least IP21 (where not specified)
with covers of type selected by D.L. fixed by pressure and removable with tools; * IP55 with closure doors with transparent elastic sheath in silicone gum or similar, resistant to
humidity and water jets, allowing secure functionality of control devices with closed doors; * IP67 with non movable cover and elastic membrain in elastomer anti-age resistant to atmosferic agents
(heat, solar light, low temperatures ecc.), salt e/o acide, alcals, mineral and plant oil, animal oil and fat, carburants and non fire materials, fixed on jack box with stainless steal screws
; - eventually transit boxes.In the case of light signal command aditional price shoud be quoted for equivalent light source. In case of dimmed command
aditional price shoul be quoted fordimmed light source having caracteristics indicated by type. The price should include interior jacks cabbling. Cabbling type should be prescribed by chapter and grafic tables.
Matrials composing control swittch should have caracteristics indicated in the specific chapter of the present study.
Switch or push button switch on wall with flexible PVC pipe and cable
| GROUND FLOOR LEVEL - LIGHTING SYSTEM |  | 35
| FIRST FLOOR LEVEL - LIGHTING SYSTEM |  | 163
| SECOND FLOOR LEVEL - LIGHTING SYSTEM |  | 61
| GROUND FLOOR LEVEL - LIGHTING SYSTEM |  | 29
| Total amount |  | 288
M20.A10.A32 |  | n
LIGHT CONTROL SWITCH EQUIVALENT Control switch equivalent is composed by: - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks
; - jacks to be inserted in walls, completed, where required, by grips and conduits; - modular control jacks with following caracteristics: SWITCHES, DIVERTERS,
AND BUTTONS * in line with: CEI 23-9 and subsequent variants; * voltage and nominal frequency: 250V c.a., 50Hz; * nominal energy power : 10A for buttons and 16A for switches; * testing voltage: 2000V on 50Hz for 1 min.; *
interuption power: 200 opening and closing movements on 1,25 In, 275V c.a., cosfi'0,3; * functionality testing : 50000 movements on In, 250V c.a., cosfi'0,6; * isolation resistance: >15Mohm a 500V; * signal identification lamp
(where by type required); DIMMERS * voltage and nominal frequency: 230V c.a.+/-10%, 50Hz; * controled power: 60-500W (for resistent resistance); * isolation resistance: >15Mohm on 500V; * regolatione with
rotating command or swith with double function: longer pressure for continual regolation in increasement or decreasement, with electronic memory on release; fast touch for on/of funtion of the lamp on selected level of lighting
; * safety fuse; - jack chase in policarbonat self-extinguishing (UL94-V0) for click instalation and removal with tool, having punctures for screw instalation
with possibility of adjustment in the case of defectouse instalation; - box closures or finishes with covering elements enabling following protection : * at least IP21 (where not specified)
with covers of type selected by D.L. fixed by pressure and removable with tools; * IP55 with closure doors with transparent elastic sheath in silicone gum or similar, resistant to
humidity and water jets, allowing secure functionality of control devices with closed doors; * IP67 with non movable cover and elastic membrain in elastomer anti-age resistant to atmosferic agents
(heat, solar light, low temperatures ecc.), salt e/o acide, alcals, mineral and plant oil, animal oil and fat, carburants and non fire materials, fixed on jack box with stainless steal screws
; - eventually transit boxes.In the case of light signal command aditional price shoud be quoted for equivalent light source. In case of dimmed command
aditional price shoul be quoted fordimmed light source having caracteristics indicated by type. The price should include interior jacks cabbling. Cabbling type should be prescribed by chapter and grafic tables.
Matrials composing control swittch should have caracteristics indicated in the specific chapter of the present study.
Control switch equivalent is composed by: - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks
; - jacks to be inserted in walls, completed, where required, by grips and conduits; - modular control jacks with following caracteristics: SWITCHES, DIVERTERS,
AND BUTTONS * in line with: CEI 23-9 and subsequent variants; * voltage and nominal frequency: 250V c.a., 50Hz; * nominal energy power : 10A for buttons and 16A for switches; * testing voltage: 2000V on 50Hz for 1 min.; *
interuption power: 200 opening and closing movements on 1,25 In, 275V c.a., cosfi'0,3; * functionality testing : 50000 movements on In, 250V c.a., cosfi'0,6; * isolation resistance: >15Mohm a 500V; * signal identification lamp
(where by type required); DIMMERS * voltage and nominal frequency: 230V c.a.+/-10%, 50Hz; * controled power: 60-500W (for resistent resistance); * isolation resistance: >15Mohm on 500V; * regolatione with
rotating command or swith with double function: longer pressure for continual regolation in increasement or decreasement, with electronic memory on release; fast touch for on/of funtion of the lamp on selected level of lighting
; * safety fuse; - jack chase in policarbonat self-extinguishing (UL94-V0) for click instalation and removal with tool, having punctures for screw instalation
with possibility of adjustment in the case of defectouse instalation; - bx closures or finishes with covering elements enabling following protection : * at least IP21 (where not specified)
with covers of type selected by D.L. fixed by pressure and removable with tools; * IP55 with closure doors with transparent elastic sheath in silicone gum or similar, resistant to
humidity and water jets, allowing secure functionality of control devices with closed doors; * IP67 with non movable cover and elastic membrain in elastomer anti-age resistant to atmosferic agents
(heat, solar light, low temperatures ecc.), salt e/o acide, alcals, mineral and plant oil, animal oil and fat, carburants and non fire materials, fixed on jack box with stainless steal screws
; - eventually transit boxes.In the case of light signal command aditional price shoud be quoted for equivalent light source. In case of dimmed command
aditional price shoul be quoted fordimmed light source having caracteristics indicated by type. The price should include interior jacks cabbling. Cabbling type should be prescribed by chapter and grafic tables.
Matrials composing control swittch should have caracteristics indicated in the specific chapter of the present study.
Visible switch or push button switch with rigid PVC pipe and cable - IP55
| GROUND FLOOR LEVEL - LIGHTING SYSTEM |  | 5
| FIRST FLOOR LEVEL - LIGHTING SYSTEM |  | 1
| SECOND FLOOR LEVEL - LIGHTING SYSTEM |  | 13
| GROUND FLOOR LEVEL - LIGHTING SYSTEM |  | 5
| Total amount |  | 24
M20.A10.A61 |  | n
LIGHT CONTROL SWITCH EQUIVALENT Control switch equivalent is composed by: - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks
; - jacks to be inserted in walls, completed, where required, by grips and conduits; - modular control jacks with following caracteristics: SWITCHES, DIVERTERS,
AND BUTTONS * in line with: CEI 23-9 and subsequent variants; * voltage and nominal frequency: 250V c.a., 50Hz; * nominal energy power : 10A for buttons and 16A for switches; * testing voltage: 2000V on 50Hz for 1 min.; *
interuption power: 200 opening and closing movements on 1,25 In, 275V c.a., cosfi'0,3; * functionality testing : 50000 movements on In, 250V c.a., cosfi'0,6; * isolation resistance: >15Mohm a 500V; * signal identification lamp
(where by type required); DIMMERS * voltage and nominal frequency: 230V c.a.+/-10%, 50Hz; * controled power: 60-500W (for resistent resistance); * isolation resistance: >15Mohm on 500V; * regolatione with
rotating command or swith with double function: longer pressure for continual regolation in increasement or decreasement, with electronic memory on release; fast touch for on/of funtion of the lamp on selected level of lighting
; * safety fuse; - jack chase in policarbonat self-extinguishing (UL94-V0) for click instalation and removal with tool, having punctures for screw instalation
with possibility of adjustment in the case of defectouse instalation; - box closures or finishes with covering elements enabling following protection : * at least IP21 (where not specified)
with covers of type selected by D.L. fixed by pressure and removable with tools; * IP55 with closure doors with transparent elastic sheath in silicone gum or similar, resistant to
humidity and water jets, allowing secure functionality of control devices with closed doors; * IP67 with non movable cover and elastic membrain in elastomer anti-age resistant to atmosferic agents
(heat, solar light, low temperatures ecc.), salt e/o acide, alcals, mineral and plant oil, animal oil and fat, carburants and non fire materials, fixed on jack box with stainless steal screws
; - eventually transit boxes.In the case of light signal command aditional price shoud be quoted for equivalent light source. In case of dimmed command
aditional price shoul be quoted fordimmed light source having caracteristics indicated by type. The price should include interior jacks cabbling. Cabbling type should be prescribed by chapter and grafic tables.
Matrials composing control swittch should have caracteristics indicated in the specific chapter of the present study.
Control switch equivalent is composed by: - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks
; - jacks to be inserted in walls, completed, where required, by grips and conduits; - modular control jacks with following caracteristics: SWITCHES, DIVERTERS,
AND BUTTONS * in line with: CEI 23-9 and subsequent variants; * voltage and nominal frequency: 250V c.a., 50Hz; * nominal energy power : 10A for buttons and 16A for switches; * testing voltage: 2000V on 50Hz for 1 min.; *
interuption power: 200 opening and closing movements on 1,25 In, 275V c.a., cosfi'0,3; * functionality testing : 50000 movements on In, 250V c.a., cosfi'0,6; * isolation resistance: >15Mohm a 500V; * signal identification lamp
(where by type required); DIMMERS * voltage and nominal frequency: 230V c.a.+/-10%, 50Hz; * controled power: 60-500W (for resistent resistance); * isolation resistance: >15Mohm on 500V; * regolatione with
rotating command or swith with double function: longer pressure for continual regolation in increasement or decreasement, with electronic memory on release; fast touch for on/of funtion of the lamp on selected level of lighting
; * safety fuse; - jack chase in policarbonat self-extinguishing (UL94-V0) for click instalation and removal with tool, having punctures for screw instalation
with possibility of adjustment in the case of defectouse instalation; - bx closures or finishes with covering elements enabling following protection : * at least IP21 (where not specified)
with covers of type selected by D.L. fixed by pressure and removable with tools; * IP55 with closure doors with transparent elastic sheath in silicone gum or similar, resistant to
humidity and water jets, allowing secure functionality of control devices with closed doors; * IP67 with non movable cover and elastic membrain in elastomer anti-age resistant to atmosferic agents
(heat, solar light, low temperatures ecc.), salt e/o acide, alcals, mineral and plant oil, animal oil and fat, carburants and non fire materials, fixed on jack box with stainless steal screws
; - eventually transit boxes.In the case of light signal command aditional price shoud be quoted for equivalent light source. In case of dimmed command
aditional price shoul be quoted fordimmed light source having caracteristics indicated by type. The price should include interior jacks cabbling. Cabbling type should be prescribed by chapter and grafic tables.
Matrials composing control swittch should have caracteristics indicated in the specific chapter of the present study.
Surcharge for dimmable switch
| GROUND FLOOR LEVEL - LIGHTING SYSTEM |  | 2
| FIRST FLOOR LEVEL - LIGHTING SYSTEM |  | 60
| SECOND FLOOR LEVEL - LIGHTING SYSTEM |  | 21
| GROUND FLOOR LEVEL - LIGHTING SYSTEM |  | 9
| Total amount |  | 92
M20.A30.A1 |  | n
EMERGENCY RELEASE PUSHBUTTON PUNTO PULSANTE DI SGANCIO AD ACCESSO PROTETTO Emergency release pushbutton with protected acess is composed by: : - connection from the transmittion box to voltage tower (where required); - conduits passing from the switcher point to interruption bobine switcher instaled on main or section board (of the certain zone),
; - electrozinked box colllored in yellow completed by cover, gasket in neoprene, glass hammer with chain, cassetta in lamiera elettrozincata e verniciata di colore giallo completa di coperchio incernierato, guarnizioni in n
eoprene, serratura a chiave, martelletto frangivetro munito di catenella, frangible sintetic anti splinter glass, with release button 6A/380V; - table indicating text selected by D.L.
Emergency release pushbutton with PVC pipe and cable
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 4
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 2
| Total amount |  | 6
M20.A50.A1 |  | n
SURCHARGE FOR INFRARED AUTOMATIC COMMAND POINT Infrared automatic command light point in presence of people trough volumetric with following caracteristics: - nominal voltage frequence
: 230V c.a. +/-10%, 50Hz; - nominal power: at least 2200 VA; - detection angle : at least 100^ horizontal and 30^ on vertical type of walls; 360^ with basic conus d.7,5m on h=2,5 for the ceiling type ; -
radius of action: front type at least 4 m for the wall type; at least 7m for the ceiling type. - detection density of at least 14 incidents segments trough fresnel lens; - regolation of brightness trashold from 5 to 1000 lux at least with possibility of exclusion
; - commutation time regolation min.: from 5 sec to 10 min; - protection leve;: min. IP44 (frontal) IP20 on ceiling; - o where required MAN/0/AUT selector in order to inhibit or mainain commutaded comand contact
; - chase in ABS composed by: * (wall type) fixed part having electronic componenets , regolation screws , grip and fixing accessories for chase fixing or out standing trough junction to max. angle of
l80^; * (ceiling type) fixing nail for detector positioning; - reley with contacts for lamp command incandescence and fluoroscent; - attesting grip with screws; - instalation:
in wall or on wall depending on type. Where required by type, detection system should be executed with more divices where the principal one with master function and secondaries (limited number) with slave function which will send detected signal to the master one;
master will have at least n.2 different contacts. Materials forming the point should have caracteristics indicated in the specific chapter of the present study.
quotation should be understood as aditional price to be added to command equivalent point
Surcharge for command point on wall with infrared sensor
| GROUND FLOOR LEVEL - LIGHTING SYSTEM |  | 13
| FIRST FLOOR LEVEL - LIGHTING SYSTEM |  | 25
| SECOND FLOOR LEVEL - LIGHTING SYSTEM |  | 14
| GROUND FLOOR LEVEL - LIGHTING SYSTEM |  | 12
| Total amount |  | 64
M20.A80.A1 |  | n
INFRARED AND LIGHTING SENSOR INTERFACED WITH LIGHTING CONTROL SYSTEM SENSORE DI PRESENZA E DI LUMINOSITA' INTERFACCIATO CON IL SISTEMA DI CONTROLLO ILLUMINAZIONE Lighting and presence sensor integrated with lighting control system for in wall instalation having following caracteristics S
: * bus system lighting controll voltage supply (protocol EIB/KNX); * detecting surface: aprox. 7 x 7 m; * movement sensor; * master/slave function; * settings: + lighting surface
: 0-700lux (with adjustment factor untill 5600lux); + delay off function calibrable 1s-120min. * modification of nominal lighting value (value lux) with object; * implemented functions: + lighting: ON/OFF; + timer function (off with delay)
+ movement sensor block ; + replay; + lighting setting ; + function master/slave; * two channel sensor; * supply: 10mA; * protection class: II;
* evential instalation chase on ceiling with insertion fixing; * instalation accessories; * attesting grip ; * instalation: ceiling
Surcharge for command point on ceiling with infrared and lighting sensor
| FIRST FLOOR LEVEL - LIGHTING SYSTEM |  | 60
| SECOND FLOOR LEVEL - LIGHTING SYSTEM |  | 10
| Total amount |  | 70
M30.A10.A7 |  | n
POWER SUPPLY POINTS Power supply is composed by : - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks (quoted appart)
; - eventualy transit boxes and jack boxes. Type of cabbling should be prescribed by chapter and dimensioned on the basis of efective voltage
used by devices (motored door/tent, cabinets, etc.) . In the case of existing conduits just the price of cabbling shoud be indicated . In the case of supply and instalation
of only conduits and boxes price for preparaty works should be indicated. Used materials should be in line with specific chaapter of present study.
Wall embedded power with PVC flexible pipe and 3x2.5 cable
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 49
| FIRST FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 247
| SECOND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 96
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 48
| Total amount |  | 440
M30.A10.A8 |  | n
POWER SUPPLY POINTS Power supply is composed by : - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks (quoted appart)
; - eventualy transit boxes and jack boxes. Type of cabbling should be prescribed by chapter and dimensioned on the basis of efective voltage
used by devices (motored door/tent, cabinets, etc.) . In the case of existing conduits just the price of cabbling shoud be indicated . In the case of supply and instalation
of only conduits and boxes price for preparaty works should be indicated. Used materials should be in line with specific chaapter of present study.
Wall embedded power with PVC flexible pipe and 3x4 cable
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 17
| FIRST FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 6
| SECOND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 28
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 6
| Total amount |  | 57
M30.A10.B18 |  | n
POWER SUPPLY POINTS Power supply is composed by : - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks (quoted appart)
; - eventualy transit boxes and jack boxes. Type of cabbling should be prescribed by chapter and dimensioned on the basis of efective voltage
used by devices (motored door/tent, cabinets, etc.) . In the case of existing conduits just the price of cabbling shoud be indicated . In the case of supply and instalation
of only conduits and boxes price for preparaty works should be indicated. Used materials should be in line with specific chaapter of present study.
Visible wall installation power supply with PVC rigid pipe and 5x4 cable, IP44
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 7
| FIRST FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 1
| SECOND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 6
| ROOF LEVEL - LV TERMINAL DISTRIBUTION |  | 1
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 1
| Total amount |  | 16
M30.A10.B7 |  | n
POWER SUPPLY POINTS Power supply is composed by : - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks (quoted appart)
; - eventualy transit boxes and jack boxes. Type of cabbling should be prescribed by chapter and dimensioned on the basis of efective voltage
used by devices (motored door/tent, cabinets, etc.) . In the case of existing conduits just the price of cabbling shoud be indicated . In the case of supply and instalation
of only conduits and boxes price for preparaty works should be indicated. Used materials should be in line with specific chaapter of present study.
Visible wall installation power supply with PVC rigid pipe and 3x2.5 cable, IP44
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 15
| FIRST FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 15
| SECOND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 65
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 17
| Total amount |  | 112
M30.A10.B8 |  | n
POWER SUPPLY POINTS Power supply is composed by : - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks (quoted appart)
; - eventualy transit boxes and jack boxes. Type of cabbling should be prescribed by chapter and dimensioned on the basis of efective voltage
used by devices (motored door/tent, cabinets, etc.) . In the case of existing conduits just the price of cabbling shoud be indicated . In the case of supply and instalation
of only conduits and boxes price for preparaty works should be indicated. Used materials should be in line with specific chaapter of present study.
Visible wall installation power supply with PVC rigid pipe and 3x4 cable, IP44
| FIRST FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 4
| SECOND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 2
| ROOF LEVEL - LV TERMINAL DISTRIBUTION |  | 9
| Total amount |  | 15
M30.A10.L8 |  | n
POWER SUPPLY POINTS Power supply is composed by : - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to jacks (quoted appart)
; - eventualy transit boxes and jack boxes. Type of cabbling should be prescribed by chapter and dimensioned on the basis of efective voltage
used by devices (motored door/tent, cabinets, etc.) . In the case of existing conduits just the price of cabbling shoud be indicated . In the case of supply and instalation
of only conduits and boxes price for preparaty works should be indicated. Used materials should be in line with specific chaapter of present study.
Visible power supply with 3x4 cable
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 20
| FIRST FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 432
| SECOND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 60
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 42
| Total amount |  | 554
M50.A90.A1 |  | n
PVC BOX WITH CONTACTORS FOR NORMAL AND SECURITY LIGHTING SCATOLA IN VISTA CON CONTATTORI PER COMANDO ILLUMINAZIONE NORMALE E DI SICUREZZA Box with contactors for normal and security lighting of premisses. Following should be installed in the box:
+ n°1 modular contactor normaly open and supply bobine on 230Vca for on/off command, installed in the box, with following caracteristics: - nominal frequency and voltage: 230V c.a. +/
-10%, 50Hz; - nominal energy supply: 16A; - instalation: click as per guide DIN. + n°1 modular contactor normaly closed with bobine supplied on 230Vca and controlled by NC contact of normaly open telerutor . The contactor should have same caracteristics as NA dispositiv.
Materials on instalation and box in isolating material.
PVC box 110x170x100mm with contactors
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 2
| FIRST FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 9
| SECOND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 11
| Total amount |  | 22
N10.A10.A13 |  | n
DOMESTIC SOCKET POINT AND PROTECTION DEVICE PRESA E FRUTTI DI PROTEZIONE DI TIPO DOMESTICO O SIMILARE Punto presa composto da: - frutti modulari aventi le seguenti caratteristiche: PRESE A SPINA PER USI DOMESTICI E SIMILARI: * conformita' alle n
orme: CEI 23-5, 23-16 e successive varianti; * conformita' alle tabelle: CEI-UNEL 47158, 47 V3. * tensione e frequenza nominale: 230V c.a. +/-10%, 50Hz; * corrente nominale: come descritto nei tipi; * grado di protezione: min. IP21; * tensione d
i prova: 2000V a 50Hz per 1 min.; * potere di interruzione: min. 100 manovre di inserimento e disinserimento della spina a 275V c.a., cosfi' 0,6, con corrente di prova 1,25 In (per prese da 10A) e 2,0 In (per prese da 16A); * resistenza d'isolament
o: > 15Mohm a 500V; * fissaggio a scatto su telaio portafrutti con rimozione a mezzo di utensile; INTERRUTTORI DI PROTEZIONE (magnetotermici e magnetotermici differenziali, a seconda dei tipi): * conformita' alle norme: CEI 23-3 e successive varia
nti; * tensione e frequenza nominale: 230V c.a. +/-10%, 50Hz; * corrente nominale: come descritto nei tipi; * potere d'interruzione: 3000A; * corrente differenziale (eventuale): 10mA; * resistenza d'isolamento: > 15Mohm a 500V; * fissaggio a sc
atto su telaio portafrutti con rimozione a mezzo di utensile; PORTAFUSIBILI E FUSIBILI * conformita' alle norme: CEI 32-1, 32-4, 32-5 e successive varianti; * tensione e frequenza nominale: 230V c.a. +/-10%, 50Hz; * corrente nominale: come descri
tto nei tipi; * potere di interruzione: 100kA con cosfi' 0,2; TRASFORMATORE D'ISOLAMENTO (nelle prese per rasoi): * conformita' alle norme: CEI 14-6 e succesive varianti; * tensione primaria: 230V c.a. +/-10%; * frequenza nominale: 50Hz; * tens
ione secondaria: doppio avvolgimento a 110V collegabile in serie (230V) o parallelo (110V) mediante commutatore; * potenza nominale: 20VA; * microinterruttore per l'inserimento del trasformatore solo a spina innestata; * protezione contro sovracca
richi; - telaio portafrutti in policarbonato autoestinguente (UL94-V0) con forature asolate per il fissaggio tramite viti tali da permettere aggiustamenti di eventuali difetti di posa della scatola nel tipo da incasso; - chiusure e/o rifiniture del
le scatole porta frutto di tipo domestico o similare, con elementi di copertura che garantiscano il grado di protezione seguente: * IP21 con placche di copertura del tipo a scelta della D.L. fissate a pressione o con viti e rimovibili per mezzo di u
tensile; * IP 44 min. con portine di chiusura munite di guaina trasparente elastica in gomma siliconica o similare, ovvero portine in materiale termoplastico, resistenti all'umidita' e ai getti d'acqua a portina chiusa. PUNTO ALIMENTAZIONE EQUIVALE
NTE Punto alimentazione equivalente comprensivo di: - quota parte della cassetta di transito e di derivazione installata lungo la dorsale; - condutture in vista oppure sottotraccia in partenza dalla cassetta di derivazione installata lungo la dor
sale fino al punto di utilizzazione (conteggiato a parte); - eventuali cassette di transito e scatole portafrutti. La tipologia del cablaggio e dei conduttori è quella riportata nello specifico capitolo dell'elaborato "Disciplinare descrittivo e pr
estazionale degli elementi tecnici". Il prezzo dovra' essere comprensivo del cablaggio interno tra i frutti. I materiali costituenti il punto dovranno avere le caratteristiche indicate nello specifico capitolo del presente elaborato.
Socket outlet 2x16 A+E
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 26
| FIRST FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 438
| SECOND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 80
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 48
| Total amount |  | 592
N10.A10.A3 |  | n
DOMESTIC SOCKET POINT AND PROTECTION DEVICE OR SIMILAR Socket point composed by: Punto presa composto da: - modular sockets with following caracteristics: DOMESTIC SOCKETS OR SIMILAR : * in line with
: CEI 23-5, 23-16 and subsequent variations; * in line with tables: CEI-UNEL 47158, 47 V3. * voltage and nominal frequency : 230V c.a. +/-10%, 50Hz; * nominal energy supply: as described by types; * level of protection: min. IP21; * testing voltage
i: 2000V on 50Hz for 1 min.; * interruption power: min. 100 movements of in/out and extraction of jack on 275V c.a., cosfi' 0,6, with testing power 1,25 In (for socket 10A) e 2,0 In (for socket 16A); * isolation resistance
o: > 15Mohm on 500V; * click fixing removal with tool; PROTECTION SWITCH (magnetotermic and magnetotermic differential, depending on type): * in line with : CEI 23-3 and subsequent variations
; * nominal frequence and voltage: 230V c.a. +/-10%, 50Hz; *nominal energy supply: as described by types; * interruption power: 3000A; * differential energy (eventualy): 10mA; * isolation resistance: > 15Mohm a 500V; * fixing on chase with tool removal
; FUSE BOX AND FUSES * in line with: CEI 32-1, 32-4, 32-5 and subsequent variation; * voltage and nominal frequency: 230V c.a. +/-10%, 50Hz; * nominal energy: as decribed by type
; * interruption power: 100kA with cosfi' 0,2; ISOLATION TRANSFORMATOR (shaving socket): * in line with: CEI 14-6 and subsequent variations; * primary voltage: 230V c.a. +/-10%; * nominal frequency: 50Hz; * secondary voltage
: double coil on 110V connectable in series (230V) or parallel (110V) trough commutator; * nominal power: 20VA; * microinterruptor for transormator insertion only for grafted; * over power protection
; - socket chase in autoestingueting policarbonat (UL94-V0) with slotted holes for screw fixing in order to permit adjustments in case of defected instalation ; - closing and finishing of domestic socket
, with covering elements in order to guarantee following protection: * IP21 with cover selected by D.L.fixed by pressure or screwed to be removed with tool
; * IP 44 min. with doors with transparent elastic sheath in silicone gum or similar or doors in termoplastic material, resistent to humidity and water jets on closed position.
POWER SUPPLY POINTS Power supply is composed by : - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to sockets (quoted appart)
; - eventualy transit boxes and sockets. Type of cabbling should be prescribed by chapter and dimensioned on the basis of specific chapter of the study "Disciplinare descrittivo e pr
estazionale degli elementi tecnici". Price should be inclusive of cabbling between sockets. Materials must be with caracteristics indicated in the specific chapter of the present study.
Socket outlet 2x10/16 A+E
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 26
| FIRST FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 455
| SECOND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 108
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 48
| Total amount |  | 637
N10.A10.A5 |  | n
DOMESTIC SOCKET POINT AND PROTECTION DEVICE OR SIMILAR Socket point composed by: Punto presa composto da: - modular sockets with following caracteristics: DOMESTIC SOCKETS OR SIMILAR : * in line with
: CEI 23-5, 23-16 and subsequent variations; * in line with tables: CEI-UNEL 47158, 47 V3. * voltage and nominal frequency : 230V c.a. +/-10%, 50Hz; * nominal energy supply: as described by types; * level of protection: min. IP21; * testing voltage
i: 2000V on 50Hz for 1 min.; * interruption power: min. 100 movements of in/out and extraction of jack on 275V c.a., cosfi' 0,6, with testing power 1,25 In (for socket 10A) e 2,0 In (for socket 16A); * isolation resistance
o: > 15Mohm on 500V; * click fixing removal with tool; PROTECTION SWITCH (magnetotermic and magnetotermic differential, depending on type): * in line with : CEI 23-3 and subsequent variations
; * nominal frequence and voltage: 230V c.a. +/-10%, 50Hz; *nominal energy supply: as described by types; * interruption power: 3000A; * differential energy (eventualy): 10mA; * isolation resistance: > 15Mohm a 500V; * fixing on chase with tool removal
; FUSE BOX AND FUSES * in line with: CEI 32-1, 32-4, 32-5 and subsequent variation; * voltage and nominal frequency: 230V c.a. +/-10%, 50Hz; * nominal energy: as decribed by type
; * interruption power: 100kA with cosfi' 0,2; ISOLATION TRANSFORMATOR (shaving socket): * in line with: CEI 14-6 and subsequent variations; * primary voltage: 230V c.a. +/-10%; * nominal frequency: 50Hz; * secondary voltage
: double coil on 110V connectable in series (230V) or parallel (110V) trough commutator; * nominal power: 20VA; * microinterruptor for transormator insertion only for grafted; * over power protection
; - socket chase in autoestingueting policarbonat (UL94-V0) with slotted holes for screw fixing in order to permit adjustments in case of defected instalation ; - closing and finishing of domestic socket
, with covering elements in order to guarantee following protection: * IP21 with cover selected by D.L.fixed by pressure or screwed to be removed with tool
; * IP 44 min. with doors with transparent elastic sheath in silicone gum or similar or doors in termoplastic material, resistent to humidity and water jets on closed position.
POWER SUPPLY POINTS Power supply is composed by : - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to sockets (quoted appart)
; - eventualy transit boxes and sockets. Type of cabbling should be prescribed by chapter and dimensioned on the basis of specific chapter of the study "Disciplinare descrittivo e pr
estazionale degli elementi tecnici". Price should be inclusive of cabbling between sockets. Materials must be with caracteristics indicated in the specific chapter of the present study.
Socket outlet 2x16 A+E with interblock switch
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 17
| FIRST FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 73
| SECOND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 44
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 14
| Total amount |  | 148
N10.A10.A65 |  | n
DOMESTIC SOCKET POINT AND PROTECTION DEVICE OR SIMILAR Socket point composed by: Punto presa composto da: - modular sockets with following caracteristics: DOMESTIC SOCKETS OR SIMILAR : * in line with
: CEI 23-5, 23-16 and subsequent variations; * in line with tables: CEI-UNEL 47158, 47 V3. * voltage and nominal frequency : 230V c.a. +/-10%, 50Hz; * nominal energy supply: as described by types; * level of protection: min. IP21; * testing voltage
i: 2000V on 50Hz for 1 min.; * interruption power: min. 100 movements of in/out and extraction of jack on 275V c.a., cosfi' 0,6, with testing power 1,25 In (for socket 10A) e 2,0 In (for socket 16A); * isolation resistance
o: > 15Mohm on 500V; * click fixing removal with tool; PROTECTION SWITCH (magnetotermic and magnetotermic differential, depending on type): * in line with : CEI 23-3 and subsequent variations
; * nominal frequence and voltage: 230V c.a. +/-10%, 50Hz; *nominal energy supply: as described by types; * interruption power: 3000A; * differential energy (eventualy): 10mA; * isolation resistance: > 15Mohm a 500V; * fixing on chase with tool removal
; FUSE BOX AND FUSES * in line with: CEI 32-1, 32-4, 32-5 and subsequent variation; * voltage and nominal frequency: 230V c.a. +/-10%, 50Hz; * nominal energy: as decribed by type
; * interruption power: 100kA with cosfi' 0,2; ISOLATION TRANSFORMATOR (shaving socket): * in line with: CEI 14-6 and subsequent variations; * primary voltage: 230V c.a. +/-10%; * nominal frequency: 50Hz; * secondary voltage
: double coil on 110V connectable in series (230V) or parallel (110V) trough commutator; * nominal power: 20VA; * microinterruptor for transormator insertion only for grafted; * over power protection
; - socket chase in autoestingueting policarbonat (UL94-V0) with slotted holes for screw fixing in order to permit adjustments in case of defected instalation ; - closing and finishing of domestic socket
, with covering elements in order to guarantee following protection: * IP21 with cover selected by D.L.fixed by pressure or screwed to be removed with tool
; * IP 44 min. with doors with transparent elastic sheath in silicone gum or similar or doors in termoplastic material, resistent to humidity and water jets on closed position.
POWER SUPPLY POINTS Power supply is composed by : - part of the quote for distribution box installed on the voltage tower; - conduits passing from the distribution box to sockets (quoted appart)
; - eventualy transit boxes and sockets. Type of cabbling should be prescribed by chapter and dimensioned on the basis of specific chapter of the study "Disciplinare descrittivo e pr
estazionale degli elementi tecnici". Price should be inclusive of cabbling between sockets. Materials must be with caracteristics indicated in the specific chapter of the present study.
Socket outlet 2x16 A+E with interblock switch, IP44
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 9
| FIRST FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 16
| SECOND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 11
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 3
| Total amount |  | 39
N10.A20.A50 |  | n
INDUSTRIAL SOCKET OUTLET In line with: CEI 23-12(92) and subsequent variations; UL94-V1. In line with tables : CEI-UNEL 47173, 47174, 47175, 47176. Nominal voltage: 230/400V c.a. +/-10%.
Niminal frequence: 50Hz; Nominal energy: as described by type. Ptotection level :as described by type. Caracteristics: - modular chase box in wall or on wall scatola in termo poliestere resine,
autoestingueting, reinforced by glass fiber or in pressofused alloy heat collored with epossidic resine with previous resine chromatization treatment depending on type ; cover with same caracteristics as the box, connected to the box complete with screws in steal stainless and elestomer age proof gasket
; signed holes complete of connections to supply conduits; - bayonet connection for closed switch manual blockage
; ferulle and protection watertight cover in termoplastic material with stainless steal closing spring ; - selector switcher rotation type with reef with contact disc intermoindurent isolation material
, autoestingueting, electric arc proof and two interuption points silver contacts; manual blocking in order to prevent, closed switche, jack extraction, opening of cover and access tu fuses and, if cover open, closure of the swither
; - where required by type, fuse box froup in ceramic material or in termpolastic material, autoestiguiting, complete by fusible cartridge of dimensions in line with international standards,
; - owhere required by type, security transformator (norm CEI 14-6) voltage at least 160VA for jack supply in lowest security voltage (SELV); interblocking switcher composed by switcher situated on the primary transformator,
, activated by jack instertion; protection of the primery and secondary by fuses.
Industrial visible socket outlet with mechanical interblock and fuses, 2x16 A+E, IP55
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 8
| FIRST FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 1
| SECOND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 6
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 1
| Total amount |  | 16
N10.A20.A56 |  | n
INDUSTRIAL SOCKET OUTLET In line with: CEI 23-12(92) and subsequent variations; UL94-V1. In line with tables : CEI-UNEL 47173, 47174, 47175, 47176. Nominal voltage: 230/400V c.a. +/-10%.
Niminal frequence: 50Hz; Nominal energy: as described by type. Ptotection level :as described by type. Caracteristics: - modular chase box in wall or on wall scatola in termo poliestere resine,
autoestingueting, reinforced by glass fiber or in pressofused alloy heat collored with epossidic resine with previous resine chromatization treatment depending on type ; cover with same caracteristics as the box, connected to the box complete with screws in steal stainless and elestomer age proof gasket
; signed holes complete of connections to supply conduits; - bayonet connection for closed switch manual blockage
; ferulle and protection watertight cover in termoplastic material with stainless steal closing spring ; - selector switcher rotation type with reef with contact disc intermoindurent isolation material
, autoestingueting, electric arc proof and two interuption points silver contacts; manual blocking in order to prevent, closed switche, jack extraction, opening of cover and access tu fuses and, if cover open, closure of the swither
; - where required by type, fuse box froup in ceramic material or in termpolastic material, autoestiguiting, complete by fusible cartridge of dimensions in line with international standards,
; - owhere required by type, security transformator (norm CEI 14-6) voltage at least 160VA for jack supply in lowest security voltage (SELV); interblocking switcher composed by switcher situated on the primary transformator,
, activated by jack instertion; protection of the primery and secondary by fuses.
Industrial visible socket outlet with mechanical interblock and fuses, 3x16 A+N+E, IP55
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 5
| FIRST FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 1
| SECOND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 6
| GROUND FLOOR LEVEL - LV TERMINAL DISTRIBUTION |  | 1
| Total amount |  | 13
TOTAL DISTRIBUTION TERMINALS AND SUPPLY POINTS
09 - EARTHING AND PROTECTION AGAINST ATMOSFERIC SHOTS
O10.A30.A1 |  | n
EQUIPOTENTIAL BOX AND CONNECTIONS IMPIANTO EQUIPOTENZIALE PER SERVIZIO TIPO Device is composed by: - floor conduits or under cement from the voltage line or distribution box jack, required for hot or cold water, lectronic devices, compossed by rigid PVC and cable non propagating fire of 4 mm2 section
; - connection accesories such tube connectors, tube collars, strings, terminals, cable ending in zinked steal or copper
; - welded where required. Tall connections should be easely accessible in the PV boxes.
Equipotential box and connections for toilets room
| GROUND FLOOR LEVEL - EARTHING AND LIGHTNING PLANT |  | 2
| FIRST FLOOR LEVEL - EARTHING AND LIGHTNING PLANT |  | 6
| SECOND FLOOR LEVEL - EARTHING AND LIGHTNING PLANT |  | 4
| GROUND FLOOR LEVEL - EARTHING AND LIGHTNING PLANT |  | 2
| Total amount |  | 14
O10.A80.A1 |  | n
CONNECTION TO BUILDING METAL ELEMENTS EQUIVALENT CONNECTION POINT composed by : - round and flat conduit up to 150 mm2 di of zinc steal section or up to 100 mm2 of copper section for the connection of dispesor ring and building metal
; - equipotential connection between all armour metals and dispesor realized in alluminotermic welding or grip joints
Connection to building metal elements by mechanical joint (clamping)
| ROOF LEVEL - EARTHING AND LIGHTNING PLANT |  | 99
| Total amount |  | 99
O20.A50.A11 |  | m
GALVANIZED STEEL CYLINDER TONDO DI ACCIAIO ZINCATO In line with: CEI 7-6 and subsequent variations. Conduit: oval in heated zinked steal, for immersion and traction, in bars (for caption networks)
or rolls (for underground instalation). Minimal mass of Zn surface : 550 gr/m2 +/-10%. Minimal tickeness of Zn surface: 78 micron. Accessories: - isolation and non isolation spacers for vertical, horizontal and steeply instalation (walls, roofs, etc)
; - heavy materials for instalation on flat covers; - junctions and intersected junctions constructed metall plates and alluminothermic weldings ; - where required
breaking up plates, dilatation or expansion junction giunti di dilatazione o espansione
Galvanized steel cylinder D=10mm
| ROOF LEVEL - EARTHING AND LIGHTNING PLANT |  | 420
| Total amount |  | 420
TOTAL IMP.TERRA E PROTEZ. CONTRO SCARICHE
10 - LIGHTING LUMINARIES
P300.A120.A1 |  | n
SELF POWERING KIT FOR EMERGENCY LIGHTING WITH FLUORESCENT LIGHTS Group of supply-reactor and battery Ni-Cd hermetic appropriate for linear and compact fluoroscent light emergency supply
, instalation in the allready cabbled lighting device . In light with: CEI 34-21, 34-22 and subsequent variations . Technical and lighting caracteritics: - voltage and nominal frequency: 230V c.a. +/-20%, 50H
z; - charging time: max. 24h; Electromeccanical caracteristics: - isolation level: class II; - protection level min: IP20; - fire resistance: 750° C. Construction caracteristic: - battery
Ni-Cd with capacity appropriate for the power of the lamp having following authonomy min: * fully charged as decsribed by type ; * at least one hour after 12 hours of charge; - slipcase in plastic material autoestinguiting ; - possibility for supply of fluoroscent lamp from
18 a 58W with minimal authonomy as decsribed per type ; - minimal percentage of emergency percentuale minima of transition of emergency of the lamp respectively to nominal as indicated del: * authonomy 1h: 35% for lamps from 18W, 20% for 36W and 1
5% for lamps 58W; * authonomy 3h: 25% for lamp of 18W, 15% for 36W and 10% for lamp 58W; - protection switch for batery total empty; - network protection fuses; - battery activity network presence LED
; - constant activity possibility SA (lamps allways on) or just emergency SE (just without voltage in network); - connection grips from comand line and emergency
. - electronic circuit contolling minimal level of voltage and of automatic charge ; - connection grips for command line conection and emergency ; - (where required by type) diagnostic circuit capable to perform test on internal circuit, on the lamp
and on batteries trough centralized system.
Self powering kit for fluorescent light up to 58W, aut. 1h
| GROUND FLOOR LEVEL - LIGHTING SYSTEM |  | 19
| FIRST FLOOR LEVEL - LIGHTING SYSTEM |  | 1
| SECOND FLOOR LEVEL - LIGHTING SYSTEM |  | 16
| GROUND FLOOR LEVEL - LIGHTING SYSTEM |  | 30
| Total amount |  | 66
P500.A10.A2 |  | globally
LIGHTING LUMINAIRES LAYING Instalation of lighting devices (exclusive of supply) including assembly of parts and all relevant costs in order to perform the work.
completa e funzionante
Lighting luminaires laying (luminaires not included) on ground level (University)
| GROUND FLOOR LEVEL - LIGHTING SYSTEM |  | 1
| Total amount |  | 1
P500.A10.A3 |  | globally
LIGHTING LUMINAIRES LAYING Instalation of lighting devices (exclusive of supply) including assembly of parts and all relevant costs in order to perform the work.
completa e funzionante
Lighting luminaires laying (luminaires not included) on ground level (University)
| GROUND FLOOR LEVEL - LIGHTING SYSTEM |  | 1
| Total amount |  | 1
P500.A10.A4 |  | globally
LIGHTING LUMINAIRES LAYING Instalation of lighting devices (exclusive of supply) including assembly of parts and all relevant costs in order to perform the work.
completa e funzionante
Lighting luminaires laying (luminaires not included) on first level
| FIRST FLOOR LEVEL - LIGHTING SYSTEM |  | 1
| Total amount |  | 1
P500.A10.A5 |  | globally
LIGHTING LUMINAIRES LAYING Instalation of lighting devices (exclusive of supply) including assembly of parts and all relevant costs in order to perform the work.
completa e funzionante
Lighting luminaires laying (luminaires not included) on second level
| SECOND FLOOR LEVEL - LIGHTING SYSTEM |  | 1
| Total amount |  | 1
TOTAL LIGHTING LUMINARIES
TOTAL ELECTRICAL - GROUND FLOOR AND UPPER FLOOR LEVELS
TOTAL ELECTRICAL