## ELECTRICAL
COD. | DESCRIPTION | u.m. | N. | UNIT PRICE | TOTAL AMMOUNT
03 | ELECTRICAL PLANTS - GROUND FLOOR AND UPPER FLOOR LEVELS
17 - VARIOUS WORKS
J10.A10.A1 | IMPIANTO FOTOVOLTAICO | globally
PHOTOVOLTAIC SYSTEM WITH HIT TECNOLOGY MODULES SISTEMA FOTOVOLTAICO A PANNELLI DI SILICIO MONOCRISTALLINO HIT Fotovoltaic system operating in prallel with electrical network supplied by user, without energy accumulation. In line with: EN 60904-1, 60904-2 , 61173, 60891, 61215, 50380 and subsequent variations. FOTOVOLTAIC FIELD Fotovoltaic field is composed by cell modules in monocristallin sillicium ( fotovoltaic pannels) covered by thin amorf sillicium layer, connected between tham in serie or parallel in order to form strings with appropriate power having following caracteristics: - max. dimensions : 1570x800x35 mm or equivalent; - peak power: 215Wp (valuated in S.T.C. conditions); - nominal power torenace: < = 3%; - open circuit voltage: 51,6V; - energy on max. power Im: 5,13A;
- energy of c.to c.to Isc (mA/°C): 5,61A; - isolation level: class II; - yield over 80% in 20 years (guaranteed by manufacturer); - accomplishing conditions required by norms EN 61215 trough certification of type proofs performed in acreditaded EA laboratories; - junction and derivation boxes containing blocking diodes and bypass ; - connection between pannels and related conductors trough connectors "plug & play" type Multicontact or similar; - minimal protection level gof the entire system (junction and connector cassette pannels): IP67; - connection/supply cabbles in continious power from pannel to electrical conversion system having following caracteristics: * in line with norms: CEI 20-19/4, 20-35, EN 60811-2-1 and subsequent variations ; * nominal voltage: 2 kV cc; * testing voltage: 6kV ca / 10 kV cc; * external sheath: etilen-vinilacetato; * internal sheath: etilen-vinilacetato. * isolation: etilen-propilenic gumhigh module; * conductor: flexsible wire coated red copper; * minimal working temperature: -15°C in c.a. - 40°C in c.c; * max. working temperatur: 120°C for continious work of at least 30 years in conditions of mechanical stress, UV exposition, ozone presence, humidity, aprticular temperatures; * short circuit max temperature: 250°C; * Fire reaction: non propagating fire, low emission of smoke, toxic and corrosive gasses. FIELD BOARD Section board and parallel to fotovoltaic pannels strings. In line with: CEI 17-13/1, CEI 17-11, 17-44 and subsequent variations; UL94-V0.
Construction caracteristics: - from the exterior side cassette in fiberglass, appropriate for on wall or floor instalation, anti impact resistance of at least 6 J, dielectric resistance of at least15 kV/mm, complete of prestamped closing doors and connections in fiberglass, autoestingueting; door with transparent window; gasket in alveolar closed cells neopren; bottom sheets appropriate for devices instalation ; protection level min. exterior IP55, internal IP20D; - cable entrance trough fairleads, glands, cone tube connections pluggable with interposed gasket; - n.1 copper bar , of minimal section 20x5 mm2, rounded angles, complete of perforated holes for equipotential connections trough case with screws; - n.2 copper bar, of minimal section 20x5 mm2, rounded angles,with perforated holes for phase condutors anchorage (with case with screws) in arrival from diferent disconnectors for realisation in parallel of pannels or fotovoltaic strings and connection to main line disconnector; - cabbling with cable type H07RN-F or analog having working temperature non under 90°C. - disconectors having following caracteristics: * isolation voltage Ui: 1000V cc; * nominal voltage: 800Vcc; * impulse voltage Uimp: 8kV for load until 125A, 12kV for load over 200A; * maneuver cycles (for load in cc cat. DC22): at least 20000 for load until 20A, 10000 for load from 63 to 125A, at least 5000 for load over 200A: * low duration admissible power for 1 sec. Icw: 1,3 (for load in cc cat. DC22): at least 1,3kA for load until 20A, 7kA for load until 63, 9kA for load until 125A, 13kA for load until 250A; * load in working category DC22 as indicated in grafic studies or valuated on the basis of: ** string disconector: string power increased of 25%; ** main disconector: sum of loads of each string disconector; * screw connection grips; * blocking possibility buy lock and key. - limitator/s of overvoltage having following caracteristics: * in line with: CEI 37-8 and subsequent variations. * classification: type 2 (class II; C); * voltage on empty (Uoc stc): <= 500V; * continuative voltage (Uc cc): 350V (refered to failure testing on TOV); * level of protection(Up): < = 3 kV (< = 2 kV con 5kA); * discharge impulsive nominal power (8/20 s) (In): 20 kA. * maximal discharge impulsive power (8/20 s) (Imax): 40kA. * installation of pannel disconector or connection string of bar to the ground; * shell in termoplastic material composed by multipolar base on which innested limitator modules as guarantee for easy substitution in case of failure; * oxid zinc varistor tecnology with Ycircuit (n.2 varistor e n.1 spinterometer or n.3 varistors with high performances); * optical failure signalisation; * distance report of failure signalisation; * click instalation as by DIN.
diode for protection of inverse polarities for each string having following caracteristics: * Vcc: 800V (inverted voltage) * I: 20A (inverted power); INTERNAL SECTIONING BOARD Internal sectioning board installed on field board in proximity of inverter. In line with: CEI 17-13 and subsequent variations. Construction caracteristics: - central in tecnopolimer with minimal exterior protection level IP55, internal IP20D, complete of transparent door, lock same as for other boards, circuit identification number; - blocking diode with following caracteristics: * Vcc: 800V (inverted voltage) * I: 20A (inverted power); - disconector with following caracteristics; * isolation voltage Ui: 1000V cc; * nominal voltage: 800Vcc; * impulse load voltage Uimp: 8kV for load until 125A, 12kV for loads over 200A;
* manouvre cycle (for loads in cc cat. DC22): at least 20000 for load to 20A, 10000 for load from 63 to 125A, at least 5000 for loads over 200A: * short admissible voltage for 1 sec. Icw: 1,3 (for loads in cc cat. DC22): at least 1,3kA for load to 20A, 7kA for loads to 63, 9kA for loads to 125A, 13kA for loads over 250A; * load in working category DC22 as indicated in graffic study or equal to main disconector located on field boards; - n.1 coppar bar, of minimal section 20x5 mm2, round angles, complete of perforated holes for equipotential connections trough screw case; - over voltage discharger of at least class 2 with caracteristics analog to the one installed in field boards. ELECTRICAL CONVERSION SYSTEM Inverter automaticaly controoled based on IGBT technology and commutation modalities on high frequency (modulation PWM) and variation impedance dispositive in entrance for constant power calibration (function MPPT maximun power point tracker). In line with norms : CEI EN 61000-3-2, 61312 and subsequent variations. - n.4 inverter 7,6 kW (side c.a.), caracteristics: * Vin CC max: 845V; * Range MPPT 330 - 700 V cc; * minimal european efficiency : 94,5%; * voltage in exit 230Vca - n.3 inverter 5 kW (lato c.a.), caracteristics: * Vin CC max: 845V; * Range MPPT 330 - 700 V cc; * european minimal efficiency: 94,5%; voltage in exit 230Vca Inverter price should be inclusive of electrical cabbling for connection to electrical board c.a. interface protection.
Supply and instalation sould include following final documentation: - Conformity declaration on electrical generation plant; - Activation and testing (collaud) certificate for fotovoltaic plant; - Conformity declaration of connection precriptions to lectrical network; - Installed devices attests (brand, model, registration number of each single fotovoltaic pannel and static conversion dispositive); - deatiled scheme of tecnological plants with indication of each device (as-built version); - Executive designs complete of eventual variants; - Technical and maintainance catalogues of all devices; - Instruction manual for the correct use and maintanance of plants and devices.
Photovoltaic system with HIT tecnology modules, power peak 44505Wp, cables, distribution boards, inverters, metallic profiles, interface
| ROOF LEVEL - PHOTOVOLTAIC SYSTEM |  | 1
| Total amount |  | 1 | 165000
TOTAL VARIOUS WORKS
TOTAL ELECTRICAL - GROUND FLOOR AND UPPER FLOOR LEVELS
TOTAL ELECTRICAL