1. INTRODUCTION

Based on the Offer accepted by the Investor, company "GEOTEHNIKA PLUS" Ltd from Niksic performed detailed geotechnical field survey of the location planned for construction of waste water treatment plant, urban lot (UP1) which consists of cadaster lot no. 76 and parts of cadaster lots no. 24, 31, 34, 35, 38, 73, 74 and 75, Cadaster area Dolac, area LSL "Donji Talum", in Berane.

The aim of survey works was to define geotechnical requirements for constructing waste water treatment plant on the given location. Within the complex, the following buildings were planned for construction: building for mechanical treatment, mechanical and electromechanical workshop, aggregate, sludge treatment plant, CBR- basins, building with compressors and equipment for sludge thickening, administration building, overflow chamber- II phase and power substation. Total surface area of the complex is 25 879.80 m2. Surface area of plant buildings (all buildings consist of ground floor) is 4 122.25 m2 (floor area and lot coverage are 0.16). Manipulative area is 4 593.77 m2 and greenery 17 163.78 m2. Aside from the stated buildings, access road, which will connect the plant with the surrounding traffic, will be built.

Survey works included field, laboratory and office works. Field works implied engineering-geological mapping, pit boring, bore pit core mapping, digging exploratory cuts, mapping exploratory cuts, taking samples for laboratory tests and geotechnical supervision of field work. The taken samples were tested in the laboratory. Based on the obtained results and data collected from the official records and literature, Elaborate on performed geotechnical research for the purpose of completing the Final plant Design was finished.

The elaborate offers information about geological structure, morphology, engineering-geological and hydrogeological features of the site, seismic aspects, geotechnical requirements for plant construction and conclusions and recommendations for the designer.

Andrija Delibasic, Engineering Geologist and Sladjana Vukasinovic, Engineering Geologist participated in carrying out of the works and writing the Elaborate.

The works were carried out in April 2013.

2. OVERVIEW OF EARLIER RESEARCH AND USED BEDS

All available documentation from prior research and specialized geological research was collected, analyzed and studied for the purpose of writing the Elaborate on completed geotechnical research for the Final Design of Waste Water Treatment Plant (WWTP) and access road in Berane.  General geological research included the following regional geological, engineering-geological and seismologic research:

- OGK list Ivangrad 1:100 000 with legend: Zivaljević Milorad et al, Institute for Geological Research SRCG, Titograd, 1979.

- Seismic regionalization map of FR Montenegro 1:100 000 with legend, Vasilije Radulovic et al.

- Regional engineering-geological research of North-eastern Montenegro, volumes I and II, Jokic Dusan et al, Institute for Geological Research SRCG, Titograd 1980.

- Regional maps of the territory of Montenegro: Tectonics map, Neotectonics map 1:100 000, Geomorphological map 1:200 000.

- Geological beds for spatial plan of the Republic, Engineering-geological map of Montenegro 1:100 000.

The following specialist geological research was used:

- Seismological beds for seismic micro-regionalization of urban area of Ivangrad with Andrijevica, Jokic Dusan, Ivanovic Goran et al. Institute for Geological Research SRCG, Titograd, 1985.

Aside from the stated documents, we used geotechnical surveys of various buildings in Berane carried out by numerous developers.

3. OVERVIEW OF RESEARCH METHODS, WAYS AND PROCEDURES

Numerous types of works have been performed during the execution of the Elaborate on performed geotechnical research. The works can be divided to: field survey works, laboratory testing and office data processing works. The Elaborate is a result of data synthesis of all works.

The survey works included engineering-geological mapping of the plant and access road area, pit boring, bore pit core mapping, digging exploratory cuts, mapping exploratory cuts, taking samples for laboratory tests and geotechnical supervision of field work. One pit boring was performed at the location of the future pump station at waste water network near the bridge.

Laboratory testing implied testing soil samples for the purpose of determining the parameters necessary for appropriate calculations and analysis. Samples of all bore pits and cuts (except the bore pit for the pump station by the bridge) were taken and tested. Materials are mostly non-cohesive, sandy-gravel and dusty, so we could only perform identification-classification tests and define deformability parameters. One sample is taken and tested for the purpose of determining optimal moisture by Proctor and CBR parameter value for the needs of access road.

Office works included processing data from field and laboratory research, as well as carrying out appropriate calculations and analysis. These results and official records were used as base for completing the Elaborate on geotechnical characteristics of the area for the purpose of constructing waste water treatment plant in Berane.

Planned and performed scope of works is sufficient for reviewing engineering-geological characteristics of the area and defining geotechnical requirements for road construction.

It can be concluded that planned and performed scope of work, along with official records data, is sufficient for reviewing geological characteristics of the area and defining geotechnical requirements for constructing waste water treatment plant and access road.

4. SCOPE AND TYPE OF THE PERFORMED RESEARCH

4.1. Field works

- engineering-geological mapping of the area; mapping was carried out on the location of the future plant and in the surroundings of the access road. As the area is almost completely covered, mapping was carried out by registering engineering-geological processes and appearances. Diabase-chert formation was discovered on a small area. The area from the plant location to the primary traffic route, surface area of cca 13 ha, was mapped. Engineering-geological field map, 1: 1 500 scale, was given in attachment  number 3,

- pit boring; 6 bore pits were dug at 8 m depth, 5 of which were on the location of WWTP and one at the pump station by the bridge. Bore core mapping was carried out successively. Engineering-geological profiles of the bores were given in attachment number 6. The following table gives an overview of performed pit boring:

Table no. 1: performed pit boring

| Pit mark | Depth (m) | coordinate X | coordinate Y | level Z |
| --- | --- | --- | --- | --- |
| B-1 | 8.00 | 4 747 072.86 | 7 408 148.46 | 659.00 |
| B-2 | 8.00 | 4 747 037.64 | 7 408 109.98 | 659.00 |
| B-3 | 8.00 | 4 747 037.64 | 7 408 148.44 | 659.50 |
| B-4 | 8.00 | 4 747 037.64 | 7 408 189.78 | 659.60 |
| B-5 | 8.00 | 4 746 946.77 | 7 408 148.44 | 659.45 |
| B-6 | 8.00 | 4 746 323.65 | 7 408 494.99 | ***.** |

- digging exploratory cuts; 6 exploratory cuts were dug at depth of 1.2 to 2.3 m. Engineering-geological mapping of the cut walls and floor was carried out after the digging. Exploratory cut profiles were given in attachment number 7. The following table gives an overview of performed exploratory cuts:

Table no. 2: overview of performed exploratory cuts

| Cut mark | Dimensions (m) | Coordinates |  | Level |
| --- | --- | --- | --- | --- |
|  |  | X | Y | Z |
| R-1 | 1.80 x 0.90 x 1.60 | 4 746 994.79 | 7 408 148.45 | 659.55 |
| R-2 | 2.10 x 1.20 x 1.20 | 4 746 943.73 | 7 408 110.56 | 659.80 |
| R-3 | 1.70 x 0.70 x 1.50 | 4 746 945.45 | 7 408 065.79 | 662.20 |
| R-4 | 2.00 x 0.70 x 2.20 | 4 746 950.75 | 7 408 037.79 | 662.30 |
| R-5 | 2.00 x 0.70 x 2.30 | 4 746 957.94 | 7 408 012.06 | 662.75 |
| R-6 | 2.70 x 0.70 x 2.20 | 4 746 963.10 | 7 407 980.45 | 665.00 |

- taking samples for laboratory geomechanic testing; during the mapping of bore pits and exploratory cuts, 12 samples of soil were taken for laboratory, 5 of which were from the bores and 7 from the cuts,

- expert, geotechnical supervision; field survey works were continuously supervised by geotechnical engineer.

4.2. Laboratory testing

Laboratory geomechanic testing was carried out on the taken samples. Procedures and results of laboratory tests are given in documentation material at the end of the Elaborate. Identification-classification tests and deformability features were determined for 11 samples, while Proctor's and CBR-test were performed on one sample. The given tests determined the following:

- volume weight in the state of natural moisture and in dry state,

- specific weight,

- natural moisture,

- granulometric composition,

- Atterberg limits of consistency,

- modulus of compressibility (Edometric test),

- optimal moisture by Proctor,

- CBR parameter.

4.3. Office works

The results of prior survey works had been interpreted, processed and synthetized with the information from the official records and literature, after which the Elaborate on performed geotechnical research for the purpose of completing the Final Design of waste water treatment plant and access road in Berane was finished.

5. REVIEW OF TEST RESULTS

5.1. Geomorphological characteristics of the area

The plant itself is located on a relatively flat area on the left bank of the river Lim. Channel of the river Lim and Jasikovac hill on the right side of the river are dominant morphological forms of the surrounding area. Berane basin is opened to the north and south. Ground level at the plant location is from  658 to 660 mnm. Mild hill-side, 5 do 150 in slope, stretches from the alluvial plane of Lim river bank towards the primary route. Ground level is from 660 at Lim alluvium to 675-690 mnm at the primary route. Hill-side next to the highway is relatively flat with small steep declivities which represent terraced cuts. The cuts are alleviated in the arable land part.

The stream of the river Lim formed 4 river terraces (3 of which are at the site) and thus had a dominant influence on the morphology of the site and its surroundings. Today’s layout of the site has been primarily formed by depositing of fluvial material and line erosion of the river flow. Additionally, anthropogenic activities, i.e. building and road construction, have had influence on the layout and morphology of the area.

5.2. Geological composition of the area

Wider area of the site planned for constructing waste water treatment plant in Berane is composed of sediments of Jurassic, Oligo-Miocene and Quarternary age. As for the tectonic aspect, the area belongs to Lim tectonic unit.

Area bed consists of Jurassic (J33) diabase-chert formation sediments with sandstones, diabase, cherks, and sporadical shale, marl and marly limestone. Thickness of diabase-chert sediment formation is changeable, and according to OGK of „Ivangrad” 1:100 000 it could be up to 350 m. Oligo-Miocene (OL,M) lake sediments are developed in Lim valley around Berane. Lithological composition includes marl, clay, sand, sandstones and sporadical gravel, as well as conglomerates with coal layers. Marl is dominant, while its outcrop is visible in the river channel on the other side of the bridge, i.e. at the location of pump station location.

Quarternary sediments at the research area include alluvial deposit (al), glacio-fluvial terraces (t1-t3) and diluvium (dl) on the surface. Alluvial deposit fills the channel of the river Lim and its tributaries and it is composed of gravel, sand, marl, mud, sand and sandy clay. Terraces of the river Lim are developed in the area of Berane basin. There are three levels of terraces at the site, form the highway to the flat plateau on the bank of Lim, where the plant is to be constructed.

Geologic map of the area is given in attachment number 2.

5.3. Engineering-geological characteristics of the site

5.3.1. Site zoning

There are several quazihomogenous zones, i.e. areas with similar geotechnical characteristics at the location of the plant, access road and pump station. These zones are within Quarternary sediments and basic area. Zones within Quarternary sediments are different by genesis and geotechnical characteristics. Basic rock from diabase-chert formation is in the bed of the plant and access road location at various depths (from 2.8 to over 10 m). Miocene marl is on the surface of the pump station site. Separate zones are shown by depth, starting from the site surface:

- Alluvium – alluvial deposit consisting of dust, sand, gravel and large marl, deposit is grey in color and present at the plant location (presented as no. 1 on area section).

Photographs no. 1 and 2: alluvial deposit in cut R-1

The middle part is non-cohesive, middle to well compacted and consolidated. The surface part (1 to 2 m) consists of humified and wet fine dusty sand. Deeper parts contain sand, gravel and large marl, immersed and water logged, as shown on the photographs above. As for lithological composition, they are mainly sandstones, vulcanite and limestone, well rounded and processed. Material is of uniform granulation in the middle part, but well granulated in the lower part (all fractions are present). Thickness of the middle part is changeable, from 2.8 m (B-2) to over 10 m (B-5). The middle part has good bearing capacity and low compressibility for the expected load, except the surface, humified layer (up to maximum of 0.5 m). According to GN-200 categorization, material is classified as II and III category of excavation. Based on laboratory test of soil samples, official records and direct field assessment, physical-mechanical parameters of the area are given in the table below:

Table no. 3: physical-mechanical parameters for alluvium

| Parameters | Value range |
| --- | --- |
|  (kN/m3) | 18.5 - 20.0 |
|  (0) | 30.0 - 32.0 |
| c (kN/m2) | 0.0 |
| Ms (kN/m2) | 8 000 - 10 000 |

- Diluvium – hill-side deposit on the area surface consists of sand, dust and fine debris, with presence of clay, grey in color (presented as no. 2 on area section).

Photograph no. 3: diluvium in cut R-3

The middle part is a bit wet, humified on the surface, with medium compactness and consolidation. Casagrande classification defines it as inorganic clay of medium plasticity (CI). The clay is visible at terraced sediments on site and its thickness is from 0.6 m (R-6) to over 2.5 m (R-4). According to GN-200 categorization, material is classified as II and III category of excavation. Based on laboratory test of soil samples, official records, direct field assessment and area characteristics, physical-mechanical parameters of the area are given in the table below:

Table no. 4: physical-mechanical parameters for diluvium

| Parameters | Value range |
| --- | --- |
|  (kN/m3) | 19.5 - 20.0 |
|  (0) | 22.0 - 26.0 |
| c (kN/m2) | 8.0 - 12.0 |
| Ms (kN/m2) | 4 000 - 6 000 |

- Terraced sediments – constitute the hill-side from alluvial plane to the highway. They consist of sand, gravel and large pebbles, are dusty, with some presence of clay, wet, grey in color (presented as no. 3 on area section).

Photograph no. 4: terraced sediments in cut R-6 (surface part)

The surface part (up to approximately 2.0 m) consists of a lot of dust and fine fraction, while deeper layer consists of “clearer” sand, gravel and pebbles, well compacted and binded by carbonate and dusty binder. Estimated depth of terraced sediments on this part of the site is up to 10 m. According to GN-200 categorization, material is classified as III and binded parts at larger depth as IV category of excavation. Based on the laboratory test of soil samples, official records and direct field assessment and area characteristics, physical-mechanical parameters of the area are given in the table below:

Table no. 5: physical-mechanical parameters for terraced sediments

| Parameters | Value range |
| --- | --- |
|  (kN/m3) | 19.5 - 20.5 |
|  (0) | 26.0 - 30.0 |
| c (kN/m2) | 10.0 - 20.0 |
| Ms (kN/m2) | 6 000 - 8 000 |

Diabase-chert formation – is in the bed and backing of the site and consists of various lithological members, mostly of sandstone, diabase and chert, with sporadical presence of shale, marl and marly limestone.  Formation may be in form of compact rock or sandy-dusty matrix with debris and parts of the mother rock which only sporadically shows primary stratification. The formation is presented in these two forms, which are not directly related to the depth of the layer. These formations may appear on the surface, as well as in the deeper layers. Sandy-dusty matrix with debris and parts of sandstone, diabase and chert, completely dry (hydro-geologically impervious), grey-blue is present in the bed of the future plant site and in bores B-1, B-2, B-3 and B-4. Matrix is found at 2.8 to 3.8 m depth in four bores, while in bore B-5 it could not be dug as its depth is more than 10 m. Outcrop of the compact formation is visible on the hill-side under the highway and on the local road above the highway. According to GN-200 categorization this area is classified in IV and V category of excavation. If the area is compacted, it is classified as VI category of excavation. Based on official records and direct field assessment, physical-mechanical parameters of the area which represents the bed of the future plant are given in the table below:

Table no. 6: physical-mechanical parameters for diabase-chert formation

| Parameters | Value range |
| --- | --- |
|  (kN/m3) | 23.0 - 24.0 |
|  (0) | 30.0 - 35.0 |
| c (kN/m2) | 80.0 - 100.0 |
| Qu (kN/m2) | 1 000 - 1200 |

- Marl – grey and brown marl layers are present on the location of the pump station by the bridge. The surface layers are decomposed and degraded, while deeper layers are fresh. Depth of decomposed zone is approximately 3.0 m. Outcrops of these sediments are visible under the bridge and on the bank. Layers are subhorizontal or slightly sloped towards the south. Official records indicate that the depth of Miocene sediments is up to 250 m. According to GN-200 categorization, the area is classified as IV and V category of excavation.

Photograph no. 5: marl in the river channel and at pump station location

Based on official records and direct field assessment, physical-mechanical parameters of the area are given in the table below:

Table no. 7: physical-mechanical parameters for marl

| Parameters | Value range |
| --- | --- |
|  (kN/m3) | 24.0 - 25.0 |
|  (0) | 32.0 - 35.0 |
| c (kN/m2) | 100.0 - 120.0 |
| Qu (kN/m2) | 1 500 - 2 000 |

5.3.2.	Relevant physical-mechanical parameters of the chosen area

The following table shows accepted values of physical-mechanical parameters for the chosen area which are relevant for geostatic calculations.

# Table no.8: parameter values of physical-mechanical characteristics

| Geotechnical area | P a r a m e t e r s |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | γ (kN/m3) | φ (0) | c (kN/m2) | Ms (kN/m2) | Qu (kN/m2) |
| 1 –Alluvium | 19 | 30 | 0 | 8 000 | - |
| 2 -Diluvium | 19.5 | 24 | 10 | 4 500 | - |
| 3 -Terrace | 20 | 28 | 10 | 6 500 | - |
| 4 –Diabase-chert formation | 23 | 30 | 80 | - | 1 000 |
| 5 –Marl | 24 | 32 | 100 | - | 1 500 |

5.3.3.	 Contemporary geodynamic processes and appearances

Planar and fluvial erosion of the rivers Lim and Makva are contemporary geodynamic processes which are present intthe area planned for construction of the plant, as well as in its surroundings.

Planar erosion is, to a larger or smaller extent, present in the entire area. Due to the mild slope of the area, erosion intensity is low and visible in slight washing off the terrain. Material is washed off and taken to Lim or Makva rivers. During high water levels or floods, the process is reverse. Rivers bring mainly fine deposit and accumulate it in flat riparian area. This deposit is separated as surface part of the alluvium which consists of fine dusty sand. Generally speaking, this process is periodic and includes the whole flat part of the site planned for constructing the plant. Lim flood flow at the site is to be determined in order to define plant foundation level which will be safe from the flood.

Aside from this appearance, the area is stable. However, the construction of the plant and access road must be performed carefully in order to avoid disturbing stability.

5.4. Hydrogeological features of the area and soil

Hydrogeological features of the area are directly connected with its lithological composition. The area consists of layers with various throughput, intergranular and fracture porosity.

Alluvial sediments of intergranular porosity have medium and high throughput. They form compacted outcrop with free level which is directly connected with water level in Lim. Water level is present in all bore pits and cuts in the area. Water level slightly descends towards Lim, from the west to the east. Surface zone, which consists of dusty sand, has medium to low throughput, while deeper parts show medium to high throughput.

Diluvial sediments have low throughput and are of intergranular and capillary porosity. Terraced sediments also have low throughput and are of intergranular porosity.

Diabase-chert formation and Miocene marl have low throughput in the surface zone, while in deeper zones they are practically impervious, of fracture and fissure porosity.

During the research period (April 2013) recorded underground water level in alluvium was from 0.45 (B-2) to 1.5 m (B-4) of depth, depending on the area morphology.

General conclusion is that the terrain has low throughput, as well as that the bed is impervious, except the alluvium where water level has been registered.

5.5. Seismic aspect of the site

Seismic intensity scale is shown on Seismic regionalization map of Montenegro 1:100 000, which represents the final result of complex seismologic study of the seismic aspect of the area and degree of earthquake risk on the territory of Montenegro. According to the above stated map, the area of Berane is in seismic zone 8. This complies with the results of seismic design which has shown that the maximum earthquake intensity for this area is I=8.1 of MCS scale, the probability for 100 year recurrence period being 63%.

Overview of recurrence periods, earthquake intensity scale and expected bedrock acceleration (ao) are given in the following table:

Table no. 9: earthquake parameters

| Recurrence period t (year) | I (MCS) | ao(g) |
| --- | --- | --- |
| 50 | 7.6 | 0.120 |
| 100 | 8.1 | 0.157 |
| 200 | 8.5 | 0.185 |

According to the Map of seismic micro-regionalization of urban area of Ivangrad with Andrijevica, the observed area belongs to seismologic zones C1 and N. Zone C1 includes the hill-side from the alluvial plane to the highway, composed of Quarternary (terraced) sediments.

Zone N includes alluvial plane where the plan is to be constructed. It is defined as unstable soil, due to occasional flooding by ground and underground water with liquefaction potential. This refers to surface zone (1 to 2 m) which consists of dusty sand of uniformed granulation.  Geotechnical model of the area, which is specific for the given location, is given in the following table:

Table no. 10: specific geotechnical model of the area GTM-5

| H (m) | Vp (m/s) | Vs (m/s) |  (kN/m3) | Composition |
| --- | --- | --- | --- | --- |
| 2.0 | 450 | 175 | 18.0 | Sand and dust |
| 8.0 | 1000 | 380 | 19.0 | Sand and dust |
|  | 2700 | 1250 | 24.5 | Diabase chert formation |

The expected maximum average acceleration on the surface is defined based on mutual influence of regional and local seismogeologic features of the area and represented by multiplying the appropriate bedrock acceleration (ao) and average acceleration coefficient (KA).

amax(g) = ao(g) x KA

Seismic parameters for design in zone C1 for recurring periods (t) of 50, 100 and 200 years are:

Table no. 11: design seismic parameters for zone C1

| Zone | Specific seismogeologic zone | Recurrence period t (year) | Bedrock acceleration ao(g) | KA | Peak ground acceleration amax(g) | Seismic coefficient Ks (amax/4g) |
| --- | --- | --- | --- | --- | --- | --- |
| C1 | Fluvial-alluvial sediments, conglomerates, clay, sand and gravel | 50 | 0.120 | 1.80 | 0.216 | 0.054 |
|  |  | 100 | 0.157 |  | 0.283 | 0.071 |
|  |  | 200 | 0.185 |  | 0.333 | 0.083 |

Dynamic coefficient Kd is determined in accordance with the Article 25. of the Rulebook on technical norms for constructing civil engineering buildings in seismic area and is:

Kd=0.7/T		1.0 > Kd > 0.47

6. GEOTECHNICAL REQUIREMENTS FOR PLANT CONSTRUCTION

6.1. Requirements for plant construction

Requirements for plant construction are complex. The area is flat, but with high water level (Quarternary alluvial deposit is water logged) throughout the year. Additionally, the area is occasionally flooded and its surface part has liquefaction potential.

Due to the above stated, measures for improving the features of foundation ground and reducing liquefaction are to be taken. Surface sand-dusty material is to be removed up to adequate depth without reaching the level below underground water level, if possible. Afterwards, stone material is to be filled up to the level which is safe from flooding. Filling is to be carried out layer by layer with rolling and compacting (minimum compatibility degree of the filling layers is to be 60 MPa). This will reduce the thickness of the layer which is subject to liquefaction, increase foundation level above the flooding level and result in obtaining high quality ground for building foundation. These works are to be carried out in hydrological minimum, i.e. in dry period of the year when underground water level is the lowest.

It would be the safest to remove entire surface layer of problematic alluvium, or its larger part, if possible.

Geostatic calculations (allowed load and base subsidence) are carried out under the assumption that the plant building is founded on the filling after the material has been replaced up to 658.5 level, i.e. up to the current water level. Filling thickness would be approximately 1.5 m, on various types of foundations. Calculations are carried out by means of Brinch-Hansen method with partial safety factors: Fc=2.5 and F=1.5. Subsidence calculation is carried out by means of modulus of compressibility for centering point. The assumed load made by the building is up to 100 kN/m2. The following values of physical-mechanical parameters for the filling and alluvium are used:

Filling:

 = 23.0 kN/m3,    = 34,  c = 0 kN/m2,  Ms = 60 000 kN/m2,

Alluvium:

’ = 9.0 kN/m3,    = 30,  c = 0 kN/m2,  Ms = 8 000 kN/m2,

In case of founding the plant on foundation strips, width from 1 to 2 m, foundation depth 1m, calculation results are the following:

Table no. 12: results of geostatic calculations for foundation strips

| Foundation depth Df (m) | Strip width B (m) | Allowed load Qa (kN/m2) | Subsidence s (cm) |
| --- | --- | --- | --- |
| 1.0 | 1.0 | 369.43 | 0.928 |
|  | 1.5 | 385.99 | 1.405 |
|  | 2.0 | 319.36 | 1.871 |

In case of founding the building on RC (reinforced concrete) slab, calculation of allowed load and subsidence is carried out for the same area parameters and building dimensions 25 by 25 m (dimensions of CBR basin). Calculation results are given in the table below:

Table no. 13: geostatic calculations for foundation RC slab

| Foundation depth Df (m) | Dimension of RC slab BxL (m) | Allowed load Qa (kN/m2) | Subsidence s (cm) |
| --- | --- | --- | --- |
| 1.0 | 25 x 25 | 358.62 | 5.280 |

The calculation shows that the values of allowed load are satisfactory, while subsidence is within the limits of allowed values.

6.2. Requirements for access road construction

Requirements of access road construction are changeable. In the flat part of the alluvium, material could be replaced up to the level above Lim flood flow in the similar way as it will be done with the plant. As for the other part of the area, it would be enough to remove surface humus layer, thickness cca 30 cm and then construct the road.

Safe construction implies preparing the base in high-quality manner, choosing good material and placing the filling adequately.

Base preparation has already been described and consists of removing the surface humus coating. Base is to be leveled and rolled. Alluvium from river Lim channel and banks can be used as material for road embankment. Additionally, river terrace material, which the entire Berane basin is made of, can be used. Terraces are of the same composition as alluvium, except that they are binded by dusty or carbonate binder. The chosen material is to be clean and well granulated (all fractions are to be present equally).

Placement of the material in the embankment is to be carried out in accordance with the appropriate standards. This implies filling layer by layer with rolling and compacting until the designed modulus of compressibility is reached. Compaction test is to be carried out for each placed layer by means of circular plate test on sufficient number of measuring points.

Special securing of the embankment is not necessary. Final embankment slopes are to be 1:1.5. Road structure calculation will accept CBR value of 15, even though the tested sample showed higher values.

6.3. Requirements for pump station construction

Requirements for pump station construction are favorable. It will be founded in Miocene marl which consists of solid rocks, mildly petrified. They are of favorable geotechnical features, stable and have good load bearing capacity. Minimum load bearing capacity is 350 kN/m2 while their subsidence can be neglected, as this is practically non-deformable area for the expected load. Even though marl, as working environment, is stable and has favorable layer orientation, the building is not to be built close to the steep bank.

7. CONCLUSIONS

In engineering-geological terms, the area of the future waste water treatment plant and access road consists of alluvium of the river Lim and terraced sediments on the hill-side. Diluvium of changeable thickness is over the terraced sediments. Diabase-chert formation is deeper in the base. In hydrogeological terms, this is an area with medium and low throughput, intergranular and fracture porosity. Water level in alluvium is at 0.5 to 1.5 m depth. Underground water level is directly connected with water levels in Lim and Makva. Diabase-chert formation is hydrogeological insulator.

Geotechnical requirements for plant construction are complex. The area is flat, but with high water level, periodically flooded and subject to liquefaction in case of earthquake. Problematic material on the surface is to be replaced and filled up to the level which provides safety from the flood. If the replacement is carried out and high quality material (crushed sand) is filled, liquefaction risk will be reduced or even eliminated and high quality foundation ground will be provided for the buildings. Bearing capacity of the ground is much bigger than the expected load from the building, while subsidence is small and within the limits of allowed values.

Geotechnical requirements for access road are changeable- they are complex in alluvium and around the buildings, but favorable in other parts.  The material is to be replaced in the alluvium, just like in case of the buildings. As for the other parts, the surface layer of humus, up to 30 cm of thickness, is to be removed and then the road can be constructed.

Geotechnical requirements for pump station construction are favorable, as the construction will be carried out on solid rocks- marl.

The performed scope of survey works has been sufficient for reviewing geological characteristics of the area and defining geotechnical requirements for constructing the plant, access road and pump station.

8. RECOMMENDATIONS TO THE DESIGNER

In order to carry out the construction of the plant and access road safely, the following recommendations should be taken into consideration:

- complete material excavation can be performed mechanically. According to civil engineering classification GN-200, layers are classified as II to IV excavation category,

- requirements for plant construction are complex. Removing the surface sand-dusty layer of alluvium and filling with high-quality material is recommended in order to reduce or eliminate liquefaction risk and provide high-quality foundation ground for the buildings,

- plant buildings are to be adequately founded on the filling. RC slab is recommended,

- requirements for access road construction are changeable- complex in the alluvium, but favorable in other parts,

- requirements for pump station construction are favorable, as this will be carried out on solid rocks,

- filling is to be placed in accordance with the standards related to that type of works. Base and layer compactness are to be tested by means of circular plate test,

- earthworks are to be carried out in hydrological minimum, i.e. in dry period of the year when Lim level is the lowest. All watercourses, including the largest (Lim) are of torrential character,

- supervision of Engineering Geologist for geotechnics is recommended during the excavation and filling works.

Niksic, April 2013.

Works Manager:

____________________________

Andrija Delibasic, Engineering

Geologist

LITERATURE AND OFFICIAL RECORDS

- Bešić Z. (1959): Geološki vodič kroz NR Crnu Gore, Posebna izdanja Geološkog društva NR Crne Gore, Titograd,

- Cvijić J. (1996): Geomorfologija, knj. II, Izdanje državne štamparije, Beograd,

- Živaljević M. i dr. (1979): Osnovna geološka karta lista “Ivangrad” 1:100 000 sa Tumačem, Zavod za geološka istraživanja SR Crne Gore, Titograd,

- Jokić D. i dr. (1985): Seizmogeološke podloge i seizmička mikrorejonizacija urbanog područja Ivangrada sa Andrijevicom, Zavod za geološka istraživanja Crne Gore – Titograd

- Radulović M., (2000): Hidrogeologija karta Crne Gore, Posebno izdanje Geološkog glasnika, knjiga XVIII, Podgorica,

- Fondovski materijal  "GEOTEHNIKA PLUS" d.o.o., Nikšić.