## Foglio di lavoro in Preventivo
D-2 | LANDSCAPING - ELECTRICAL INSTALLATIONS
NO. | DESCRIPTION | unit | QTY | unit price | total
01 - CONDUCTORS, CABLES AND ACCESSORIES
A110.A10.A20 |  | m
MEDIUM-VOLTAGE CABLE, XHE TYPE. Insulation: ethylene-propylene rubber, G7 quality. Enclosure: PVC. Conductor: annealed tinned copper wire, filled with synthetic semi-conducting elastomer.
Protection: copper strip installed on the coil. Armature (if envisaged): galvanized steel strip placed underneath the outer protection layer. In contact with flame: does not incite flame spreading - reduced emission of corrosive gases. For the connection of the newly designed single-core cable 12/20 kVA to the existing cable IPO 13 3x95 mm2, appropriate joints should be used, i.e. joints type EPKJ-24C/1XU-3 SB of the Raychem manufacturer. Installation of joints to be calculated in the price.
cable XHE 49-A 12/20kV, 1x240 mm2
1710
| Total |  | 1710
TOTAL FOR CONDUCTORS, CABLES AND ACCESSORIES
02 - DUCTS
B50.A20.A1 |  | m
FLEXIBLE PROTECTIVE HIGH-DENSITY POLYETHYLENE TUBE TO BE LAID IN THE GROUND. Compliance with the following norms: CEI 23-39, 23-46 and further variances. Classification: not lower than 3441. Pressure resistance: >= 450N
Impact resistance >= 6J. Electric resistance of the insulation >= 100Mohm. Dielectric strength >= 20kV/mm. Resistance to chemical agents and microorganisms. Make properties: high-density polyethylene tube
(PEHD) with double and smooth interior, and corrugated exterior walls; joints for the connection of several elements. System protection degree: min. IP4X.
Flexible high-density polyethylene tube D=50mm
868
| Total |  | 868
B50.A20.A8 |  | m
FLEXIBLE PROTECTIVE HIGH-DENSITY POLYETHYLENE TUBE TO BE LAID IN THE GROUND. Compliance with the following norms: CEI 23-39, 23-46 and further variances. Classification: not lower than 3441. Pressure resistance: >= 450N
Impact resistance >= 6J. Electric resistance of the insulation >= 100Mohm. Dielectric strength >= 20kV/mm. Resistance to chemical agents and microorganisms. Make properties: high-density polyethylene tube
(PEHD) with double and smooth interior, and corrugated exterior walls; joints for the connection of several elements. System protection degree: min. IP4X.
Flexible high-density polyethylene tube D=50mm D=160mm
950
| Total |  | 950
CD.A16.A1 |  | m3
EXCAVATION AT LIMTED AREAS USING MACHINERY Excavation at a limited area (digging up the trenches) regardless of the nature and strength of the soil, in presence of water lower than 20 cm, which can be done using machinery, except for
rocky areas. The price must include the following obligations: taking out the stone blocks of up to 0.400m3 volume; - removal of elements of all kinds up to 0.400m3 volume; - removal of plants and stumps;
possible soil drainage; - destruction of all types of asphalt and road surfaces that cannot be re-used; - levelling the ground; - depositing the material next to the excavation site; - filling the area with the material from the excavation;
preventive detection and registration of electric and telephone cables, water pipes, gas pipes, irrigation pipes, street drainage ducts and so on. Demolition and complete reconstruction of protective shields of compacted soil
damaged during the works; - selection of fine materials for re-burial of the pipe and soil possible present on the surface; - full recovery of the ground level using machinery
compaction of material and possible re-filling. The following is excluded from the price: - transport of excavated waste excess materials, and/or materials that cannot be re-used or is deemed inadequate; - landfill fee;
preventive cutting of asphalt or cement road surfaces. The volume of the excavated material will be calculated based on the usual width determined according to the provided types of cross section, and based on the designed depth for pipes laying, increased
according to the thickness of the base layer, which was also determined according to the provided cross section types, caused by the field features, presence of water
rocks and so on, or caused by weather circumstances , but all has to be completed pursuant to the regulations and in accordance with the instructions. During the excavation operation, safety of workers must be ensured at all times.
If the risk of collapse appears, the walls must be secured applying one of the following procedures: - supporting and applying temporary protection; appropriate sloping of the walls, greater volume of which is conditioned by
such wall sloping, that will be covered by the same price.
365
| Total |  | 365
CD.C12.A1 |  | m
CUTTING THE ASPHALT BASE Cutting of the asphalt base is carried out using the appropriate circular saw, calculated in for the efficient cutting operations. The price must include the following obligations:
marking the excavation with appropriate signs; - determining the presence of public service network in the subject area; cutting of the surface layer and binder using appropriate machinery. Except in case of strict order from the Supervision.
Only the first cutting of the existing base will be calculated in, and if it turns out that partial re-profiling is needed for full connection of the base with the renewed part.
290
| Total |  | 290
CD.D10.A1 |  | m3
BASE WITH THE CRUSHED ROCKS BINDER Creating the base and/or filling with crushed rocks, granulation of which is 0-30mm, assessed as suitable by the Supervision. The price must include the following obligations:
transport; - placement; - creation of a slope; - compaction; - a part of possible signal tape; - other things needed for execution of works
in compliance with regulations.
205
| Total |  | 205
CD.D32.A1 |  | m3
FILLING WITH SAND Provision and placement of the sand as a base and coverage of the pipes. The price must include the following obligations: transport; - placement;
compaction; - participation in possible procurement and placement of a warning tape 30 cm under the finished road surface; - other things needed for execution of works in compliance with regulations
115
| Total |  | 115
CE.A11.A16 |  | n
PREFABRICATED MANHOLE Prefabricated manhole made of vibrated reinforced concrete, 6-8- cm thick, for the connection of piping systems. The price must include: - obligations related to opening the holes
and for their sealing; - making a concrete prop (light concrete); - filling around the gutter; The price does not include: - cover lid; - excavation
Dimensions of the prefabricated manhole 60x60x20cm
2
| Total |  | 2
CE.A11.A2 |  | n
PREFABRICATED MANHOLE Prefabricated gutter made of vibrated reinforced concrete, 6-8- cm thick, for the connection of piping systems. The price must include: - obligations related to opening the holes
and for their sealing; - making a concrete prop (light concrete); - filling around the gutter; The price does not include: - cover lid; - excavation
Dimensions of the prefabricated manhole 40x40x40cm
31
7
| Total |  | 38
CE.A19.A1 |  | n
REVISION MANHOLE MADE ON THE SPOT Make of revision manholes of all types and dimensions for the control of networks in the places of use belonging to classes B125 and C250 according to the norm
Characteristics of the make: - cement conglomerate, properties of which are harmonised with UNI EN 206-1, UNI 11104 in accordance with DM 14. 9. 2005. Exposure class in the XC environment and characteristic strength of at least Rck UNI EN 124
> 25 N/mmq, mechanically manufactured; iron armature FeB44k with improved adherence controlled in the factory and shaped in envisaged quantities based on static calculations that will be made under the control of and at the expense of the Tender announcer. The price must
include: - proper disposition in accordance with the design levelling; - placement and removal of casting formworks; mechanical vibrations; - making the holes; - access staircase with steps made of
plasticized steel, dimensions 16x33 cm with the positioning elements, dimensions 25mm; - filling the material around the construction; - other things needed for execution of works in compliance with regulations. The price does not include:
potential reconstruction of the base; The price is defined based on the volume measured outside the manhole.
Dimensions of the revision manhole 150x150x100cm
9
| Total |  | 9
CE.C10.A43 |  | n
COVER LID MADE OF SPHEROIDAL CAST IRON The lid made of spheroidal cast iron consists of a frame for fixing, and the lid. Compliance with the norm UNI EN 124 Concordance with tables UNI 454. Strength class (depending on the type)
B125 with tensile strength of >= 125 kN (12.5t) for use in places such as sidewalks, pedestrian zones occasionally open for traffic, parking zones, multi-level parking lots for cars. - C250 with tensile strength of 250 kN (25t)
for placement on the edges of the roads stretching not more than 0.5 m within traffic lanes and up to 0.2 m on the sidewalks, roadsides and parking lots for heavy-duty vehicles; - D400 with tensile strength of >= 400 kN (40t)
for use on roads (I and II tier), in parking lots for all kinds of vehicles. Characteristics of make: square-shaped frames on the bottom and the top
with the protective external edges from all sides, rounded on angles not narrower than 20mm in order to ensure better fixing; if required, the U-shape frame to limit the penetration of
liquids (airlock type); sealing made of elastomer with the protection against noise and oscillations, placed in the appropriate semi-circular opening; cap with the lid locking system in the open position under 110; - spot for the placement of
the closing system; - anti-slip patterns on the walking surface; square lid with: anti-slip patterns; - slot for the lifting ley; closing by the means of
turning screwed bolt; - adequate extension to guarantee mobility of the frame and opening with a possibility of the lid drawing out; - height of 20mm, for the strength class B125,
40mm for strength class C250, 60mm for D400. Processing: fixing to the gutter applying lime cement screed at least 2 cm thick, and final sealing along the entire frame circumference; bolt for the earthing (if required by the Supervision)
Labels: - the lids will have to bear permanent and legible labels that refer to norm UNI EN 124; - inscription on the central part of the lid indicating the type of utility (e.g. PUBLIC LIGHT)
which should be defined at the seat of the Supervision. The strength class; - norms and/or constructor's mark; - potential label of compliance of a certifying institution.
Dimensions of the lid made of spheroid cast iron 40x40cm, class C250
| LANDSCAPING - VN/NN ROUTES |  | 31
| LANDSCAPING - EARTHING AND LIGHTNING PROTECTION INSTALLATION |  | 7
| Total |  | 38
CE.C10.A45 |  | n
COVER LID MADE OF SPHEROIDAL CAST IRON The lid made of spheroidal cast iron consists of a frame for fixing, and the lid. Compliance with the norm UNI EN 124 Concordance with tables UNI 454. Strength class (depending on the type)
B125 with tensile strength of >= 125 kN (12.5t) for use in places such as sidewalks, pedestrian zones occasionally open for traffic, parking zones, multi-level parking lots for cars. - C250 with tensile strength of 250 kN (25t)
for placement on the edges of the roads stretching not more than 0.5 m within traffic lanes and up to 0.2 m on the sidewalks, roadsides and parking lots for heavy-duty vehicles; - D400 with tensile strength of >= 400 kN (40t)
for use on roads (I and II tier), in parking lots for all kinds of vehicles. Characteristics of make: square-shaped frames on the bottom and the top
with the protective external edges from all sides, rounded on angles not narrower than 20mm in order to ensure better fixing; if required, the U-shape frame to limit the penetration of
liquids (airlock type); sealing made of elastomer with the protection against noise and oscillations, placed in the appropriate semi-circular opening; cap with the lid locking system in the open position under 110; - spot for the placement of
the closing system; - anti-slip patterns on the walking surface; square lid with: anti-slip patterns; - slot for the lifting ley; closing by the means of
turning screwed bolt; - adequate extension to guarantee mobility of the frame and opening with a possibility of the lid drawing out; - height of 20mm, for the strength class B125,
40mm for strength class C250, 60mm for D400. Processing: fixing to the gutter applying lime cement screed at least 2 cm thick, and final sealing along the entire frame circumference; bolt for the earthing (if required by the Supervision)
Labels: - the lids will have to bear permanent and legible labels that refer to norm UNI EN 124; - inscription on the central part of the lid indicating the type of utility (e.g. PUBLIC LIGHT)
which should be defined at the seat of the Supervision. The strength class; - norms and/or constructor's mark; - potential label of compliance of a certifying institution.
Dimensions of the lid made of spheroid cast iron 60x60cm, class C250
| LANDSCAPING - VN/NN ROUTES |  | 2
| Total |  | 2
CE.C10.C2 |  | n
COVER LID MADE OF SPHEROIDAL CAST IRON The lid made of spheroidal cast iron consists of a frame for fixing, and the lid. Compliance with the norm UNI EN 124 Concordance with tables UNI 454. Strength class (depending on the type)
B125 with tensile strength of >= 125 kN (12.5t) for use in places such as sidewalks, pedestrian zones occasionally open for traffic, parking zones, multi-level parking lots for cars. - C250 with tensile strength of 250 kN (25t)
for placement on the edges of the roads stretching not more than 0.5 m within traffic lanes and up to 0.2 m on the sidewalks, roadsides and parking lots for heavy-duty vehicles; - D400 with tensile strength of >= 400 kN (40t)
for use on roads (I and II tier), in parking lots for all kinds of vehicles. Characteristics of make: square-shaped frames on the bottom and the top
with the protective external edges from all sides, rounded on angles not narrower than 20mm in order to ensure better fixing; if required, the U-shape frame to limit the penetration of
liquids (airlock type); sealing made of elastomer with the protection against noise and oscillations, placed in the appropriate semi-circular opening; cap with the lid locking system in the open position under 110; - spot for the placement of
the closing system; - anti-slip patterns on the walking surface; square lid with: anti-slip patterns; - slot for the lifting ley; closing by the means of
turning screwed bolt; - adequate extension to guarantee mobility of the frame and opening with a possibility of the lid drawing out; - height of 20mm, for the strength class B125,
40mm for strength class C250, 60mm for D400. Processing: fixing to the gutter applying lime cement screed at least 2 cm thick, and final sealing along the entire frame circumference; bolt for the earthing (if required by the Supervision)
Labels: - the lids will have to bear permanent and legible labels that refer to norm UNI EN 124; - inscription on the central part of the lid indicating the type of utility (e.g. PUBLIC LIGHT)
which should be defined at the seat of the Supervision. The strength class; - norms and/or constructor's mark; - potential label of compliance of a certifying institution.
Dimensions of the lid made of spheroid cast iron 150x150cm, class D400
| LANDSCAPING - VN/NN ROUTES |  | 9
| Total |  | 9
CF.E10.A1 |  | m2
BINDER Procurement, placement and compaction of asphalt made in hot process for the formation of binder layer, granulation of 0-25, composed of aggregates obtained by crushing and mixing with the bitumen.
The price includes the following obligations: - cleaning and subsequent spraying of the surface; - protection and placement of safety signalisation; - all other obligations needed for the execution of works in compliance
with regulations.
Binder depth 7 cm
| LANDSCAPING - VN/NN ROUTES |  | 290
| Total |  | 290
TOTAL FOR DUCTS
08 - ENERGY DITRIBUTION AND POINTS OF SUPPLY
M10.A10.A1 |  | n
SOURCE OF LIGHT Source of light composed of: - part of the quota for the switchbox installed on the voltage post; lines going from the switchbox to
the lighting device (which is separately calculated); terminal box for the supply of the source of light (if necessary): in case of supply of two separate lights placed in the same lighting device for lighting, which includes modifications or integration of wires, addition for the price for double source of light will have to calculated in (for the source of light).
In case of supply of lighting devices with the dimming light, which includes modifications or integration of wiring addition for the price for the dimming source of light will have to be calculated in (to the source of light)
(excluding the resistors for light dimming and commands). The typology of cables for wiring must be the one envisaged in specifications and tables.
The used materials must be of characteristics listed in the appropriate chapter of this study.
The source of light on the wall with flexible PVC tube and cable.
| LANDSCAPING - LIGHTING |  | 249
| Total |  | 249
M10.A10.A8 |  | n
SOURCE OF LIGHT Source of light composed of: - part of the quota for the switchbox installed on the voltage post; lines going from the switchbox to
the lighting device (which is separately calculated); terminal box for the supply of the source of light (if necessary): in case of supply of two separate lights placed in the same lighting device for lighting, which includes modifications or integration of wires, addition for the price for double source of light will have to calculated in (for the source of light).
In case of supply of lighting devices with the dimming light, which includes modifications or integration of wiring addition for the price for the dimming source of light will have to be calculated in (to the source of light)
(excluding the resistors for light dimming and commands). The typology of cables for wiring must be the one envisaged in specifications and tables).
The used materials must be of characteristics listed in the appropriate chapter of this study.
Visible source of light with rigid PVC tube and cable IP65
| LANDSCAPING - LIGHTING |  | 68
| Total |  | 68
M20.A10.A32 |  | n
CONTROL SWITCH Control switch that make a part of the quota for the switchbox installed on the voltage post; the lines going from the switchbox to
the socket box; socket boxes to be installed in the wall, depending on the type, if necessary, with joints for cables; - control modular switch with the following characteristics
CIRCUIT BREAKERS, SWITCHES AND BUTTONS Compliance with norms CEI 23-9 and further variances, voltage and nominal frequency 250V , 50Hz. Current 10A for buttons and 16A for switches; trial voltage 2000V at 50Hz per 1min; breaking power:
200 openings and closings at 1.25 In, 275V, power factor 0.3; functioning test 50000 per In, 250 V, power factor 0.6; insulation resistance >15Mohm at 500V; - signal light for identification
(if required); LIGHT INTENSITY REGULATORS (DIMMERS) Voltage and nominal frequency 230V +/- 10%; controlled power 60-500W (for resistant loads), insulation resistance >15Mohm at 500V; regulation via rotation command or
a double-function button; extended button pressure to regulate increase or decrease, with electronic memorising upon the release of the button, short pressure for on and off function on the light with
the selected lighting value; protection switch; frame for the terminal box made of self-extinguishing polycarbonate (UL94-V0) for the snap-in fixing and removal, with openings for fixing by the means of
screws that enable corrections of possible lacks of the box in the opening; - closing and final processing of the box with elements that guarantee next level of protection: at least IP21
(if not precisely set) with covering plates as selected by the Supervision, fixed under pressure with screws by the means of a device; IP55, with lids that have transparent elastic wrapping made of silica rubber or similar, resistant to moist and
water jets, which would enable functioning of command devices, guaranteeing the protection degree with the closed lid; IP67, with non-removable lid with elastic membrane made of elastomer resistant to atmospheric agents
(storms, heat, sunlight, low temperatures, and so on), to saline and/or acidic environments, alkalis, mineral and vegetable oils, animal fats and oils, fuels, and to be fire-resistant, fixed to the socket box with stainless steel screws
of the possible switchbox. In case that the command with light signalisation must be connected to the source of light, addition to the price will be calculated. In case that the dimming command must be applied to
the source of light, addition to price will be calculated for the command with the mentioned characteristics. The price must include interior wiring between the sockets.
The typology of wiring cables must be the one envisaged in specifications. The used materials must have characteristics listed in suitable chapter of this study. CONTROL SWITCH Control switch that make
a part of quota for the switchbox installed on the voltage post; the lines going from the switchbox to the socket box; socket boxes to be installed in the wall, depending on the type, if necessary, with joints for cables; - control modular switch with the following characteristics;
CIRCUIT BREAKERS, SWITCHES AND BUTTONS Compliance with norms CEI 23-9 and further variances, voltage and nominal frequency 250V , 50Hz. Current 10A for buttons and 16A for switches; trial voltage 2000V at 50Hz per 1min; breaking power:
200 openings and closings at 1.25 In, 275V, power factor 0.3; functioning test 50000 per In, 250 V, power factor 0.6; insulation resistance >15Mohm at 500V; - signal light for identification
(if required); LIGHT INTENSITY REGULATORS (DIMMERS) Voltage and nominal frequency 230V +/- 10%; controlled power 60-500W (for resistant loads), insulation resistance >15Mohm at 500V; regulation via rotation command or
a double-function button; extended button pressure to regulate increase or decrease, with electronic memorising upon the release of the button, short pressure for on and off function on the light with
the selected lighting value; protection switch; frame for the terminal box made of self-extinguishing polycarbonate (UL94-V0) for the snap-in fixing and removal, with openings for fixing by the means of
screws that enable corrections of possible lacks of the box in the opening; - closing and final processing of the box with elements that guarantee next level of protection: at least IP21
(if not precisely set) with covering plates as selected by the Supervision, fixed under pressure with screws by the means of a device; IP55, with lids that have transparent elastic wrapping made of silica rubber or similar, resistant to moist and
water jets, which would enable functioning of command devices, guaranteeing the protection degree with the closed lid; IP67, with non-removable lid with elastic membrane made of elastomer resistant to atmospheric agents
(storms, heat, sunlight, low temperatures, and so on), to saline and/or acidic environments, alkalis, mineral and vegetable oils, animal fats and oils, fuels, and to be fire-resistant, fixed to the socket box with stainless steel screws
of the possible switchbox. In case that the command with light signalisation must be connected to the source of light, addition to the price will be calculated. In case that the dimming command must be applied to
the source of light, addition to price will be calculated for the command with the mentioned characteristics. The price must include interior wiring between the sockets.
The typology of cables for wiring must be the one envisaged in specifications and tables. The used materials must be
of characteristics listed in the appropriate chapter of this study.
| LANDSCAPING - LIGHTING |  | 1
| Total |  | 1
M20.A30.A1 |  | n
SAFETY TRIGGER WITH THE PROTECTED ACCESS The trigger with the protected access composed of: a part of the quota for the installed switchbox (if necessary); - the lines going from
the safety trigger to the switch coil installed on the main and/or local command table; galvanised tin box painted in yellow, with the lid with lock, neoprene seals,
with a locking option, hammer for glass breaking with the chain. Breakable glass, synthetic one, safety one, with trigger 6A/380V; table with instructions written in screen print, and formulated in the way selected by the Supervision.
| LANDSCAPING - NN DISTRIBUTION |  | 2
| Total |  | 2
M30.A10.B8 |  | n
SUPPLY SOURCE Supply source for various use composed of: - part of the quota for the switchbox installed on the voltage post; lines going from the switchbox
to the spot for use (separately calculated); - possible switchboxes and socket boxes (termina boxes). The type of wiring cables must be the one envisaged in specifications, and will be dimensioned based on the effective power
used by the devices (door/awning with the motor, switchboxes and so on). In case of use of the existing, or specifically envisaged main, only the price for wiring will be applied. In case of the procurement and installation only of
lines and boxes, the price for preparation will only apply. The used materials must be of characteristics stated in the suitable chapter of the subject study.
Visible wall installation power supply with PVC rigid pipe and 3x4 cable, IP44
| LANDSCAPING - NN DISTRIBUTION |  | 5
| Total |  | 5
TOTAL FOR ENERGY DISTRIBUTION AND POINTS OF SUPPLY
09 - EARTHING AND PROTECTION AGAINST ATMOSPHERIC DISCHARGES
O10.A21.A4 |  | n
EARTHING ROD Compliance with norms: CEI 11-8(89) and further variances. Characteristics of make: body with four arms made of steel protected by hot-dip galvanization, plate on the side with the terminal
For the connection of round or flat conductors; - minimal dimensions 50x50x5 mm.
Inox steel ground pillar D=20mm, L=3m
| LANDSCAPING - EARTHING AND LIGHTNING PROTECTION INSTALLATION |  | 7
| Total |  | 7
O10.A60.A1 |  | n
Copper rod of 200 mm2 minimal cross-section with rounded edges, with openings with coils for fixing the protective conductor and earthing conductor by the means of a fixing item, fixed to the manhole wall
of the earthing rod and fixed with two insulators.
| LANDSCAPING - EARTHING AND LIGHTNING PROTECTION INSTALLATION |  | 7
| Total |  | 7
O20.A10.A14 |  | m
COPPER WIRE Compliance with norms: CEI 7-1 and further adjustments and variances; UNI 5649/1. Conductor: wire obtained of copper fibres (7 for the diameter from 16 to 50 mm2, and 19 from 70 to 150 mm2 diameter, not less than 1.8 mm)
with smooth surface, cylindrical, made of raw or annealed copper of CU-ETP type with the percentage of Cu Ag 99.9%. Supplements: connectors of mechanical type (pressure or fixing
by the means of a nut and bolt) or by soldering, identification plate, possible holders and fixing material, dilatation or expansion joints.
Copper wire 50mm2
| LANDSCAPING - EARTHING AND LIGHTNING PROTECTION INSTALLATION |  | 125
| Total |  | 125
TOTAL FOR EARTHING AND PROTECTION AGAINST ATMOSPHERIC DISCHARGES
10 - LIGHTING DEVICES
P500.A10.A6 |  | lump
INSTALLATION OF LIGHTING DEVICES Works on the positioning and installation of lighting devices (excluded from the procurement), and they include installation of parts and all obligations fulfilled in order to have all installed devices completed and in function.
| LANDSCAPING - LIGHTING |  | 1
| Total |  | 1
TOTAL FOR LIGHTING DEVICES
D-2 | LANDSCAPING - ELECTRICAL INSTALLATIONS