## DWC
NOTE: UNIT PRICES TO BE ENTERED WITHOUT V.A.T.
B | WATER SUPPLY AND SEWERAGE
B-1 | water supply
NOTES:
If manufacturer name or material name is stated in individual positions, a bidder may incorporate the equipment and material of other manufacturers provided that such equipment and material have the same-equivalent or better characteristics corresponding to the project documents. All materials and elements that will be used during execution of works must be approved by the Investor.
All preparatory works, final cleaning of the structure, recess cutting, punching, drilling, patching of damaged surfaces etc. that are necessary for the execution of individual positions of works, as well as testing of incorporated material, installations and equipment, obtaining of required certificates, shall be neither calculated not paid separately. A bidder shall allocate costs for these works and cover them by unit prices of positions from the Bill of Quantities for works. For the execution of the stated work positions, all necessary building materials, means of work, formworks, scaffolding, external and internal transport, organization of the construction site, construction extensions, workforce, insurance etc. with elements and costs that are necessary for completion of individual works according to provided conditions, total finalization with a corresponding guaranty - all ready for technical acceptance - are implied.
CODE | DESCRIPTION | u.m. | QUANTITY | UNIT PRICE | TOTAL
01 | CENTRAL DEVICES
TA | THERMOSTATIC MIXER
TA.835.A7 | CENTRAL THERMOSTATIC MIXER | pcs
CENTRAL THERMOSTATIC MIXER in compliance with norms: UNI 9054 – UNI EN 1286 and 1287 Construction and mounting characteristics:
thermostatic mixer for making hot water for sanitary needs and for central installation on centralized installations, consisting of: - a body of highly chrome plated brass or bronze, with thread connections and shaped pieces or with flanges in compliances with norms - replaceable insert and plug of very resistant plastics, springs of INOX steel; - interior parts and gaskets of a material resistant to corrosion and formation of deposits; - expansion thermostat element; - exterior regulation system with an operating button with gradual reduction or increase. Where needed and/or emphasized: - accessible filters and control valves on the inlet. Technical characteristics: - maximum operating temperature: 85°C – maximum working pressure (static): 14 bars; maximum working pressure (dynamic):
5 bars; - precision: +/- 2°C. The price shall include: - accessories to completion; - possible holders and various fasteners; - water supply connection; - various expendables.
CENTRAL THERMOSTATIC MIXER, 2"
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TA.931.A1 | FLOOR DRAIN | pcs
FLOOR DRAIN In compliance with norms: UNI EN 274 Construction and mounting characteristics: a floor drain system made of highly-resistant plastic consisting of: - a wide head for collecting liquid from a number of lateral openings of dimensions 50 mm or 63 mm, with a brim and adjustable infeed hopper; - capping grate of stainless steel. The price shall include: - accessories to completion; - various holders and connectors; - connection to pipe drain.
Floor drain, 120x120 mm
| Central devices / water supply and sewerage |  | 5
| total |  | 5
TOTAL THERMOSTATIC MIXER
TB | PIPES
TB.120.A1 | GALVANIZED STEEL PIPES | kg
GALVANIZED STEEL PIPES In compliance with norms UNI EN 10255 medium series galvanized before treatment for diameters in inches or nominal diameter DN, up to 4’’ with bell-and-spigot joint; UNI EN 10216-1/TR1 galvanized after treatment for larger diameters, expressed in millimetres or in DN (minimum table thickness 5 as per the norm), with a flange joint; UNI EN 10240-A1 (for galvanization). Construction and mounting characteristics: - hot-dip galvanized steel pipes drawn without welding (for pipes UNI EN 10255 medium series, it is possible to also get welded pipes Fretz-Moon for the same price); bell-and-spigot joint with special parts, from flange (with galvanized screws) for commercial smooth pipes (UNI EN 10216-1/TR1). – the conventional weights of pipes of various diameters as well typology of use of pipes for various devices are defined by the norm, established in the Specification and/or other technical documents;
- as per bookkeeping needs, values of linear density will be used depending on the typology of pipes and applied diameter, as indicated in tables of the UNI EN norm. The price shall include: - as appropriate, for imbedded pipes: external coating of extruded polyethylene, with a layer on every joint; - scraps and write-offs; - special parts, accessories and possible fixing parts; - carriers, supports and clips; - various expendables.
GALVANIZED STEEL PIPES
| Central devices / water supply and sewerage |  | 400
| total |  | 400
TB.130.A1 | ELECTRIC WELDED STAINLESS STEEL PIPES | kg
ELECTRIC WELDED STAINLESS STEEL PIPES In compliance with norms: UNI EN ISO 1127 Construction and mounting characteristics: - austenitic stainless steel pipes type AISI 304 (ASTMTP304) and/or AISI 316 (ASTMTP316), welded and calibrated (removed external seem), white spheroidization, pickled. Seems are made by welding with electric arc with austenitic steel electrodes; when needed and/or emphasized, joints of parts with flanges on extremities are possible; – the conventional weights of pipes of various diameters, as well the typology of use of pipes for various devices are determined by the norm, established in the Specification and/or other technical documents. The price shall include: - scraps and write-offs; - special parts, accessories and possible fixing parts; - carriers, supports and cli+B43ps; - various expendables.
included: - scraps and write-offs; - special parts, accessories and possible fixing parts; - carriers, supports and clips; - various expendables.
| Central devices / water supply and sewerage |  | 452
| total |  | 452
TB.220.A3 | POLYETHYLENE RUN-OFF PIPES | m
POLYETHYLENE RUN-OFF PIPES In compliance with norms: UNI EN 1519-1:2001 series S16 (application zone 'B') for interior drains; UNI EN 12666:2006 for external imbedded drains. Construction and mounting characteristics: - high density polyethylene pipes, high dynamic strength, resistant to frost, to water up to 100 °C and to chemical aggressions, B54. Welded joints (polyfusion) and/or a cesspit, with O-ring flanges or with multiple plates as specified in the Specification. Where needed and/or emphasized, they are equipped with phono-insulation (separate description and price). The mounting typology is described in the Specification. The price shall include: - scraps and write-offs; - fittings, accessories and possible fixing parts; - carriers, supports and cli+B53ps; - various expendables.
Polyethylene pipe, diam. 50 mm
| Central devices / water supply and sewerage |  | 57
| total |  | 57
TB.220.A5 | POLYETHYLENE RUN-OFF PIPES | m
POLYETHYLENE RUN-OFF PIPES In compliance with norms: UNI EN 1519-1:2001 series S16 (application zone 'B') for interior drains; UNI EN 12666:2006 for buried drains. Construction and mounting characteristics: - high density polyethylene pipes, high dynamic strength, resistant to frost, to water up to 100 °C and to chemical aggressions, for waste water discharge not under pressure. Welded joints (polyfusion) and/or a cesspit, with O-ring flanges or with multiple plates as specified in the Specification. Where needed and/or emphasized, they are equipped with phono-insulation (separate description and price). The mounting typology is described in the Specification. The price shall include: - scraps and write-offs; - fittings, accessories and possible fixing parts; - carriers, supports and cli+B57ps; - various expendables.
POLYETHYLENE RUN-OFF PIPES, diam. 75 mm
| Central devices / water supply and sewerage |  | 75
| total |  | 75
TB.222.A6 | POLYETHYLENE PIPES OF HIGH HDPE DENSITY FOR FLUID UNDER PRESSURE | m
POLYETHYLENE PIPES OF HIGH HDPE DENSITY FOR FLUID UNDER PRESSURE In compliance with norms: UNI EN 12201-5:2004; UNI EN 1555:2004 (flammable gases). Construction and mounting characteristics: - high density PE pipes, high dynamic strength, resistant to frost, chemical aggressions etc., suitable for distribution of fluid under pressure, including alimetric fluids. Clip fittings to DN100; welded joints (polyfusion) for more DN. As needed and/or emphasized, pipes will be type: - PE80 or PE100, PN6, 3 (SDR26), PN10 (SDR17) or PN16 (SDR11); - PE80 (series S5 to outside diameter 75mm and series S8 for outside diameters above 75mm) in compliance with norms UNI EN 155:2004 for distribution of flammable gases. Mounting typology is described in the Specification. The price shall include: - scraps and write-offs; - fittings, accessories and possible fixing parts; - carriers, supports and clips; - various expendables.
POLYETHYLENE RUN-OFF PIPES PN10, PeHD, diam.63
| Central devices / water supply and sewerage |  | 26
| total |  | 26
TOTAL PIPES
TC | VALVES FOR WATERSUPPLY SYSTEM
TC.110.A10 | BLEACHED BRASS THREADED BALL VALVE, PN16 | pcs
BLEACHED BRASS THREADED BALL VALVE, PN16 In compliance with norms: UNI EN 1074; UNI 8858 Construction and mounting characteristics: 2-way or 3-way valve (as needed and/or requested) with a brass body POT 58Pb, chromed or nickel-plated, with the ball of stainless steel inox AISI 304; full flow, with handle nut mounted on the inside of the body with double gasket (2 Viton O-rings and PTFE sealing ring), a handle with a bar or a fly made of plasticized metal (with axis bumper bearing, included in the price in case of insulated pipes) and thread connections; for hot or cold water, drinking water, fire protection installations and gas/air networks; - procurement in the version with hoses, male/female couplings or with Hollander couplings, as requested. Technical characteristics: - maximum temperature 110°C – working nominal pressure: PN16. The price shall include: - fittings, accessories; - various expendables.
BALL VALVE, diam. 3"
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TC.110.A5 | BLEACHED BRASS BALL VALVE WITH THREADS, PN16 | pcs
BLEACHED BRASS THREADED BALL VALVE, PN16 In compliance with norms: UNI EN 1074; UNI 8858 Construction and mounting characteristics: 2-way or 3-way valve (as needed and/or requested) with a brass body POT 58Pb, chromed or nickel-plated, with the ball of stainless steel inox AISI 304; full flow, with handle nut mounted on the inside of the body with double gasket (2 Viton O-rings and PTFE sealing ring), a handle with a bar or a fly made of plasticized metal (with axis bumper bearing, included in the price in case of insulated pipes) and thread connections; for hot or cold water, drinking water, fire protection installations and gas/air networks; - procurement in the version with hoses, male/female couplings or with Hollander couplings, as requested. Technical characteristics: - maximum temperature 110°C – working nominal pressure: PN16. The price shall include: - fittings, accessories; - various expendables.
BALL VALVE, diam. 1"
| Central devices / water supply and sewerage |  | 13
| total |  | 13
TC.110.A7 | BLEACHED BRASS THREADED BALL VALVE, PN16 | pcs
BLEACHED BRASS THREADED BALL VALVE, PN16 In compliance with norms: UNI EN 1074; UNI 8858 Construction and mounting characteristics: 2-way or 3-way valve (as needed and/or requested) with a brass body POT 58Pb, chromed or nickel-plated, with the ball of stainless steel inox AISI 304; full flow, with handle nut mounted on the inside of the body with double gasket (2 Viton O-rings and PTFE sealing ring), a handle with a bar or a fly made of plasticized metal (with axis bumper bearing, included in the price in case of insulated pipes) and thread connections; for hot or cold water, drinking water, fire protection installations and gas/air networks; - procurement in the version with hoses, male/female couplings or with Hollander couplings, as requested. Technical characteristics: - maximum temperature 110°C – working nominal pressure: PN16. The price shall include: - fittings, accessories; - various expendables.
BALL VALVE, diam. 1"1/2
| Central devices / water supply and sewerage |  | 9
| total |  | 9
TC.110.A8 | BLEACHED BRASS THREADED BALL VALVE, PN16 | pcs
BLEACHED BRASS THREADED BALL VALVE, PN16 In compliance with norms: UNI EN 1074; UNI 8858 Construction and mounting characteristics: 2-way or 3-way valve (as needed and/or requested) with a brass body POT 58Pb, chromed or nickel-plated, with the ball of stainless steel inox AISI 304; full flow, with handle nut mounted on the inside of the body with double gasket (2 Viton O-rings and PTFE sealing ring), a handle with a bar or a fly made of plasticized metal (with axis bumper bearing, included in the price in case of insulated pipes) and thread connections; for hot or cold water, drinking water, fire protection installations and gas/air networks; - procurement in the version with hoses, male/female couplings or with Hollander couplings, as requested. Technical characteristics: - maximum temperature 110°C – working nominal pressure: PN16. The price shall include: - fittings, accessories; - various expendables.
BALL VALVE, diam. 2"
| Central devices / water supply and sewerage |  | 19
| total |  | 19
TC.110.A9 | BLEACHED BRASS THREADED BALL VALVE, PN16 | pcs
BLEACHED BRASS THREADED BALL VALVE, PN16 In compliance with norms: UNI EN 1074; UNI 8858 Construction and mounting characteristics: 2-way or 3-way valve (as needed and/or requested) with a brass body POT 58Pb, chromed or nickel-plated, with the ball of stainless steel inox AISI 304; full flow, with handle nut mounted on the inside of the body with double gasket (2 Viton O-rings and PTFE sealing ring), a handle with a bar or a fly made of plasticized metal (with axis bumper bearing, included in the price in case of insulated pipes) and thread connections; for hot or cold water, drinking water, fire protection installations and gas/air networks; - procurement in the version with hoses, male/female couplings or with Hollander couplings, as requested. Technical characteristics: - maximum temperature 110°C – working nominal pressure: PN16. The price shall include: - fittings, accessories; - various expendables.
BALL VALVE, diam. 2"1/2
| Central devices / water supply and sewerage |  | 8
| total |  | 8
TC.120.A11 | CAST IRON VALVE WITH A RUBBER WEDGE, PN 16 | pcs
CAST IRON VALVE WITH A RUBBER WEDGE, PN 16 In conformity with norms: UNI 7125/72 Construction and mounting characteristics: narrowed valve without maintenance type BOA compact, with: - GG2 cast iron body and cover, mono block; - stainless steel bar highly resistant to high temperatures with double O-ring; - soft sealing wedge with EPDM rubber flanges; - steering wheel of synthetic material fastened by cast iron for fast closing; - indicator of the openness extent (elevated); flange joints as per norms; - internal and external painting by a double layer of atoxic plastic enamel suitable for drinking waters. As needed and/or requested: - the valve will be wafer type with the same number of through holes for centring the number of holes of joint flanges on pipes and will be mounted so as to allow dismantling of the pipeline after initial mounting;
Valve for stopping fluids in hydrothermal installations, gas installations and cooling systems. Technical characteristics: - temperature limit: 120°C – nominal working pressure: 16 bars.
The price shall include: - accessories, opposite flanges; - various expendables.
CAST IRON VALVE WITH A RUBBER WEDGE, DN 100
| Central devices / Fire protection |  | 1
| total |  | 1
TC.130.A10 | CAST IRON BUTTERFLY VALVE BETWEEN FLANGES, PN16 | pcs
CAST IRON BUTTERFLY VALVE BETWEEN FLANGES, PN16 Construction and mounting characteristics: butterfly valve with spheroid GG40 cast iron housing, interior coated with EPDM rubber and pre-formed holding rings with: - threaded through holes for fixing with screws, of the same number as joint flanges holes on pipes or through centering holes (wafer type) for fixing with clips and screws; mounted so as to, when the valve is closed, allow dismantling of pipes and/or the stop section prior or after the initial mounting; - axis and plug disc with lense of inox steel or spheroid cast iron GG40, coated with material that prevents transmission of vibration; - handle of hard resistant material with appropriate opennings for installation of a lock with a key and safety code that is included in the price in case of butterflz valve for fire protection devices; - a system for blocking and/or pre-determined placing into the right position (for diameters larger than DN200 with a light steering wheel and a reducer).
In case of the use for drinking water intended for humans, the valve will be treated by a special inside epoxy treatment certified by norms in force. In case of the use for fire extinguishers, all locks will have the same keys. In case of the use for flammable gases, the buterfly valve will be as previously described, except for joints that will be implemented with nitrile rivets.
Technical characteristics: - maximum working temperature: 120°C – nominal working pressure: 16 bars. The price shall include: - accessories, opposite flanges and screws; - various expendables.
Butterfly valve, DN80
| Central devices / water supply and sewerage |  | 13
| total |  | 13
TC.130.A9 | CAST IRON BUTTERFLY VALVE BETWEEN FLANGES, PN16 | pcs
CAST IRON BUTTERFLY VALVE BETWEEN FLANGES, PN16 Construction and mounting characteristics: butterfly valve with spheroid cast iron housing GG40, interior coated with EPDM rubber and pre-formed holding rings with: - threaded through holes for fixing with screws, of the same number as the joint flanges holes on pipes, or through holes for centering (wafer type) for fixing with clips and screws; mounted so as to, when the valve is closed, allow dismantling of pipes and/or stop section prior or after the initial mounting; - axis and stop disc with lense of inox steel or spheroid cast iron GG40, coated with material that prevents transmission of vibrations; - handle of hard resistant material with appropriate opennings for installation of a lock with a key and safety mark that is included in the price in case of butterfly valve for fire protection devices; - a system for blocking and/or pre-determined placing into the right position (for diameters larger than DN200 with a light steering wheel and a reducer).
In case of the use for drinking water intended for humans, the valve shall be treated by a special internal epoxy treatment as certified by norms in force. In case of the use for fire protection devices, all locks shall have the same keys. In case of the use for flammable gases, the buterfly valve shall be as previously described, except for joints that will be implemented by nitrile plugs. Technical characteristics: - maximum working temperature: 120°C – nominal working pressure: 16 bars. The price shall include: - accessories, opposite flanges and screws; - various expendables.
Butterfly valve, DN65
| Central devices / water supply and sewerage |  | 6
| total |  | 6
TC.210.A7 | BRONZE BALANCING AND REGULATION VALVE, THREADED, PN 16 | pcs
BRONZE BALANCING AND REGULATION VALVE, THREADED, PN 16 Construction and mounting characteristics: balancing and regulation valve consisting of a bronze body, a cover of brass alloy and a bronze stop crossbar; with inclined seat, threaded, with a wheel for reading and blocking regulation positions and piezometric disconnection joints. Intended for devices for heating, cooling and distribution of hot/cold sanitary water. Technical characteristics: - working temperature: -20 +120 °C; nominal working pressure: PN 16. The price shall include: -accessories; various expendables.
Balancing valve, 1"1/2
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TC.320.A5 | CHECK VALVE WITH BRASS DISC, THREADED, PN16 | kom.
CHECK VALVE WITH BRASS DISC, THREADED, PN16 Construction and mounting characteristics: check valve with a brass body, stop disc of austenite steel or INOX steel with INOX steel spring and threaded in conformity with norms; intended for all types of hydraulic, pneumatic and heating installations, etc. Technical characteristics: - maximum working temperature: - 200°C; nominal working pressure: 16 bars. The price shall include: - accessories; - various expendables.
Check valve, 1"
| Central devices / water supply and sewerage |  | 5
| total |  | 5
TC.320.A8 | CHECK VALVE WITH BRASS DISC, THREADED, PN16 | pcs
CHECK VALVE WITH BRASS DISC, THREADED, PN16 Construction and mounting characteristics: check valve with a brass body, stop disc of austenite steel or INOX steel with INOX steel spring and threaded in conformity with norms; intended for all types of hydraulic, pneumatic and heating installations, etc. Technical characteristics: - maximum working temperature: - 200°C; nominal working pressure: 16 bars. The price shall include: - accessories; - various expendables.
Check valve, 2"
| Central devices / water supply and sewerage |  | 3
| total |  | 3
TC.321.A10 | CHECK VALVE WITH A BRASS DISC/CAST IRON DISC, EXTRA FLAT (BETWEEN FLANGES), PN16 | pcs
CHECK VALVE WITH A BRASS DISC/CAST IRON DISC, EXTRA FLAT (BETWEEN FLANGES), PN16 Construction and mounting characteristics: check valve with a bronze/brass body for diameters to DN100 and of cast iron for larger diameters, a stop disc of austenite steel or inox steel with inox spring, or a cast iron stop for diameters larger than DN100; extra flat execution for fixing between flanges (wafer) with a centering ring; usually intended for all types of hydraulic installations: for fluids, gas, steam etc. Technical characteristics: maximum working temperature: 200°C – nominal working pressure: 16 bars. The price shall include: - accessories, opposite flanges and screws; - various expendables.
Check valve, DN80
| Central devices / water supply and sewerage |  | 4
| total |  | 4
TC.410.A4 | STANDARD WATER MEMBRANE SAFETY VALVE | pcs
STANDARD WATER MEMBRANE SAFETY VALVE In conformity with norms: I.S.P.E.S.L. Construction and mounting characteristics: Safety valve with a brass body and seat, with a membrane of synthetic material and a contrast spring of inox steel; fixed calibrated valve, stanradized and with qualification certificate I.S.P.E.S.L., with manual steering and denticulated steering wheel with an option for removal of the cover without conditioning calibration values. Technical characteristics: - maximum working temperature: 110°C. The price shall include: - accessories; - various expendables.
Safety valve, diam. 3/4" x 1"
| Central devices / water supply and sewerage |  | 2
| total |  | 2
TC.610.A8 | BRONZE ’Y’ FILTER FOR COLLECTING DIRT, THREADED, PN10 | pcs
BRONZE ’Y’ FILTER FOR COLLECTING DIRT, THREADED, PN10 Technical and mounting characteristics: inclined ’Y’ filter with a bronze body, bronze and cast brass cover and filtering dismountable cylyndric basket of inox steel; for hydrothermal installations. Technical characteristics: - maximum fluid temperature: - 80°C – nominal working pressure: 10 bars. The price shall include: - accessories; - various expendables.
Y filter, 2"
| Central devices / water supply and sewerage |  | 2
| total |  | 2
TOTAL VALVES
TE | REGULATING WATER SYSTEM
TE.146.A1 | Regulation servo-driven valve for terminal units, made of broze, with helixes, PN 16 | pcs
Regulation servo-driven valve for terminal units, made of broze, with helixes, PN 16 Construction and mounting characteristics: Regulation servo-driven valve for terminal units, with two or three arms, consisting of: a bronze body with threaded connections in conformity with norms and a by- pass for valves with three arms (at the same price mounted by the installer); - seat, axis, piston, of inox steel, electro mechanical command actuators (servo engine) with three arms or modular, supply voltage 24 V - 50 Hz, consisting of: eelctrican engine contained in a protected solid plastics or metal box with a protection degree above IP54, manual steering handle, valve connection elements, where required returning spring to the initial position (N.C or N. A.) Characteristics of the servo commans must still be in conformity with diameter or operational characteristics of the valve (differential pressure).
Valve functioning characteristics: fluid temperature: from 2 to 110 °C; - working pressure: 16 bars. The price shall include: - special accessories; - hydro and electrical connections; - various expendables.
Regulation servo-driven valve for terminal units
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TE.700.A1 | ELECTRICAL INSTALLATION WITH CONDUIT BOX AND CONNECTIONS FOR ALL DEVICES | pcs
Construction and mounting characteristics: - conduit box for thermo-mechanical devices, implemented and completed in conformity with requirements and specifications in technical documents and the Specification, together with a connection to the distribution supply network;
- connecting conduit box with all devices, including conducting pipe, pipes, power lines and the entire small material required for completing mounting and for proper functioning of the installation;
- switches - safety disconnectors - stop switches for all devices; - connecting all devices to corresponding lines of the conduit box. Methods of application are described in the Specification.
ELECTRICAL INSTALLATION WITH CONDUIT BOX AND CONNECTIONS FOR ALL DEVICES
| Central devices / Fire protection |  | 1
| total |  | 1
TE.700.A2 | ELECTRICAL INSTALLATION WITH CONDUIT BOX AND CONNECTIONS FOR ALL DEVICES | pcs
Construction and mounting characteristics: - conduit box for thermo-mechanical devices, implemented and completed in conformity with requirements and specifications in technical documents and the Specification of the project, together with a connection to the distribution supply network;
- connecting conduit box with all devices, including conducting pipe, pipes, power lines and the entire small material required for completing mounting and for proper functioning of the installation;
- switches - safety disconnectors - stop switches for all devices; - connecting all devices to corresponding lines of the conduit box. Methods of application are described in the Specification.
ELECTRICAL INSTALLATION WITH CONDUIT BOX AND CONNECTIONS FOR ALL DEVICES
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TE.700.A4 | ELECTRICAL INSTALLATION WITH CONDUIT BOX AND CONNECTIONS FOR ALL DEVICES | pcs
Construction and mounting characteristics: - conduit box for thermo-mechanical devices, implemented and completed in conformity with requirements and specifications in technical documents and the Specification of the project, together with a connection to the distribution supply network;
- connecting conduit box with all devices, including conducting pipe, pipes, power lines and the entire small material required for completing mounting and for proper functioning of the installation;
- switches - safety disconnectors - stop switches for all devices; - connecting all devices to corresponding lines of the conduit box. Methods of application are described in the Specification.
ELECTRICAL INSTALLATION WITH CONDUIT BOX AND CONNECTIONS FOR ALL DEVICES, EB_GS
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TE.710.A1 | DDC MONITORING SYSTEM | pcs
BMS regulation-automation system by Direct Digital Control (DDC), without central monitoring unit (workstation) – peripheral substation DDC... .... In conformity with the specification and other studies of the project, and implies necessarily:
- peripheral substation DDC…with appropriate frame (i.e. contained within power box Q:E…=
Consists of CPU units, supply modules, input-output module, access terminal
- servo-driven valves or servo steering wheel for iron blinds, where envisaged, given that they are separately calculated;
- share of the quota of connection bus lines with other peripheral; - engineering, start-up;
- instructions for personnel with respect to everything that is required to bring the system to flawless functioning
HVAC control system, DDC1 (EB_FP)
| Central devices / Fire protection |  | 1
| total |  | 1
TE.710.A2 | DDC MONITORING SYSTEM | pcs
BMS regulation-automation system by Direct Digital Control (DDC), without central monitoring unit (workstation) – periferična podcentrala DDC... .... In conformity with the specification and other studies of the project, and implies necessarily:
- peripheral substation DDC…with appropriate frame (i.e. contained within the power box Q:E…=
Consists of CPU units, supply modules, input-output module, access terminal
- connection lines leading from the substation to all elements in the field or the network - elements in the field on in the network such as probes, sensors, relays, transmitters etc. except servo-driven valves or servo steering wheels for iron blinds, where envisaged, given that they are calculated separately;
a share of the quota of connection bus lines with other peripheral; - engineering, start-up;
- instructions for personnel concerning everything that is required to bring the system to flawless functioning.
HVAC control sytem, DDC2 (EB_DW)
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TE.710.A4 | DDC MONITORING SYSTEM | pcs
BMS regulation-automation system by Direct Digital Control (DDC), without central monitoring unit (workstation) – peripheral substation DDC... .... In conformity with the specification and other studies of the project, and implies necessarily:
- peripheral substation DDC…with appropriate frame (i.e. contained within the power box Q:E…=
Consisting of CPU units, supply module, input-output module, access terminal
- connection lines leading from the substation to all elements in the field or network '- elements in the field or in the network such as probes, sensors, relays, transmitters etc. except servo-driven valves or servo steering wheel for iron blinds, where envisaged, given that they are calculated separately;
a share of quota of connection bus lines with other peripheral; - engineering, start-up;
- instructions for personnel with respect to everything that is needed to bring the system to flawless functioning
HVAC control system, DDC4 (EB_GS)
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TE.710.A5 | DDC MONITORING SYSTEM | pcs
BMS regulation-automation system by Direct Digital Control (DDC), without central monitoring unit (workstation) – peripheral substation DDC... .... In conformity with the specification and other studies of the project, and implies necessarily:
- peripheral substation DDC…with appropriate frame (i.e. contained within the power box Q:E…=
Consists of CPU units, supply modules, input-output modules, access terminal
- connection lines leading from the substation to all elements in the field or the network '- elements in the field or in the network such as probes, sensors, relays, transmitters etc. except servo-driven valves or servo steering wheels for iron blinds, where envisaged, given that they are calculated separately;
a share of quota of connection bus lines with other peripheral; - engineering, start-up;
- instructions for personnel with respect everything that is needed to bring the system to flawless functioning
HVAC control system, DDC5 (EB_WW1 EB_WW2)
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TE.730.A1 | BASIN REGULATING STATION Electronic station with a micro processor for timed titration type “Cillichemie or equivalent mode. -Allsil Super 25 Ag and Cillit- Atopool 30" consisting of: a control panel which has an electronic station with a transformer, reaction chamber with optoelectronic or colorimetric sensor, magnetic eelctro starter and a dsicharge siphon, two peristaltic pumps for dosing reagents A and B, stop electro valve and accessories to completion. | pcs
Main characteristics:
- display with back light;
4 lines – 20 characters, min and max set value;
automatic calibration,
operating dosing pumps PFM e PWM dosing time
- sign 0/4÷20 or 20÷0/4 Ma
- level of reagents
- number of completed analyses; manual analyses management
- PT 100 temperature probe preventing exceeding of threshold
- remote alarms; - adjustable temperature alarms
- programming languages: I, GB, D, E, F.
Technical data:
Field of detection: 0 ÷ 100 ppm Allsil Super 25 Ag
Field of detection: 0 ÷ 100 ppm Atopool 30
Temperature of the fluid that is tested: 5 ÷ 55 °C
Working pressure min/max: 1 ÷ 4 bar
Analysis interval min/max: 15 min c. / <100 h
Volume of water for analysis: 500 cc
Flow capacity: max: 50 l/h
Analysis of reagents' autonomy: 750 c. (40 ppm Allsil)
BASIN REGULATING STATION
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TOTAL WATER REGULATING SYSTEM
TF | HEAT GENERATING DEVICES
TF.710.A6 | Single-piped chimney of INOX steel, with double walls | m
Single-piped schimney of inox steel, with double walls In conformity with norms: UNI 7129:2008 for gas devices type "B" or "C"; UNI 11071:2003 for devices that serve for condensation and similar devices; UNI 10641:1997 only for gas devices type “C” with a fan in the combustion circuit; L. 615/66 - D.P.R. 1391/70 (fluids-solid matters combination for voltage for a single devices exceeding 35 kW); UNI EN 1443:2005 (general classifications); UNI EN 13384-1:2008 (methods of calculation for the chimney envisaged for multiple devices) Construction and mounting characteristics: vertical pipeline for collecting and discharging combustion products resulting from the heat generating apparatus, natural ventilation type (the chimney base is in an indendation) adjusted both for the liquid fuel furnace and those with gas fuel.
In specific cases, it will be manufactured in conformity with the above norms and consist of: - main part for collecting and discharging condensation, manufactured of austentic inox steel 316L; - collection chamber of inox steel, with double walls, insulated, as well as linear elements and equipped with impermeable inspection hole of inox steel;
bearing shaft plate of inox steel. A set of elements envisaged to form exhaust pipes consisting of double walls of inox steel, inside pipes of austentic inox steel AISI 316L, discharge channel not smaller than 0.4 mm and with a longitudinal seem, a sprazer not smalled than 0.5 mm (or copper with outside finalization when needed or specified) with insulating layer of minimum density of 1000 kg/m (glass wool or mineral wool), circular cross-section, and equipped with joints (connectors) male-female connectors mounted with the use of a suitable ring for connecting pipes and screws of inox steel to be provided by the same manufacturer; all parts are highly resistant to high temperatures of smoke, acids, guarantee perfect durability of the product to combustion, impermeability of fireplace to condensation, thermal dilatations and mechanical stability. - connecting to
smoke channel coming out of the heat generator – with a connection to 135°; chimney top with a cover; - inspection hole of inox steel with holes, located in the base and on the end section of the drain (at easily accessible position) for relieving pressure and inside temperature; for gas furnace; '- for solid-liquid fuel furnaces; pressure-temperature meter on the base and on top; a metal plate with holes and plugs on the base and (for furnace above 580 kW) on top, all must be at pre-determined distances. The overall system will be designed, implemented and maintained in conformity with the above norms, with specific reference to L. 46/90 and L. 10/91 and D.P.R. 412/93 - 551/99 in particular cases;
Technical characteristics: thermal resistance: >= di 0,22 mq K/W; insulator thickness (minimum): * 25 mm for diameters to DN 400; * 35 for larger diameters; folding of interior walls r < = 1 mm. The price shall include: accessories and special parts; - holders and supports; - various expendables; dimensioning and calculations, chimney fully presented in graphic documents, material certification (heat, corrosion resistance etc.); in conformity with the Law L. 46/90 and designation of the product with CE mark as per (EN 1856-1).
A single-pipe fireplace of INOX steel, with double walls 200 mm diameter
| Central devices / Fire protection |  | 25
| total |  | 25
TOTAL HOT WATER GENERATING DEVICES
TH | INSULATION FOR HEATING BODIES
TH.710.A1 | SYSTEM WITH SELF-REGULATING HEATING CABLE | m
SYSTEM WITH SELF-REGULATING HEATING CABLE In conformity with norms: Approvals: BS; OVE; DIN VDE; DVGW. Construction and mounting characteristics: a system for temperature maintenance and/or frost protection for transient fluids contained in pipes, reservoirs, drains etc. or for avoiding creating of ice on street inclinations, squares, staircases etc., implemented by heating cable consisting of: - appropriate electrical copper sheet conductors depending on the required application on the cable; - heating self-regulating core (inside expanding or narrowing layer), of polymer mixed with graphite particles; - insulating poliolefine or fluoropolymer coating; - durable copper sheet cover for mechanical protection and proper laying of the cable; - outside coating of poliolefine, fluoropolymer or similar material, resistant to UV rays, suitable thickness for the function of required installation; - a box or a connection set for power supply of the cable, of resistant plastics, protection level minimum IP66;
- a set, extensions and/or cable receptacle for linear connections and connecting multiple cables, provided by the same manufacturer as for the cable. Where specifically emphasized and/or requested: - temperature control equipment suitable for installation on the distribution box, including temperature sensors and with a display for direct reading of main parameters (temperature, heating on etc.), relay outlet for indicating failures and remote alarm. Methods of application are described in the Specification. Technical characteristics: - power supply of the heating cable: around 230°C (+/- 10%) – frequency: 50Hz. The price shall include: - special parts; - connnection strip resistant to high temperatures and UV radiation, for fixing and perfect adhesion of the heating cable to the element to be protected; - holders and connectors; - electrical connection; - various expendables
SYSTEM WITH SELF-REGULATING HEATING CABLE
| Central devices / water supply and sewerage |  | 8
| total |  | 8
TH.710.Z1 | SYSTEM WITH SELF-REGULATING HEATING CABLE | Lump sum
SYSTEM WITH SELF-REGULATING HEATING CABLE In conformity with norms: Approvals: BS; OVE; DIN VDE; DVGW. Construction and mounting characteristics: a system for maintaining temperature and/or frost protection of transient fluids contained in pipes, reservoirs, drains etc. or for avoiding creation of ice on street inclinations, squares, staircases etc., implemented by heating cable consisting of: - appropriate electrical copper sheet conductors depending on the required application on the cable; - heating self-regulating core (inside expanding or narrowing layer), of polymer mixed with graphite particles; - insulating poliolefine or fluoropolymer coating; - durable copper sheet cover for mechanical protection and proper laying of the cable; - outside coating of poliolefine, fluoropolymer or similar material resistant to UV rays, suitable thickness for the function of required installation; - a box or connection set for power supply of the cable, made of resistant plastics, protection level minimum IP66;
- a set, extensions and/or cable receptacle for linear connections and connecting multiple cables, provided by the same manufacturer as for the cable. Where specifically emphasized and/or requested: - temperature control equipment suitable for installation on the distribution box, including temperature sensors and with a display for direct reading of main parameters (temperature, heating on etc.), relay outlet for indicating failures and remote alarm. Methods of application are described in the Specification. Technical characteristics: - heating cable power supply: around 230°C (+/- 10%) – frequency: 50Hz. The price shall include: - special parts; - connected strip resistant to high temperatures and UV radiation, for fixing and perfect adhesion of the heating cable to the element to be protected; - holders and connections; - electrical connections; - various expendables
SYSTEM WITH SELF-REGULATING HEATING CABLE
| Central devices / water supply and sewerage |  | 1
| total |  | 1
INSULATION FOR HEATING BODIES
TL | FIRE PROTECTION DEVICES
TL.210.A2 | MANUAL POWDER FIRE EXTINGUISHER | pcs
MANUAL POWDER FIRE EXTINGUISHER In conformity with norms: D.M. 20/12/1982 (and subsequent changes); D.L. n.93 25/02/2000 (act Dir. 97/23/CE) Construction and mounting characteristics: mobile fire extinguisher with a welded steel tank filled with fire extinguishing agent (powder) which can be directed towards fire due to inside pressure, manufactured as per norms D.M. 20/12/1982 and designed so that it can be carries and used manually, mass maximum 20 kg. Polyvalent and atoxic type, for fires type A, B and C, nitrogen-pressurized and completed with: - uncrewing valves with a bar or a trigger; - a safety system against accidental manouvers; - control gauge (zero position, green safe use position, two red zones outside the green zone); - pipe and nozzle (for the capacity exceeding 3 kg or 3 l);
- suitable holder for hanging on the wall; - varnishing the fire extinguisher body red RAL 3000; - easy-to-read identification marks, as per instructions D.M. 20/12/1982, on the extinguisher. Technical characteristics: - calibration pressure minimum 1 ¼ of the pressure developed on the inside of the extinguisher at the temperature of 60 °C and in any case not exceeding 2,4 MPa. – working pressure between -20 and +60°C; - filling depending of various types offered. The price shall include: - wall two-sided sign in conformity with norms of the Law No. 493 14/08/1996, indicative dimensions 25x25 cm; - possible accessories; - various expendables.
Manual fire extinguisher, 34A-233BC, 6 kg
| Central devices / Fire protection |  | 4
| total |  | 4
TL.211.A2 | MOBILE FIRE EXTINGUISHER CO2 | pcs
MOBILE FIRE EXTINGUISHER CO2 In compliance with norms: D.M. 20/12/1982 (and subsequent amendments); D.L. n.93 25702/2000 (act Dir 97/23/CE) Construction and mounting characteristics: mobile fire extinguisher with a welded steel tank filled with fire extinguishing agent (CO2) which can be directed towards fire due to inside pressure, manufactured as per norms D.M. 20/12/1982 and designed so that it can be carried and used manually, mass maximum 20kg. Polyvalent and atoxic type for fires type B and C, nitrogen-pressurized and completed with: - unscrewing valves with a bar or a trigger; - safety system against accidental manouvers; - control gauge (zero position, green safe use position, two red zones outside the green zone); - a pipe with a nozzle and safety handle (for capacities above 3 kg or 3l);
- pipe with a spray and a safety handle (for capacities above 3 kg or 3l); - suitable holder for hanging on the wall; - varnishing the fire extinguisher body red with grey end section; - easy-to-read identification marks on the extinguisher as per instructions D.M. 20/12/1982. Technical characteristics: - cylinder ISPESL with pressure of 250bars; - calibration pressure between 17 and 20 MPa; – working pressure between -20 and +60°C; - filled depending on various types offered. The price shall include: - two-sided wall sign in conformity with norms of the Law No. 493 14/08/1996, indicative dimensions 25x25 cm; - possible accessories; - various expendables.
Manual fire extinguisher, CO2 113BBC, 5 kg
| Central devices / Fire protection |  | 3
| total |  | 3
TL.715.B2 | FIRE PUMPING SYSTEM IN COMPLIANCE WITH THE NORM UNI EN 12845 WITH AN ELECTRO PUMP/ELECTRO PUMPS, MOTO-PUMP AND SPARE ELECTRO PUMP | pcs
FIRE PUMPING SYSTEM IN COMPLIANCE WITH THE NORM UNI EN 12845 WITH AN ELECTRO PUMP/ELECTRO PUMPS, MOTO-PUMP AND SPARE ELECTRO PUMP In conformity with norms: UNI EN 12845 Construction and mounting characteristics: a fire pumping system with one or more (depending of the need and/or requirement) main electro pumps, with Diesel moto-pump and a spare electro pump consisting of: - one or more (depending on the need and/or request) main centrifugal electro pumps of normalized type (DIN 24255), horizontal axis, connected (by a connection part) with electric three-phase rotating engine of 2.900 turns/minute. The engine will have a protection level of minimum IP55. The pumo rotor and body will be of grey cast steel G25 (or higher quality) or of inox steel AISI 304 (or higher quality); axis will be of inox steel, and bearings will be without maintenance.
Features will be designated on regulatory table on the pump; - one moto pump, with the pump body and rotor as previously described, Diesel engine with direct injection and with 2900 turns/minute (with rotation regulator), cooled with direct air intake or by a cooler with propelers or by feeding water from hydric tank; a silencer and pipes for collecting exhaust gases outside the place; - water or oil pre-heating system; 12 or 24V alternator;
- electromagnet for stopping operation; a tank of varnished steel, with floor holder of the capacity to allow autonomous functioning for 6 house under full borden with a visible level indicator and a contact alarm for the lowest level, a vessel for collecting possible benzine drains, capacity at least equal to the tank, placed below the tank, a couple of driving batteries both of which are of 10 initiation turns of 10 seconds per battery, with electrical cables. Characteristics will be indicated on the regulation table on the motor pump. – one spare electro pumo of small reach and large head, mono block, multi-phase horizontal or vertical, with a rotor and body of cast iron G25 (or higher quality), with diffusers with propellers of structural steel, or inox steel AISI 304 (or higher quality); rotors of cast iron G25 or inox steel 304, on inox steel axis; motor of rotation of 2.900 turns in a minute, three-phase, with a protection level not below IP55.
Features will be designated on regulatory table on the pump. – galvanized steel collector of appropriate diameter; - one or more tanks with a membrane of total capacity of minimum 80 liters, of quality steel, treated by epoxy protection on the inside and the outside, or inox steel 304. Working pressure: PN10 (10bar). – stop valves on outlets and suctions of eevry pump (both main and standby), wafer typa butterfly (for tightening between flanges) of soft grip, cast steel PN 10-16 (or, for the standby pump, threaded brass ball valves), check valve Clapet of cast iron with flanges (or of bronze for the standby pump) – regulation gauges on exhausts and suctions of every main pump, together with taps and a suitable ladder; - automatic starting systems (one for each pump) with two pressure switches with manual reset and stop, drain and control ½’’ valves.
– a system for starting and control of the protection pump, together with a pressure switch for automatic starting, calibrated diaphragm with 4 5 mm openning, a check valve, all installed on pipes connecting with the tank. – a pipeline for water circulation between every main pump and the storage tank with a calibration dipragm with opennings of 5 to 6 mm and a pressure switch with manual reset and a remote "pump in operation" signal on the diapragm. Signal transmission will be of a "negative type", i.e. when contacts are open. – a test system with a capacity meter (aximeter or a diaphragm for direct reading) with joints for mobile control instruments, a stop valve for mounting of exhaust valve as well. – base of galvanized and painted structural steel to which all parts such as pumps, tanks etc. with non-vibrating neoprene holders will be fastened.
- command/control eelctrical distribution boxes, especially for the main electro pump and for motor pump, with additional distribution box for the standby pump and other ancillary devices (a distribution box for the main electro pump will not have magnetic and thermal protection); they will be assembled and completed as specified by norms UNI EN 12845, including, for the main electro pump, signs on the front side of the box (yellow lamp) and auxiliary contacts for remote signalling (in the protected zone) lack of pressure or phase power supply, as well as additional contacts for remote transmission of signal of started pump and the selector in the "not automatic" position. Distribution boxes will be completed, where required, with a star-delta motor starter.
Distribution box of the moto-pump will also include a counter, two battery chargers, and battery voltmeters and ammeters, as well as visible indications of pumps switched on, breakdowns on pumps, minimum oil pressure, maximum water temperature, minimum benzine level, lack of supply, minimum battery pressure; it will also include ancillary contacts for remote transmission of the motor switched on, a breakdown on the motor, anomalies on the battery, selector in the "not automatic" position, minimum benzene level.
Signalling of maximum level of the hydric reserve will be present also on the distribution box of the standby pump (yellow lamp) and a remore. Distribution boxes will be od galvanized and varnished sheet metal, or of solid glass wool or similar plastic material resistant to humidity. – a small remote distribution box, for the installation in a protected zone, for optic-acoustic signalling (buzzer and ice) from all ancillary contacts of eelctric distribution boxes: lack of voltage or a phase at the electro pump; eelctric pump started; selector of the "not automatic" position of the electrical pump; motor pump started; the motor pump breakdown; anomaly on the battery; selector of the "not automatic" position of the motor pump; minimum benzene level; maximum/minimum level of the hydric reserve.
The small distribution box will be provided with batteries with spark plugs, under constant voltage, for functioning of the signalization, with autonomy of minimum 24 hours in case of network failure; it will be made of galvanized sheet metal with fine varnish, in a colour selected by the contractor. – power lines (voltage, earthed, signalling) between distribution boxes, pumps and all devices, including a small remote distribution box: the lines will be placed between pipes of heavy resistant PVC, and final joints with motors and other devices will be made of flexible aroured coatings. – "minor" valves and twinning pipes will be in full conformity with the standard;
- Two sprinkler nozzles (for pump protection) together with feeding pipes (from exhaust collector, upon installation of check valve/s at the exhaust of the main pump) with support stop valve in open position, a fluxostat in conformity with the norm UNI EN 12259-5:2003, a system of acoustic/visual alarm installed in a protected location and a test exhaust valve (of nominal diameter of 15 mm) mounted upon installation of flow alarm so as to allow practical test of the alarm system. Other technical data: - supply voltage: around 400V three-phase (+/- 10%); frequency: 50Hz; - protection level of electrical engines: minimum IP55; - protection level of distribution boxes: minimum IP54. A pumping system will be manufactured to completion, tested and flawlessly functional. All parts (including pipes) will be red. The price shall include: - calibration, adjustments, functional testing and testing of counter-flow together with the contractor; - water supply connections, oil and electrical connections.
A SYSTEM FOR FIRE PROTECTION PUMPING IN CONFORMITY WITH THE NORM UNI EN 12845 WITH ELECTRO PUMP/ELECTRO PUMPS, MOTO PUMP AND A SPARE ELECTRO PUMP EN 12845 with two pumps, Q= 30 mc/h, P= 500 kPa
| Central devices / Fire protection |  | 1
| total |  | 1
TL.731.A1 | A SET OF ADDITIONAL PARTS FOR FIRE TANK | Lump sum
A SET OF ADDITIONAL PARTS FOR FIRE TANK In conformity with norms: UNI EN 12845 Construction and mounting characteristics: a set of additional parts for a hydric fire tank that includes: - suitable joints for various pipes, inlet or outlet, with threads or flanges (as needed). Joints consist of pipe fittings of galvanized steel (already with threads or flanges), for passing between walls and fastened to walls with special clips. Pipes passing through the cover of sewerage holes not allowing for easy dismantling are not allowed.
All pipes will pass through lateral parts of sewerage holes and manholes and, where needed, through tank's walls; - exhaust-overfill pipes, diameter not smaller than feed pipes, reach of minimum two metres from the tank, at the height of 0,5 meters from the ground level, bent at the end in the shape of a pipe and provided with an insect net.
Pipes will be of galvanized steel, coated with tar and jute; - two level probes, one for maximum level (for height exceeding around 10 cm of usable capacity) and one for minimum level (for height of around 30% of usable capacity), for alarm signalling; - a supply system with a float (or as per requirements), suitable diameter, with a butterfly or a ball stop valve and 'Y' filter between valves and feeders; - level indicator in the form of a transparent unbreakable pipe (protected in an opposite metal pipe with a front openning and with two stop taps) or pneumatic high precision type (including accessories); - passes already provided with firmly fastened cable bearing for possible electrical cables. In any case, connecting for inlet pipes and parts of tank joints will be manufactured of flexible non-vibrating knuckles of solid neoprene (or similar), included in the tank contracted price.
The price shall include: - hydraulic connections and possible electrical connections; - accessories until completion; - various expendables.
SET OF ADDITIONAL PARTS FOR FIRE TANK
| Central devices / Fire protection |  | 1
| total |  | 1
TOTAL FIRE PROTECTION DEVICES
TM | HEAT EXCHANGERS
TM.260.B13 | THERMAL GENERATOR (BOILER) WITH EXTERNAL PLATE EXCHANGER OF INOX STEEL AISI 316 | pcs
THERMAL GENERATOR (BOILER) WITH EXTERNAL PLATE EXCHANGER OF INOX STEEL AISI 316 In conformity with norms ISPESL (where requested and/or emphasized); Directive 97/23/CE; D.M. 21/03/73 and DPR 777/82 and subsequent changes; D.M. 108 25/01/92 and subsequent changes. Construction and mounting characteristics: a reservoir for making/storing sanitary hot water and for functioning with fluids under pressure, vertical or horizontal type (in conformity with requirements and/or needs), cylindrical form, with rounded bottom and support legs, manufactured of pickled steel sheet metal with carbon (thickness minimum 4mm) and treatment with organic enamel (or similar), in conformity with applicable norms so as to achieve suitability for storing drinking water. Tank will be complited with:
- outside heater with an exchanger of plate type of inox steel AISI 316, for inspection, including NBR plugs (oil-resistant rubber) or EPDM (acid-resistant rubber), end heads of varnished carbon steel with bearing bars and screws for assembly and fixing of plates, with threaded joints or flanges for main heating circuit; - a circulator for hot sanitary water flow between a battery and the exchanger; - two-position thermostat, submersible with a channel in the vicinity of the suction pipe towards the exchanger; - fittings and stop valve for the exchanger and the circulator; - threaded joints or flange joints, as requested and/or needed, for water intakes and outlets, as well as couplings for all required instruments and probes;
magnesium anode of dimensions that are proportionate to the surface to be protected; - bottom drain with a ball tap; - a thermometer with inert gas, of inox steel, maximum precision (class 1) and a gauge with a dial and a stop tap; - air exhaust valve on top; - safety valve with a spring calibrated on 6 bars with a drain; - thermal insulation, manufactured of (except in case of different requirements) high density glass wool coating and minimum thickness of 60 mm with thermal conductivity at temperature of 40 °C not above 0,040 W/mK (the value verified by a university laboratory)
with class 1 fire reaction certificates. Insulation will be completed with external final treatment of aluminium sheet metal not less than 6/10 mm. Where requested/emphasized: - tank will be manufactured entirely of inox steel AISI 316L (varnishing is not required in that case) and as previously described; - armored electrical resistors, mounted on the upper part, voltage of 1 kW per every 100 litres of the tank's capacity, except in case of different indications: in this case, a safety thermostat with direct shock on charging of resistors in case of preheating will have to be installed in the upper part of the tank. Technical characteristics: - a tank intended for pressures 20% higher than the actual working pressure of the tank and in any case not lower than PN6 (bar). The price shall include: - various accessories to completion; - hydraulic and power connections; - possible fastening and support material; - small expendables.
Heat boiler of the capacity of 3000 l, with a heat exchanger and a pump - cca 33kW
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TOTAL HEAT EXCHANGERS
TN | THERMAL INSULATION AND COATINGS
TN.110.A4 | THERMAL PIPE INSULATION OF ELASTOMER EXPANDED FOAM | m2
THERMAL PIPE INSULATION OF ELASTOMER EXPANDED FOAM In conformity with norms UNI EN 10376; UNI EN ISO 8497; - UNI EN 12086; - fire behaviout: Class 1 fire behaviour certificate. Construction and mounting characteristics: insulation in expanded elastomer of closed cells, implemented by extrusion and vulcanization of synthetic nitrile rubber, smooth surface and cylyndrical section, automatic switching off and resistant to effects of oil, usual chemical solvents and mould. For larger diameters, when coating is not possible, panels of the same material will be used. Joints between different parts will be glued and sealed by suitable self-adhesive tape to be provided by the same manufacturer. Mounting typology is described in the Specification or other technical documents of the project.
Technical characteristics: - heat conductivity at temperature of 40°C, not exceeding 0.040 W/mK (the value certified by the University laboratory); - vapour expanding resistivity factor above 7000; - working temperature range: between -50°C and +100°C; - product without CFC, HCFC, PVC and alogenes (chlorine and bromine); fire behaviour as previously indicated, with low toxicity and mistiness. The price shall include: - scraps and write-offs and special parts; - various expendables.
THERMAL PIPE INSULATION OF ELASTOMER EXPANDED FOAM, 13 mm thick
| Central devices / water supply and sewerage |  | 50
| total |  | 50
TN.110.A7 | THERMAL PIPE INSULATION OF ELASTOMER EXPANDED FOAM | m2
THERMAL PIPE INSULATION OF ELASTOMER EXPANDED FOAM In conformity with norms UNI EN 10376; UNI EN ISO 8497; - UNI EN 12086; - fire behaviour: Class 1 fire behaviour certificate. Construction and mounting characteristics: insulation in expanded elastomer of closed cells, implemented by extrusion and vulcanization of synthetic nitrile rubber, smooth surface and cylyndrical section, automatic switching off and resistant to effects of oil, usual chemical solvents and mould. For larger diameters, when coating is not possible, panels of the same material will be used. Joints between different parts will be glued and sealed by suitable self-adhesive tape to be provided by the same manufacturer. Mounting typology is described in the Specification or other technical documents of the project.
Technical characteristics: - heat conductivity at temperature of 40°C, not exceeding 0.040 W/mK (the value certified by the University laboratory); - vapour expanding resistivity factor above 7000; - working temperature range: between -50°C and +100°C; - product without CFC, HCFC, PVC and alogenes (chlorine and bromine); fire behaviour as previously indicated, with low toxicity and mistiness. The price shall include: - scraps and write-offs and special parts; - various expendables.
THERMAL PIPE INSULATION OF EXPENDED FOAM, 30 mm thick
| Central devices / water supply and sewerage |  | 35
| total |  | 35
TN.410.A1 | EXTERNAL THIN METAL SHEET COATING | m2
EXTERNAL THIN METAL SHEET COATING Construction and mounting characteristics: outside coating of thin sheet metal (aluminium, galvanized or varnished, or of inox steel depending on requirements and indications in the project technical documents) of minimum thickness of 0,6 mm consisting of polished parts (cylindric in case of pipe and circular channels), cut out and arranged along generatrice. The manner of application is described in the Specification. The price shall include: - scraps, write-offs and special parts; - various expendables.
Aluminium cover
| Central devices / water supply and sewerage |  | 87
| total |  | 87
TOTAL THERMAL INSULATION AND COATINGS
TO | MEASURING INSTRUMENTS
TO.120.A1 | DIAL THERMOMETER WITH INERT GAS (NITROGEN) DILATATION | pcs
DIAL THERMOMETER WITH INERT GAS (NITROGEN) DILATATION In conformity with norms: standardization ISPESL (thermometers in hot water thermal power plants); Construction and mounting characteristics: a system for measuring temperature in hydro-sanitary devices and air cooling devices, dilatation type with inert gas (nitrogene) with thermometric spiral spring and capillary pipe of inox steel, 100 mm diameter, with radial or back joint depending on the need, together with an insert for carrying glass of the same material, hermetic closing and with glass; - a dial of white aluminium with permanent numbering and adjusted to Celsius temperature scale (°C), with division in degrees depending on temperature and type of operating fluid. In case that a thermometer is installed on the pipe or air channels, it will be of ball type, together with solid channel for submerging in the pipe or channels with ball-channel joint to a flange or a threaded bell.
Technical characteristics: -readining precision: ne više od +/- 1 % širine skale. The price shall include: - umetno korito; - special parts; - various expendables.
Thermometer
| Central devices / water supply and sewerage |  | 6
| total |  | 6
TOTAL MEASURING INSTRUMENTS
TP | ELECTRO PUMPS AND COMPRESSORS
TP.110.4E | CIRCULATOR FOR HYDRO-THERMAL-SANITARY DEVICES | pcs
CIRCULATOR FOR HYDRO-THERMAL-SANITARY DEVICES In conformity with norms: UNI EN 1151 Construction and mounting characteristics: a device for circulation and distribution of hot or cold water, even for sanitary use or ice water, with a wet rotor during operation without sealing, consisting of: - a pump rotor and body of material highly resistant to wearing and corrosion, for example bronze or cast steel with surface treatment (vetrifikacija or treatment based on epoxy resin or similar), or, in case of a rotor, of robust cast plastics. The pump body will have joints with normalized threads or flanges together with fittings and gaskets, as per requirements/needs; ceramic or graphite bearings; - stainless steel axis; -air removal system; - electrical engine with a wet rotor with connectors, together with a protective cover for passing of the cable; - speed changing system (minimum three speeds (max 1450 turns/min), manual selection or selection by connectors).
Systems with only by-pass on the axis will not be accepted; - Capacitor permanently switched on (in case of a single-phase engine); - axial burden removal system; - operation indicator lamp and automated system for controlling rotation direction. Circulators for freezing water will be protected from inside condensation and in every case will have to be mounted so as to avoid leakage and condensatuon on joints.
Technical characteristics: - working temperature: from -10°C to +110°C; - maximum working pressure: 10 bars; supply voltage: around 230V single-phase (+/- 10%) for indicative power up to 1 kW; around 400V three-phase (+/- 10%) for indicative power above 1 kW; - frequency: 50 Hz; - engine with class F insulation and protection not below IP42. In case that diameters of check valves or stop valves are different from openning on the circulator, the price shall include conical connections (conicity not exceeding 15%) for binding, with end threads or flanges (depending on the type of joints on valves and on the circulator). The project working regime will be performed with a varioator in medium position (for example position number 2 in case of 3 positions on the variator) . The price shall include: - various accessories to completion, reverse flanges and screws; - possible holders and supports with clips; - small expendables.
CIRCULATOR FOR HYDRO-THERMAL-SANITARY DEVICES, Q= 2000 l/h P= 70 kPa
| Central devices / water supply and sewerage |  | 2
| total |  | 2
TP.420.A10 | MONOBLOCK INSTALLATION OF TANK-PUMP FOR LIFTING OF WASTEWATERS (SEWERAGE) | pcs
MONOBLOCK INSTALLATION OF TANK-PUMP FOR LIFTING OF WASTEWATERS (SEWERAGE) Construction and mounting characteristics: a system for lifting and draining of wastewaters consisting of a polyethylene tank of minimum 400 liters, with two lifting pumps with interior floats. Two possible alternatives are accepted: a) a tank with a wide cover for opening and interior submerged pumps which can be checked and detached from the cover, with a handle for managing lifting and a cast iron support which is firmly fastenend to the tank (‘loware’ system or similar); b) a tank with a cover which is fastened with bolts and provided with holes to which pump engines are fastened to (with flanges), with interior submerged rotor, with pumps which are detached from the cover by opening of flanges.
(KSB’ system or similar). In any case, each pump will consist of: - a single-phase or a three-phase system (with 2 or 4 poles) with a safety degree not lower than IP58 in case a), IP57 in case b), insulation class F, with axis on minimum tro spherical bearings without maintenance and thermal probes for overheating protection with automatic feeding; - centrifugal axes corresponding to sewerage outlets and pump body of baterial highly resistant to wearing and corrosion, for example bronze or cast steel, or of stainless stell for rotor; - suction grate with propellers of the same material as the rotor; - one-piece axis of inox steel with mechanical holders without maintenance; outside box of inox steel or cast iron, varnished in multiple layers (with initial treatment) based on epoxy resins or chlorinated rubber; - screws entirely of inox steel.
Each pump will be completed with: - electrical cable of appropriate length (cable inlet to the engine will be protected by resin seal); - a system with automatic mercury switch-float, properly fixed on the pump supply pipe (or similar) with electrical cable of appropriate lenght, together with accessories.
Pump level switches will be mounted and calibrated so as to achieve sequential operation of the pump; - check valve of grey cast iron, type appropriate for discharge waters, diameter minimum DN40, in every case with a plug fully coated with highly resistant rubber, together with the plug control and blocking system. Screws entirely of inox steel; - discharge pipes of HD polyethylene, PN10 or galvanized; pipes of two pumps will be merged into one, taken outside the tank, with a threaded joint of minimum 2’’. In aby case, the tank will be provided with a cover for internal inspection and access to pumps, with joint holes for inlet pipes on least two places or with a joint for exhaust pipes.
The system will be completed with a distribution box (installed in the system vicinity) and with connection lines (voltage, signal transmission, earthing) between the distribution box and the system. Except in case of specific instructions, the distribution box will be of wall cabinet type, of galvanized steel, varnished (or with epoxy coating), or of solid resistant plastic, in any case with protection not below IP44 (IP20 with open distribution box). It will include, together with a general switch, units for management, protection and safety of the pump and will correspond to the following criteria: - a selector with every pump with three positions, manual or automatic; - operation indicators for every pump, for manual start, automatic start and for failute indicator; - a system of automatic alternation of the order of inserting of pumps; - presence of contacts without voltage for distant signalling of operation overview.
Electric system will be completed by voltage connection, earthing and signal transmission lines (with suitable electric cables) between circuit box and devices (pumps, float switches etc.) which will be placed between solid PVC threaded pipes. Where requested and/or emphasized: - the lifting system will be supplied by a generator with a 230 Volt outlet, as described in the second document, and with automatic action upon power disconnecting by the provider. In this case, all cables between the circuit box and the generator will be provided. – pumps will be made completely of inox steel AISI 316 and suitable for aggressive waters. Technical characteristics: - working temperature: -20°C - +50°C; - supply voltage: around 230 V single-phase (+/- 10%) for indicative power of every pump above 1 kW, around 400V three-phase (+/- 10%) for indicative power of every pump above 1 kW; - frequency 50Hz; - motor with insulation class ’F’ and protection level minimum IP58/57.
The price shall include: - various accessories to completion; - electrical and hydraulic connection; - small expendables.
Wastewater lifting system with 2 pumps and a switch, Q=10 mc/h P=90 kPa pcs.
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TOTAL ELECTRO PUMPS AND COMPRESSORS
TQ | WATER TANK DEVICES
TQ.110.B30 | CYLINDRICAL TANK WITH STEEL INTERIOR FOR INITIAL COLLECTION OF WATER | pcs
| In conformity with norms: D.M. 21/03/73 e DPR 777/82 and subsequent amendments. UNI EN ISO 1461 (for hot galvanization). Construction and mounting characteristics: a recipient for initial water collection, vertical type and cylindrical shape with convex bottom and support legs, made of black steel tray, pickled, whose thickness may not be less than 4 mm and for installation inside buildings. Internal treatment (where necessary or determined by typologies) by organic varnishes in conformity with applicable norms will ensure suitability for drinking water storage. Besides, the tank will be equipped with threaded joints for supply pipes with joints' diameter up to 3" and flange joints for larger diameter of joints; passage for people to the top of the tank, with flanges, fastened with screws, with a cover and air exhaust pipes, level indicator made of a system of pipes of suitable transparent material equipped with a check valve and a discharge male valve protected against shocks with U or similar profile. |  |  |  |  | ty
A supply system with a float (in every case in conformity with requirements) of appropriate diameter, with ball stop valve, "Y" filter and anti-vibrating rubber flange (between the valve and the float); galvanized exhaust pipeline of diameter not smaller than the dimater of the supply pipeline, folded upwards in the form of a pipe with an insect net, which ends in the draining funnel with a siphon drain connected to the nearest sewerage; a flange and 1" ball drainage valve at the bottom with a rubber holder; anti-vibrating rubber spi calculation of the fireplace completely presented in graphic documents, material certification (resistant to heat, corrosion etc.); in conformity with the Law L. 46/90 and designation of the product with CE sign in conformity with (EN 1856-1). Joints on every receptacle; thermal insulation made of (except in special cases) of a panel
of expanded elastomer with closed cells, thickness above 19 mm with thermal conductivity at temperatures exceeding 40°C, not higher than 0.040 W/mK (the value verified by a university laboratory) and class 1 fire behaviour certificates. Insulation will be completed by external finalization of aluminium steet panelnot less than 6/10 mm. Where needed or specified: tank will be made of inox steel AISI 316L (interior enamelling is not needed in that case), equipped as already described; -maximum state level (alarm) and minimum (extraction pump). The price shall include: hydraulic connections, accessories to completion, possible support material, small expendables.
Water reservoir, AISI 316 stainless steel, 3000 litres
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TQ.175.A1 | WATER PRESSURE SYSTEM WITH PUMPS AND MEMBRANE TANKS AND CONTINUOUS REGULATION WITH INVERTER | pcs
WATER PRESSURE SYSTEM WITH PUMPS AND MEMBRANE TANKS AND CONTINUOUS REGULATION WITH INVERTER In conformity with norms: UNI ISO 9906 Construction and mounting characteristics: water pressurization system consisting of: -tank-autoclave with a supply membrane (Directive 97/23/CE, Decree-Law 174/04) of minimum number 2, suitable capacity which is, in any case, not below 20 l per tank, manufactured of steel of suitable thickness, treated on the inside and on the outside with epoxy alimentary protection, or of inox steel. Each tank will be adjusted to actual working pressures and in any case not below 5 bars, and the membrane will need to be easily replaceable; - two or more centrifugal electro pumps depending on the requirement and/or indications, with appropriate characteristics and vital parts of inox steel, three-phase power engine (or a single-phase in case of power up to 0,5 KW), protected type.
Each electro pump will be provided with a check valve resistant to water shocks and with two stop valves; - pump inlet collector of galvanized steel and suitable diameter (larger than the dimeneter of the pump valve), with a gauge and a stop valve; - a gauge with a stop valve; - a distribution box with hermetic closing, of galvanized metal, varnished with resin, with front door that open and consisting of: *a door blocking switch; *a switch for remote control and protection of pumps.
WATER PRESSURE SYSTEM WITH PUMPS AND MEMBRANE TANKS AND CONTINUOUS REGULATION WITH INVERTER, Q= 13 mc/h, P= 400 kPa
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TQ.220.A1 | WATER ADDITIVE DOSING SYSTEM | pcs
WATER ADDITIVE DOSING SYSTEM In conformity with norms: UNI CTI 8065; D.M. 443/90 and LG. 46/90. Construction and mounting characteristics: water treatment devices consisting of: - a storage tank with a cover, of robust plastic material resistant to wearing, of suitable capacity (minimum 50 litres) and in any case to guarantee autonomy of minimum two months in working conditions for which the device is designed. The tank will have a float which, when minimum level is reached, stops the dosing pump and signals alarm to the distribution box; - adjustable dosing pump together with: *joints with the tank and the injecting spot of durable flexible pipe resistant to high pressures; *a check valve; *injecting spot with a stop valve. – volumetric counter with an impulse sending system of appropriate type and characteristics.
The counter will allow switching-off and bypassing by three valves and offer option for direct fixing on the dosing pump into a single piece - the distribution operation/control box will be manufactured so as to allow feeding with only one single-phase line sufficient for impecable automatic functioning. It will be completed with all systems and automations required for full automatic functioning of the
system B402. Main additives, depending on requirements/indications, may be: - products for reducing hardness and deposits for hot sanitary drinking water with an efficiency threshold at least to the temperature of 70 °C and suitable for drinking water; - products for treatment of waters from the tower and/or from the humidification system, with algicidal effect and for preventing formation of deposits, and which are not harmful during manupulation; - aliphatic film-forming polyamines. Anyway, additives will in no case have toxic characteristics and will be manufactured by the most prestigious and most experienced manufacturing companies in the sector. Their effect will be documented by a clear and detailed documents to be provided by the manufacturing company, that the company will provide to the contractor and to the ordering party.
Calibration of dosing pump (included in the price) will be performed carefully with a series of controls of water properties and in conformity with instructions of the manufacturer of injected products. Technical characteristics: - supply voltage of the distribution box: around 230V (+/- 10%); - frequency: 50Hz; - protection level of the distribution box: not below IP44. The price shall include: - after initial injection of additives, quantities for the second filling (contained in cans or similar); - various accessories to completion; - hydraulic and electrical connection; - small expendables.
WATER ADDITIVE DOSING SYSTEM
| Central devices / water supply and sewerage |  | 2
| total |  | 2
TQ.220.A2 | WATER ADDITIVE DOSING SYSTEM | pcs
WATER ADDITIVE DOSING SYSTEM In conformity with norms: UNI CTI 8065; D.M. 443/90 and LG. 46/90. Construction and mounting characteristics: water treatment device consisting of: - a storage tank with a cover, of robust plastic material resistant to wearing, of suitable capacity (minimum 50 litres) and in any case to guarantee autonomy of minimum two months in working conditions for which the device is designed. The tank will have a float which, when minimum level is reached, stops the dosing pump and signals alarm to the distribution box; - adjustable dosing pump together with: *joints with the tank and the injecting spot of durable flexible pipe resistant to high pressures; *a check valve; *injecting spot with a stop valve. – volumetric counter with an impulse sending system of appropriate type and characteristics.
The counter will allow switching-off and bypassing by three valves and offer option for direct fixing on the dosing pump into a single piece - the distribution operation/control box will be manufactured so as to allow feeding with only one single-phase line sufficient for impecable automatic functioning. It will be completed with all systems and automations required for full automatic functioning of the system and and it will include a general switch with blocking of the door.
WATER ADDITIVE DOSING SYSTEM
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TQ.220.A3 | WATER ADDITIVE DOSING SYSTEM | pcs
WATER ADDITIVE DOSING SYSTEM In conformity with norms: UNI CTI 8065; D.M. 443/90 and LG. 46/90. Construction and mounting characteristics: water treatment devices consisting of: - a storage tank with a cover, of robust plastic material resistant to wearing, of suitable capacity (minimum 50 litres) and in any case to guarantee autonomy of minimum two months in working conditions for which the device is designed. The tank will have a float which, when minimum level is reached, stops the dosing pump and signals alarm to the distribution box; - adjustable dosing pump together with: *joints with the tank and the injecting spot of durable flexible pipe resistant to high pressures; *a check valve; *injecting spot with a stop valve. – volumetric counter with an impulse sending system of appropriate type and characteristics.
The counter will allow switching-off and bypassing by three valves and offer option for direct fixing on the dosing pump into a single piece - the distribution operation/control box will be manufactured so as to allow feeding with only one single-phase line sufficient for impecable automatic functioning.
It will be completed with all systems and automations required for full automatic functioning of the system and and it will include a general switch with blocking of the door. Main additives, depending on requirements/indications, may be: - products for reducing hardness and deposits for hot sanitary drinking water with an efficiency threshold at least to the temperature of 70 °C and suitable for drinking water; - products for treatment of waters from the tower and/or from the humidification system, with algicidal effect and for preventing formation of deposits, and which are not harmful during manupulation; - aliphatic film-forming polyamines. Anyway, additives will in no case have toxic characteristics and will be manufactured by the most prestigious and most experienced manufacturing companies in the sector. Their effect will be documented by a clear and detailed documents to be provided by the manufacturing company, that the company will provide to the contractor and to the ordering party.
Calibration of dosing pump (included in the price) will be performed carefully with a series of controls of water properties and in conformity with instructions of the manufacturer of injected products. Technical characteristics: - supply voltage of the distribution box: around 230V (+/- 10%); - frequency: 50Hz; - protection level of the distribution box: not lower than IP44. The price shall include: - after initial injection of additives, quantities for the second filling (contained in cans or similar); - various accessories to completion; - hydraulic and electrical connections; - small expendables.
WATER ADDITIVE DOSING SYSTEM
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TQ.220.A4 | WATER ADDITIVE DOSING SYSTEM | pcs
WATER ADDITIVE DOSING SYSTEM In conformity with norms: UNI CTI 8065; D.M. 443/90 and LG. 46/90. Construction and mounting characteristics: water treatment device consisting of: - a storage tank with a cover, of robust plastic material resistant to wearing, of suitable capacity (minimum 50 litres) and in any case to guarantee autonomy of minimum two months in working conditions for which the device is designed. The tank will have a float which, when minimum level is reached, stops the dosing pump and signals alarm to the distribution box; - adjustable dosing pump together with: *joints with the tank and the injecting spot of durable flexible pipe resistant to high pressures; *a check valve; *injecting spot with a stop valve. – volumetric counter with an impulse sending system of appropriate type and characteristics.
The counter will allow switching-off and bypassing by three valves and offer option for direct fixing on the dosing pump into a single piece - the distribution operation/control box will be manufactured so as to allow feeding with only one single-phase line sufficient for impecable automatic functioning.
It will be completed with all systems and automations required for full automatic functioning of the system and and it will include a general switch with blocking of the door. Main additives, depending on requirements/indications, may be: - products for reducing hardness and deposits for hot sanitary drinking water with an efficiency threshold at least to the temperature of 70 °C and suitable for drinking water; - products for treatment of waters from the tower and/or from the humidification system, with algicidal effect and for preventing formation of deposits, and which are not harmful during manupulation; - aliphatic film-forming polyamines. Anyway, additives will in no case have toxic characteristics and will be manufactured by the most prestigious and most experienced manufacturing companies in the sector. Their effect will be documented by a clear and detailed documents to be provided by the manufacturing company, that the company will provide to the contractor and to the ordering party.
Calibration of dosing pump (included in the price) will be performed carefully with a series of controls of water properties and in conformity with instructions of the manufacturer of injected products. Technical characteristics: - supply voltage of the distribution box: around 230V (+/- 10%); - frequency: 50Hz; - protection level of the distribution box: not below IP44. The price shall include: - after initial injection of additives, quantities for the second filling (contained in cans or similar); - various accessories to completion; - hydraulic and electrical connections; - small expendables.
WATER ADDITIVE DOSING SYSTEM
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TQ.310.B1 | AUTOMATIC SOFTENER | pcs
AUTOMATIC SOFTENER In conformity with norms: Decree-Law n°31/01; D.M. 443/90 e LG. 46/90; UNI CTI 8065; UNI CTI 8884; UNI CTI 7550. Construction and mounting characteristics: apparatus for softening of sanitary water or feeding steam generator, type ion-exchange resins, dimensions suitable for the cyclic capacity which is 200 times larger than the design capacity, as per the French water hardness degree (for example: water softener of 5 mc/h watered with water whose hardness is 20 as per the French degrees, cyclic capacity must be 5x200:20 = 50 mc) and consists of: steel anionic resin flume, minimum PN 10, whose interior is coated with ebonite or suitable plastics varnished on the outside, resistant to corrosion and the aging process.
It will include resin filling (bacteriostatic, as intended for nutrition)-tank of suitable material for brine (whose capacity will be sufficient for at least 10 regenerations) that contains filling for rasin and a cover; -pipeline of pvc material-PN 10 for connection (including a drain), servo-driven valves for performing functional programmes, regeneration, counter rinsing and a drain; partial by-pass device for mixing treated and untreated waters; thus bringing hardness of outlet water to the desired value. The servo-driven valves and partial by-pass device may be grouped into a single block;- n° 3 ball valve of pvc material PN 10 for stopping and by-pass of the softener; - control electric circuit manufactured so that it is sufficient to supply it from the single-phase line (without additional
apparatus) in order to have perfect automatic functioning.
It will be provided with all apparatus and automatisms required for fully automatic functioning of the system and provided with a general switch with doors for blocking. Where required or emphasized: in case that water softener is intended for hygienic-sanitary-alimentary use of water, resin must be of bacteriostatic type, and apparatus must be provided with automated self-desinfection system during regeneration or continuous post-disinfection; -softener type "packaged" (monoblock, with outside coating containing also a brine tank. Technical characteristics: softener must be adapted so as to treat volumes which correspond to the pressure enabled by the network, with load loss not exceeding 0,4 bars. – supply pressure of the distribution box: 230 V c.a. (+/- 10%); frequency: 50 Hz; protection level of the distribution box: not lower than IP 44. The price shall include: hydraulic connections, accessories to completion, small expendables.
AUTOMATIC WATER SOFTENER, 5 mc/h
| Central devices / water supply and sewerage |  | 2
| total |  | 2
TQ.415.A1 | MICROMETRIC SELF-CLEANING WATER FILTER | pcs
MICROMETRIC SELF-CLEANING WATER FILTER In conformity with norms: D.M. 443/90 e LG 46/90 Construction and mounting characteristics: water treatment device and for alimentary use, self-cleaning type, consisting of: - 360° moving head of brass body, with threaded fittings, or flange joints for diameters larger than 2’’ depending on the need and/or indication;
'- a vessel of solid transparent material with O-ring joints, together with a filtering element (insert) of stainless steel AISI 316; - manual steering by a handle and a flux deviator for reverse rinsing mechanism for cleaning of the insert; valve guide and lower valve that guarantee impecable hermetic closing of the flow after reverse rinsing; - lower drain with a funnel; - a part of the flexible pipeline (fastened to the drain joint) of the length that allows feeding of water for reverse rinsing to the nearest drain outlet or to the basin for collecting fluids (which is not included in the bid).
Self-cleaning by reverse flow will be performed by a simple start of the handle or similar, and the volume of water required for the self-cleaning process will need to be small, for example only a few litres. Technical characteristics: -filtriranje do 50 microcon; - maximum working pressure: 10 bars; - working temperature: to 40°C. Dimensions of the filter will be such so as not to cause pressure drop (clean filter and the highest capacity of the used scale) higher than 5% of the pressure upon switching-on, and in any case not higher than 0,40 bars. The price shall include: - hydraulic connection; - various accessories to completion; - small expendables.
MICROMETRIC SELF-CLEANING WATER FILTER, 8 mc/h
| Central devices / water supply and sewerage |  | 2
| total |  | 2
TQ.645.A1 | PRE-FABRICATED BASIN FOR SEPARATION OF GREASE FROM PLASTIC MATERIAL AND TREATMENT SYSTEMS | pcs
In compliance with norms - norm DIN 4040; - tab. 3 allegato n.5 D.L. n.152 - 03/04/2006 and additional changes, for discharge to public sewerage - norm EN 1825;
Construction and mounting characteristics:
Monoblock vessel of perfect hydraulic impermeability for outside installation, rectangular or round shape (depending on the capacity and/or the requirement), manufactured of polyethylene, provided on the inside with one or more partitions so as to create three chambers (higher, medium, lower) for accumulating oil and grease, for natural separation of grease from public wastewaters and for disposal-decanting of heavy matters (sand, food residues etc.)
Partition/s will be placed at the height varying from ½ to ¼ in relation to the height of the water column of the basin and the ratio between surface section and the height of the water column will have minimum value of 0,35 mq/m for separation of grease of the capacity up to 1000 l; 1 mq/m for larger capacities.
Pipeline at inlet-outlet will have a difference in the level of 30mm. Immediatelly upon commissioning (and before wastewater inflow), the basin will be filled with clean water.
The device implies: control manholdes of cast iron class D 400 placed on panels of the basin cover, in line with railway area-interior hydromechanical automated cleaning under high pressure (process of removing deposits, emulsions and rinsing) with automatic control functioning at 175 bars by a pump '-exhaust connection for quick joining Storz – B with a nozzle for draining by direct suction D N 65;
The price shall include: '- special parts '- connection to the inlet/outlet network of wastewater pipelines '- test of hydrical impermeability '- manhole for taking samples after separator '- filling unit '- small expendables
TQ645.A1
Rectangualr basin for separation of grease from polyethylene, capacity 320 litres, with a hydromechanic automated self-cleaning system and a water drain pump (Mod. ACO HIDROJET-OS or similar)
Grease separator, 320 litres
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TQ.900.A1 | SYSTEM FOR MAINTAINING FOUNTAIN PRESSURE | Lump sum
SYSTEM FOR MAINTAINING FOUNTAIN PRESSURE Centrifugal electro pump with automatic ignition with cast iron body together with pre-filter with a cover and mobile cast iron basket. Axis of inox steel, rotor of non-corrosive cast iron resistant to chemical agents in basins, electrical engine of horizontal disposition and direct matching.
Technical data: Capacity: 30 m³/h, Pressure: 1,3 bars, Joints: 2 ½’’ F, Power: 2,2 kW, Rotation number: 2.900 rotations/min Voltage: 230 – 400 +/- 10%V Frequency: 50Hz Protection: IP54 Absorption: 5,3 A
Compnsation tank with 2 pumps for maintaining pressure in the system, Q= 30mc/h, P = 130 kPa pcs.
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TQ.900.B1 | BASIN RECIRCULATION SYSTEM | Lump sum
BASIN RECIRCULATION SYSTEM Basin water recirculation system consisting of two centrifugal pumps with automatic ignition, horizontal disposition with directly paired engine, integrated pre-filter, axis of inox steel, a cast iron body and rotor, and the whole material is resistant to basin water.
Technical data for every pump: Capacity: 40 m³/h, Pressure: 400 kPa, Power: 7,5 kW, Electric joints: 400V – 50 Hz, Number of rotations: 2.900 rotations/min Protection: IP54 Joints of drain jet and aspiration: 3’’
Basin pump group with 2 integrated pumps, Q= 40mc/h, P = 400 kPa pcs.
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TQ.900.C1 | AUTOMATED BASIN FILTER | Lump sum
AUTOMATED BASIN FILTER Automated basin filter with a carbon steen pillar Fe 360 B, sand blasting SA 3 on the inside and SA 2,5 on the outside; interior alimentary plastification and outside auto-corrosive coating of glossy enamel. Double membrane head chamber – started by aquduct pressure and/or compressed air – performs commands by two 3-way 24V electro valves. A filtering system Multilayer for heterogenous mixtures consists of DREN HZ 2000 thermoactivated hydroantricites. – catalytic effect suitable for flocculation – with a support of the cleanest quartzite of diversified and selected granulometrty; gauge, holes for preventing preferential channels; upper handrail and square lower opening. In conformity with norms UNI 10637
Technical data: Capacity: 30 m³/h Working pressure: 4 bars Joints: 2’’ F Maksimalni gubitak opterećenja: bar Voltage/frequency: 24 V / 50 Hz Drain joints: 1 ½ ‘’ F Minimum and maximum water temperature: 5 ÷ 30 °C Minimum and maximum surrounding temperature: 5 ÷ 40 °C Dimensions h x Ø = 1760 x 900 mm Transport and working weight: 1000 / 1450 kg
AUTOMATED BASIN FILTER, capacity 30 mc/h
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TQ.900.D1 | ACCESSORIES TO COMPLETION FOR THE BASIN | Lump sum
ACCESSORIES TO COMPLETION FOR THE BASIN Accessories for proper functioning of basin devices including detergents, degreasers, products for removing grease from the basin, whirlpool itd. putties for analysis, salt-based powder products that eliminate chlorine from water for alimentary use, dosed in conformity with applicable norms and in any case suitable for use, drain faucets, probes for dosed injecting, valves and whatever is required for proper functioning of devices.
ACCESSORIES TO COMPLETION FOR THE BASIN
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TOTAL WATER TANK APPARATUS
TR | ADDITIONAL PARTS FOR DEVICES
TR.130.B10 | RUBBER COMPENSATION ELEMENT FOR VIBRATION ABSORPTION, PN 10/16 | pcs
RUBBER COMPENSATION ELEMENT FOR VIBRATION ABSORPTION, PN 10/16 Construction and mounting characteristics: - rubber compensator, opened in a shape of strip of spherically undulated material, highly elastic and with nylon support. Strip ends are provided with two rubber rings, end moving steel flanges suitable for passing through of screws; or with end joints with threads of soft cast steel. Element for elastic joining of pipes (for transport of fluids: water, acids, oil etc.) and for apsorbing resistance, oscillations, inclination, vibration etc.; suitable for amortization of transmission of vibration and noise in the vicinity of pumps, machines and similar devices; - installation typology is described in the Specification. Technical characteristics: - maximum working temperature: 90°C – working nominal pressure: 10/16 bars. The price shall include: - joining accessories with three parts (i.e. with reverse flanges and screws); - various expendables.
RUBBER COMPENSATION ELEMENT FOR VIBRATION ABSORPTION, DN80
| Central devices / water supply and sewerage |  | 8
| total |  | 8
TR.130.B8 | RUBBER COMPENSATION ELEMENT FOR VIBRATION ABSORPTION, PN 10/16 | pcs
RUBBER COMPENSATION ELEMENT FOR VIBRATION ABSORPTION, PN 10/16 Construction and mounting characteristics: - rubber compensator, opened in a shape of strip of spherically undulated material, highly elastic and with nylon support. Strip ends are provided with two rubber rings, end moving steel flanges suitable for passing through of screws; or with end joints with threads of soft cast steel. Element for elastic joining of pipes (for transport of fluids: water, acids, oil etc.) and for apsorbing resistance, oscillations, inclination, vibration etc.; suitable for amortization of transmission of vibration and noise in the vicinity of pumps, machines and similar devices; - installation typology is described in the Specification. Technical characteristics: - maximum working temperature: 90°C – working nominal pressure: 10/16 bars. The price shall include: - joining accessories with three parts (i.e. with reverse flanges and screws); - various expendables.
RUBBER COMPENSATION ELEMENT FOR VIBRATION ABSORPTION, DN50
| Central devices / water supply and sewerage |  | 4
| total |  | 4
TR.130.B9 | RUBBER COMPENSATION ELEMENT FOR VIBRATION ABSORPTION, PN 10/16 | pcs
RUBBER COMPENSATION ELEMENT FOR VIBRATION ABSORPTION, PN 10/16 Construction and mounting characteristics: - rubber compensator, opened in a shape of strip of spherically undulated material, highly elastic and with nylon support. Strip ends are provided with two rubber rings, end moving steel flanges suitable for passing through of screws; or with end joints with threads of soft cast steel. Element for elastic joining of pipes (for transport of fluids: water, acids, oil etc.) and for apsorbing resistance, oscillations, inclination, vibration etc.; suitable for amortization of transmission of vibration and noise in the vicinity of pumps, machines and similar devices; - installation typology is described in the Specification. Technical characteristics: - maximum working temperature: 90°C – working nominal pressure: 10/16 bar. The price shall include: - spojni dodaci sa tri dijela (tj. sa suprotnim prirubnicama i zavrtnjima); - various expendables.
RUBBER COMPENSATION ELEMENT FOR VIBRATION ABSORPTION, DN65
| Central devices / water supply and sewerage |  | 2
| total |  | 2
TR.211.A5 | EXPANDABLE MEMBRANE VESSEL | pcs
EXPANDABLE MEMBRANE VESSEL – In conformity with norms – Directive: 97/23/CE (PED) Construction and mounting characteristics: expandable vessel with a fixed membrane, manufactured of welded iron sheet metal, cylyndric form. Provided with a feeding membrane of atoxic rubber filled with inert gas (nitrogen), under appropriate pressure (usually 3 bars). Inside and outside finalization is anti-corrosive and suitable for alimentary purposes; it is used in hot sanitary water distribution systems, for water boiling apparatus, as a compensator for systems having a stop valve etc. Functioning characteristics: -maximum working temperature: 99°C-maximum working pressure 10 bars. The price shall include: support holders (where needed); - various expendables.
EXPANDABLE MEMBRANE VESSEL, 50 liters
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TR.360.A4 | MONOBLOCK AUTOMATED FILLING SYSTEM Construction and mounting characteristics: monoblock automated filling system with forged brass body, cover and closure, NBR stop seal, threaded joints with a connections consisting of: pressure regulator with a switch and a partition with counter-spring of inox steel, a stop device, inlet filter of sintered bronze and a gauge with a Bourdon spring (scale 0-6 bars). Manual stop valve placed in lower section, allows opening or closing of supply of devices. It is used for hydrothermal devices and mounted with water supply pipes, allows automated reintegration and/or charging of devices, maointaining pre-determined value of a closed electrical circuit pressure. | pcs
Functioning characteristics: maximum working temperature: 70 °C;-maximum working pressure upon installation: 16 bars; -smanjeni podesivi pritisak: 0.3-4 bars. The price shall include: hydraulic connections and calibration; accessories; various expendables.
AUTOMATED CHARGING SYSTEM, diam. 3/4"
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TR.380.A8 | HYDRAULIC SWITCH IN THE ZONE OF REDUCED VERIFIABLE PRESSURE | pcs
HYDRAULIC SWITCH IN THE ZONE OF REDUCED VERIFIABLE PRESSURE In conformity with norms: - UNI EN 12729; Construction and mounting characteristics: a double-stop hydraulic switch; in the zone of reduced verifiable and controlled pressure, with bronze body and cover or, however, at the same price, of cast iron and threaded joints with pipe joints for diameters up to 2” with flanges for larger diameters; supports, springs and bolts of inox steel, with brozne double stop valve with central chamber provided with automated drain valve, joints and measuring valves and apparatus for depressurization; visible drain funnel. Apparatus for preventing return/reverse contaminations of hydro network after mounting of the apparatus.
Where provided by the law or where it is necessary to avoid any type of return contamination in water, mounting of devices must be performed in the vicinity of the risk zone. Technical characteristics and functioning characteristics: nominal working pressure: 1 bar-maximum working temperature: : 65 °C The price shall include: hydraulic connections and calibration, reverse flanges accessories and screws; various expendables.
HYDRAULIC SWITCH IN THE ZONE OF REDUCED VERIFIABLE PRESSURE, diam. 2"
| Central devices / water supply and sewerage |  | 1
| total |  | 1
TR.752.A5 | PRE-FABRICATED CHANNELS WITH CEMENT CONGLOMERATE GRATES | m
PRE-FABRICATED CHANNELS WITH CEMENT CONGLOMERATE GRATES Procurement and installation of pre-fabricated channels of vibrated cement conglomerate, together with a frame and grates of galvanized steel resistant to shocks with a sealed 30x10 mm net, in conformity with norms UNI EN 124, which are used in class C 250 spots when executing a system for collecting flow waters, on a bearing of minimum thickness of 15 cm, and with limiters of cement conglomerate with a dose of 150 kg of cement type R 3,25 per m³ of aggregate. The price shall include levelling with the design inclination levels, procurement and installation of bearings and limiters, special accessories, a metal grate, conformitz with CE designation for construction products as per Directive 89/106/CEE in DPR 21.04.93, No. 246 and everything that is required for completion of the project. Possible renewal of floors will be calculated separately.
Channels with grates, 225x220 mm
| Central devices / water supply and sewerage |  | 8
| total |  | 8
TOTAL ADDITIONAL PARTS FOR DEVICES
B-1 | TOTAL WATER SUPPLY INSTALLATIONS